## Assignment Codes (hidden)
1 | Source Protection Planning Unit
2 | Asset Planning
3 | Asset Lifecycle Capability
4 | Project Delivery
5 | Tactical Asset Maintenance
6 | Process Engineering
7 | Process Improvement
8 | Operations - Supply
9 | Operations - Maintenance
10 | Water Quality Unit

## Action Register Final
Site | Region | Improvement # | Issue | Description | Origin of Improvement | Significant Risk | Significant Risk Level | Responsability | Due for Completion | Status | Risk Treatment Comments | Raised By | Date Raised | Manager | Closed
Supply System | Central | 9461 | Supply System - Disinfection (secondary) - Incorrect chlorine dose Under dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water. Medium (8). | Redlands Supply Zone - Investigation of having duplicate single instruments for Heinemann Road Reservoirs 1, 2 & 3. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-06-30 | In progress |  | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9464 | Eastbank WTP - Raw Water Abstraction - Change in Raw Water Source Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. Medium (8). | 1). Undertake HBT Assessment for this site. Completed. Refer Rex D19/46266 Eastbank WTP - HBT Assessment 2017-18 - HBT Assessment Report July 2017 - June 2018. 2) Long term planning is underway for this WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2028-12-29 | In progress | 1). HBT Assessment been completed. Refer Rex D19/46266 Eastbank WTP - HBT Assessment 2017-18 - HBT Assessment Report July 2017 - June 2018. | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9470 | Eastbank WTP - Coagulation - Flash mixer failure. Ineffective coagulation, flocculation and sedimentation, filter breakthrough and out of specification treated water. Medium (8). | 1). Installation of jet flash mixers for Sedimentation Basins No. 3 and 4. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 | In progress | 1). Trial for jet flashmixers has failed and this has gone back to planning. | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9473 | Eastbank WTP - Flocculation and Settling - Flocculator Failure. Ineffective flocculation and sedimentation, filter breakthrough and out of specification treated water. Medium (8). | - There is currently an options analysis being undertaken looking at what works would be required to improve flocculation associated with Sedimentation Basin No. 1 - Options analysis underway. Currently sitting with planning. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-06-30 | In progress | This item is a duplication of Action 9472. Refer to Action 9472 for further information around this improvement. | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9474 | Eastbank WTP -Flocculation and Settling - Carryover of floc, sludge, algae and/or turbidity in settled water. Carry over on to the filters and possible filter break through. Medium (8). | 1). Investigate what is causing the carryover onto the filters especially during Enhanced Coagulation. 2). Action any identified optimisation opportunities associated with the investigation. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-12-30 | In progress | 1). Pin floc at much increased alum dose without particle to work on plus short circuiting from basin 3 and 4, trial next year to improve short circuiting issue. | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9476 | Eastbank WTP - Media Filtration - Incorrect Polymer Dose. Under dose of Polymer resulting in reduced filter performance. Medium (8). | - Improve monitoring and control of the filter aid dosing system. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-12-30 | In progress |  | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9477 | Eastbank WTP - Media Filtration - Filter breakthrough. Potential contamination of treated water. High (16) | Upgrade of Eastbank filters. | Risk Assessment | High | 16 | Senior DWQ Advisor - Central | 2025-06-30 | In progress | Filter upgrade project started in March 2020. Update August 2022: Filter upgrade completed in early May 2022. All new filters operational. Project Completed. | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9480 | Eastbank WTP - Disinfection (primary) - Contamination by ingress Contamination of the treated water reservoirs at Camerons Hill Medium (8). | Improvement to vermin proofing need to be made to CH1 and CH2. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-12-31 | In progress |  | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Eastbank WTP | Central | 9482 | Eastbank WTP - Disinfection (secondary) - Inadequate mixing Overdose of chlorine leading to >ADWG health guideline Medium (9) | 1), There is currently a project to install a mixer to improve mixing. 2). Monochloramine instrument needs to be permanently mounted and recomissioned. | Risk Assessment | Medium | 9 | Senior DWQ Advisor - Central | 44926 | In progress | 1. Awarding a construction contract this calendar year and construction will start Jan/Feb 2022. Installation works proposed for May-July 2022. Update Aug 2022: Mixers have now been installed in the outlet pipework of Camerons Hill Reservoirs 1 and 2 during winter maintenance in June/July 2022. Mixers have now been commissioned and are operational. Project Completed. 2. Chemscan has been installed, calibrated and commissioned. Accuracy of the instrument is currently being verified. Until then operators are conducting regular grab samples and testing for monochloramine and ammonia. Update Aug 2022: Initial issue with accuracy was found to be that the Chemscan has not been fully calibrated correctly. Instrument is now accurate and being used to monitor WQ. Project Completed. | Senior DWQ Advisor - Central | 43579 | Senior DWQ Advisor - Central | N
Mt Crosby Westbank WTP | Central | 9506 | Westbank WTP - Raw Water Abstraction - Change in raw water source Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. Medium (8). | 1). Undertake HBT Assessment for this site; 2). Long term planning is underway for this WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2028-12-29 | In progress | 1). Completed. Refer Rex D19/84421 Westbank WTP - HBT Assessment 2017-18 - HBT Assessment Report July 2017 - June 2018. | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Westbank WTP | Central | 9507 | Westbank WTP - Disinfection (primary) - Contamination of service water distribution system due to main break or backflow incident. Potential contamination of treated water. Medium (8). | Conduct audit of the the service water to ensure that there are adequate measures in place to stop backflow events. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 | In progress | Audit completed. Recommendations to be delivered. | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Westbank WTP | Central | 9508 | Westbank WTP - Whole of System - Failure or incorrect operation of a bypass valve. Leading to out of specification treated water. Medium (8). | Consider reviewing lockout arrangements so that these bypass valves cannot be accidentally opened, prior to them being blanked off - Plates welded over spindles - | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 | In progress |  | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Mt Crosby Westbank WTP | Central | 9509 | Westbank WTP - Whole of System - Contamination due to backflow Service water backflow prevention inadequate leading to out of specification treated water. Medium (8). | Full audit needs to be undertaken on backflow prevention at Westbank. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 | In progress |  | Senior DWQ Advisor - Central | 2019-04-24 | Senior DWQ Advisor - Central | N
Wivenhoe WTP | Central | 9512 | Media Filtration - Filter breakthrough. Leading to out of specification treated water. Medium (8). | "Package plant to replace the existing plant between the raw water tanks and the clear water storage. Expected to be completed Dec 2018. Consideration should be given to ascertaining if it would be practical to installed a first filtered water to waste system, and undertake necessary works if this idea was deamed to be advantageous; Any upgrade of the control system associated with this WTP should retain interlocks that will automatically shutdown the relevent parts of the WTP in the advent of a critical limit being triggered (i.e. filtered water turbidity)." | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-01-31 | In progress | Package plant to be commissioned January 2021. | Senior DWQ Advisor - Central | 2019-04-24 | DWQ Advisor - Continuous Improvement | N
Wivenhoe WTP | Central | 9513 | Wivenhoe dam WTP- Disinfection (primary) - Insufficient C.t. "Insufficient C.t resulting from: - Inadequate t10; - Low free chlorine residual; - High pH; and - Low temperature." | Wivenhoe dam WTP- Disinfection (primary) - Insufficient C.t. "Insufficient C.t resulting from: - Inadequate t10; - Low free chlorine residual; - High pH; and - Low temperature." | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-01-31 | In progress | New plant to be commissioned January 2021 Update: delivery delay: agreed design is at 30% No change in project status. Operator vigilance in place. No incidents relating to hypo dosing pumps recorded. | DWQ Advisor - Continuous Improvement | 2019-04-24 | DWQ Advisor - Continuous Improvement | N
Wivenhoe WTP | Central | 9514 | Wivenhoe dam WTP- Whole of System - Loss of SCADA and/or communications system. Leading to loss of supply and/or out of specification treated water. Medium (8). | Wivenhoe dam WTP- Whole of System - Loss of SCADA and/or communications system. | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-01-31 | In progress | "Package plant to replace the existing plant between the raw water tanks and the clear water storage. Jacobs report (October 2015) recommends that Wivenhoe Dam WTP to proceed to preliminary design in the second phase of this project, including: Upgrading the control system." | DWQ Advisor - Continuous Improvement | 2019-04-24 | DWQ Advisor - Continuous Improvement | N
North Stradbroke Island WTP | South | 9561 | TNS - Supernatant Return - Superntant return quality exceeds treatment capacity. "For Herring Lagoon: Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return greater than 10% (pathogen risk) For Bores: N/A. Bore process does not include Supernatant Return process". Medium (8). (NSI-17) |  | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-07-31 | In progress | Update R.A review 2017: Improvements should also include automation of supernatant return process i.e batch sequence etc control and interlocks on flow and turbidity. Swapi to check Update R.A review 2018: APMP 2019 doc includes: NSI: Install turbidity monitoring on supernatent return - Install a turbidity meter in the supernatent pump well and connect and alarm to scada for 21/22. Supernatant return flow meter not included." Update geotube installation R.A review 2019: supernatant return turbidity installed with supernatant return pumps to interlock on HACCP limit. Geotube upgrade also includes control system sequencing and automation of batch sequence. Flow rate is based on calculation on SCADA and rate of return is limited to 10% by design and control of supernatant return pumps however the HBT manual and WSAA Good Practice Guide to the Operation of Drinking Water Supply Systems for the Management of Microbial Risk specifies a return rate of < 5 % of the raw water flow is recommended by the AWWA, Water Treatment Alliance and the WaterRA report 1079 Good Practice Guide to the Operation of Drinking Water Supply Systems for the Management of Microbial Risk 2015. Opportunities to meet this requirement using current assets should be investigated with a view to making recommendations for future upgrades if required to meet this target. A dedicated supernatant return flow meter would be required to verifiy < 5 % and should be progressed in the APMP program. Update 17/04/2020: ION Raised (ION01325) for installing independent supernatant return flow monitoring to allow for accurate flow monitoring. Currently flow rate is monitored by assumptions of supernatant return pump capability and observing increase in raw flow (combined raw water and supernatant flows). Supernatant Return is a HACCP CCP and independent flow rate monitoring is required. | Senior DWQ Advisor - South | 2015-01-28 | Senior DWQ Advisor - South | N
North Stradbroke Island WTP | South | 9562 | TNS - Coagulation - Incorrect lime dose/ Incorrect Coagulant dose. "For Herring Lagoon (pre lime): Underdose of lime into raw water main leading to: - low alkalinity for coagulation - incorrect dosed water pH Overdose of lime into raw water main leading to: - incorrect dosed water pH For Bores: N/A. Bore water does not pass through Coagulation Process Step". Medium (8). (NSI-8 & NSI-13) | Leading to loss of supply and/or out of specification treated water. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-12-31 | In progress | Update R.A 2017: 1) Operations South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included improvements to Lime System. Project cancelled Oct 2017. Project to be restarted. Update R.A 2018: 1) Interlocks programed Sep 2018 - Complete 2) APMP 2019 doc includes TNS: MCS Renewal: TNS: MCS Preliminary design for 20/21 and 21/22 3) APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Update 12/03/2020: timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 Update 12/03/2020: timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 | Senior DWQ Advisor - South | 2015-01-28 | Senior DWQ Advisor - South | N
North Stradbroke Island WTP | South | 9565 | TNS - Dissolved Air Flotation (DAF) - Failure or incorrect operation of a bypass valve. "Failure or incorrect operation of bypass from flash mixer to settled water main, or Failure or incorrect operation of bypass from supernatant return line to settled water main". Medium (8). (TNS-24) |  | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-12-31 | In progress | Update R.A 2018: Raised R&R workshop 2018. Update 25/03/2020: ION raised (ION01324): Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF oPRP). Under no circumstances would these bypasses be operated. | Senior DWQ Advisor - South | 2017-11-20 | Senior DWQ Advisor - South | N
North Stradbroke Island WTP | South | 9566 | TNS - Media Filtration - Filter breakthrough. "Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (AN905-PWG)". Medium (8). (NSI-9 & NSI-13) | Medium (8). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-12-31 | In progress | Update R.A review 2017: 1) Operations South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included improvements to monitoring and control of filter process. Project cancelled Oct 2017. Project to be restarted. Update R.A review 2018: 1) interlocks complete 2) APMP 2019 doc includes TNS: MCS Renewal: TNS: MCS Preliminary design for 20/21 and 21/22 3) APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Update 12/03/2020: Timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 | Senior DWQ Advisor - South | 2015-01-28 | Senior DWQ Advisor - South | N
North Stradbroke Island WTP | South | 9567 | TNS - Disinfection (primary) - Insufficient C.t. "When running Borefield and Herring Lagoon through CCT and Res 1 (Res 2 balancing or offline) Insufficient C.t due to: - low chlorine - high pH due to post lime overdose - insufficient contact time - high treated water turbidity". Medium (8). (NSI-10 & NSI-13) | "Risk Treatment (raised R.A 2015 and Report to Asset Planning D14/149372): It is recommended, to mitigate the hazardous event ‘insufficient C.t’ that control of disinfection is improved. This improvement should consider: - installation of online free chlorine and pH analysers downstream of the chlorine contact tank and lime dosing point at a point that provides suitably mixed and representative water sample, upstream of the Treated Water Reservoir No. 1. (Complete at R.A 2017) - implementation of associated call out alarming and interlocks to WTP operation from these pre-reservoir analysers - trim control of the chlorine and lime dose using the online free chlorine and pH analysers - dynamic monitoring and call out alarming of C.t is introduced in the SCADA. Interlock to WTP operation should also be implemented. - the maximum instantaneous flow rate leaving the WTP and if required installation of additional contact time to enable the minimum C.t to be achieved under worst case conditions. This should include investigation of the hydraulics of the chlorine contact tank and the potential for flooding of the baffles. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-12-31 | In progress | Update R.A 2017: 1) Operation South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included upgrade and/or addition to the exiting lime dosing system or construction of an alternative means of alkalinity adjustment was captured as a work package. Project cancelled Oct 2017. Project to be restarted. 4) PID02656 - TNS: Renew Chlorine Dosing Lines in Project Delivery 17/18 Program PID02863 - TNS: Replace Chlorinators in Project Delivery 17/18 Program". Update R.A 2018: - APMP 2019 doc includes TNS: MCS Renewal: TNS: MCS Preliminary design for 20/21 and 21/22 - APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24 - Dynamic C.t monitoring on SCADA to be implemented for all WTPs - CCT max flow investigations not yet started. Update R.A 2018: - APMP 2019 doc includes TNS: MCS Renewal: TNS: MCS Preliminary design for 20/21 and 21/22 - APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24 - Dynamic C.t monitoring on SCADA to be implemented for all WTPs Update 25/03/2020: Refer to RW-A-11528 for Dynamic C.T Monitoring on SCADA - CCT max flow investigations not yet started - investigation to be undertaken as part of Major Upgrade Matt Tomlins | Senior DWQ Advisor - South | 2015-01-28 | Senior DWQ Advisor - South | N
North Stradbroke Island WTP | South | 9569 | TNS - Disinfection (primary) - Incorrect lime dose. Underdose of lime resulting in pH less than ADWG aesthetic guideline. Medium (9). (NSI-18) | Risk Treatment (raised Report to Asset Planning D14/149372 and IMS audit Feb 2016. Increased from IO to Risk Treatment in R.A review 2017 due to potential for widespread aesthetic impact by grid WTP): The lime dosing system is a constant operational issues. Numerous incidents, HACCP Critical Limits excursions and HACCP Action Limit excursions have been reported due to lime dosing system faults. | Risk Assessment | Medium | 9 | Senior DWQ Advisor - South | 2023-06-30 | In progress | Update R.A review 2018 Interlocks enabled Sep 2018. APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24 Update 12/03/2020: Timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 Update 25/03/2020: APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 | Senior DWQ Advisor - South | 2017-11-20 | Senior DWQ Advisor - South | N
North Stradbroke Island WTP | South | 10141 | TNS - Media Filtration - Filter breakthrough. "Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (AN905-PWG)". Medium (8). | Risk Treatment (raised R.A review 2017): Investigate the risk associated with walking over filters due to significant amount of Kangaroo droppings around the site. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2021-12-31 | Completed | Update R.A review 2018: TNS Install Walkway Vertical Ladders and Davit Bases for Operations and Maintenance Access to Each Filter Base to include risk mitigation. Update 25/03/2020: Has been included in PID03374 – TNS: Filter media top up project in delivery 20/21. Installed/delivered during 20/21 | Senior DWQ Advisor - South | 2017-11-20 | Senior DWQ Advisor - South | Y
North Stradbroke Island WTP | South | 10182 | TNS - Coagulation - IIncorrect coagulant aid dose. For Herring Lagoon: Overdose of AN905 into inlet floculation tank leading to ineffective coagulation or acrylamide > ADWG OR Underdose of AN905 into inlet floculation tank leading to ineffective coagulation For Bores: N/A. Bore water does not pass through Coagulation Process Step Medium (8). (TNS-21) | Risk Treatment (raised R.A 2017): Improvements to dosing, monitoring and alarming relating to poly system. Current impact of failure is minimal under normal conditions however when required, if poly dosing fails, subsequent processes are likely to fail. Improvements required. TNS-Media Filtration - Incorrect Floculation aid Dose Overdosing of filter aid into the filter inlet | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-12-31 | In progress | Update R.A 2018: APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Timelines under review. Update 11/03/2020: APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 | Senior DWQ Advisor - South | 2017-11-20 | Senior DWQ Advisor - South | N
Boonah-Kalbar WTP | South | 10283 | TBK - Disinfection (primary) - Contamination by ingress Contamination of treated water tank Medium (8) (TBK-17) | Risk Treatment raised (raised Audit 2017): Vermin proofing of reservoir required. Update R.A review 2017: Emergent works request submitted and in EW register. Update R.A review 2019: PID03044 TBK Vermin Proofing project completed late 2018. Reservoir roof hatch and level cable still open. Works Request May 2019 with Maintenance to repair the holes. TBK: Install Dry-Panning: Install dry-panning around access hatch to prevent ponding and roof corrosion in APMP 2019 plan for 21/22. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 | Completed |  | Senior DWQ Advisor - South | 2017-08-23 | Senior DWQ Advisor - South | Y
Molendinar WTP | South | 10321 | TMO-RW-A-10321 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. | TMO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMO-17) Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatment capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-06-30 09:00 | Completed | Update October 2019: Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81738 Molendinar WTP - HBT Assessment 2018/19 - Draft Report. Note this does not incorporate review of source water category. Rex Ref. D19/81738. Update 21/07/2020: Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled for August 2020 Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. | Senior DWQ Advisor - South | 2017-11-03 09:00 | Senior DWQ Advisor - South | Y
Molendinar WTP | South | 10339 | TMO-RW-A-10339 Risk Treatment: WTP shutdown takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Under high flow conditions this is not insignificant. Review and optimise interlock sequencing. Develop recovery plans where required if impacts to CCPs during high flow conditions require recovery. | TMO - Whole of System - Loss of control system. Loss of SCADA system or loss of PLC leading to impacts to treated water quality Medium (8) Risk Treatment (raised R.A 2017): Raw water pump shut down takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Review and optimise interlock sequencing. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2019: WTP shutdown takes 20 mins because raw water valve takes 20 mins to close due to functionality set. This improvement may not be possible until new valve installed. Update R.A 2021: Being actioned under Risk Wizard incident 26864 HACCP critical limit exceedance no coag flow. HACCP crash stop is 12 mins. | Senior DWQ Advisor - South | 2017-11-03 09:00 | Senior DWQ Advisor - South | Y
Beaudesert WTP | South | 10350 | TBE - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - blockage of tridant arms from algae sloughing off aerator causing bypass of clarifier - blockage of tridant arms when bypass raw water screens when deisel pumps causing bypass of clarifier - Underdose of poly (floc/settling aid) | Risk Treatment: (raised Mar 2018 during Ammonia Project commissioning): Review clarifier design with the purpose of improving settling. Permanent poly batching and dosing assets required. Consider need for pre filter chlorine dosing to prevent filter head loss issues. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: pre filter chlorine introduced. Poly dosing was introduced under an incident process. As such it is a temporary set up the poly is not flow paced to raw water flow. Preventative measures are considered sufficient to reduce overdose to Unlikely however there is a high uncertainty rating associated with this due to the lack of site specific operational experience and rapid introduction under incident process. Upgrade of poly dosing system being delivered under PID03434 TBE Beaudesert Polymer and acid dosing - HAZOP and Design Review. ION00365 for improvements to pre filter chlorine dosing system assets. Refer Raw Water Abstraction Improvemetn Opportunity TBE-RW-A-10346 for clarifier tridant arm blockage (in dashboard) | Senior DWQ Advisor - South | 2018-03-05 | Senior DWQ Advisor - South | Y
Beaudesert WTP | South | 10351 | TBE - Flocculation and Settling - Failure or incorrect operation of a bypass valve Failure or incorrect operation of a clarifier bypass valve. | Tag out bypass to ensure clear identification of valve and prevent accidental use. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: increased to Risk Treatment due to relocation of alum dosing after the aerator this bypass is now a raw water to filtered water bypass which is an unacceptable risk. Remove bypass pipework to create air gap. Currently two closed valves in place. Check if maintenance can remove section of pipework between valves as intermin until blanking plates can be installe via ION process. | Senior DWQ Advisor - South | 2017-06-07 | Senior DWQ Advisor - South | Y
Hinze Dam WTP | South | 10395 | THZ - Raw Water Abstraction - Rain event in catchment Intake of increased treatment load that could potentially result in contaminated treated water Medium (8) (TMO-17) | Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category for Hinze Dam. Treatment capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. Risk Treatment Reference is as per Molendinar WTP Risk Treatment Reference. Acknowledge that BoH tank is not filled when raw water quality at lower intake is undesirable. Assessment carried out for Molendinar WTP should incorporate Hinze Dam WTP. Refer Molendinar WTP Risk Improvement Item | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2019: PE team undertaking WTP performancec HBT assessment. | Senior DWQ Advisor - South | 2017-06-22 09:00 | Senior DWQ Advisor - South | Y
Hinze Dam WTP | South | 10397 | THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water Medium (8) (HNZ-5) | Risk Treatment: Although this is not known to have occurred at Hinze Dam WTP there is occurrences of coag dosing pipe breakages at other WTPs. There is currently a coagulant flow switch interlocked to WTP operation however coag flow monitoring interlocked to WTP operation is required. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-11-30 09:00 | Completed | Update R.A review 2017: Confirmed as viable WTP and will continue operating. Project will be pursued by Process Improvement Specialists based on current understanding that WTP will remain for the foreseeable future. To be included in Minor Works upgrade 17/18. Note Control System is very limited in terms of adding any further alarms or monitoring. Sludge upgrade project would trigger upgrade of PLC. Update R.A review 2019: Not delivered at time of R.A. Update 9/07/2021: Sen. DWQ Advisor Sth: wait for outcome of Moogerah and Maroon Dam coag flow meter projects. Similar flow rate and project currently in delivery. Issues with measuring such low flow rate may or may not be overcome. Update 21/09/2021: Senior DWQ Advisor - Continuous Improvement to escalate ION184 or raise a new ION to install ACH coag flow meter. In the short term identify options to get existing signals available on the ACH dose pump into SCADA that can be used as the HACCP critical limit to interlock the WTP. Update Hinze Dam WTP HACCP Wall Chart and HACCP Plan Validation 3.2 to document signal in use for this HACCP critical limit. Update 29 NOV 21: Date extended 12 months as this work has not yet included in any program. Management of this risk to be reviewed on-site and then discussed at next HACCP team meeting (Mar 22). | Senior DWQ Advisor - South | 2015-03-23 09:00 | Senior DWQ Advisor - South | Y
Moogerah WTP | South | 10411 | TMG - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMG-15) TMG - Coagulation - Incorrect coagulant dose Underdose of alum including inadequate mixing Medium (8) (TMG-15) TMG - Coagulation - Incorrect coagulant dose Overdose of alum leading to ineffective coagulation affecting treated water quality Medium (8) (TMG-15) | TMG - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Deterioration of Granular Activated Carbon (GAC) media resulting in inadequate removal of TO (primarily) and organics and manganese (secondary) due to: - exceed GAC lifespan Medium (8) (TMG-15) Risk Treatment (raised R.A 2017): HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP likely to required additional protoza removal (i.e UV). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: Conservative assessment at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP will require additional protoza treatment (i.e UV). Update 2020: ION01470 raised for the installation of UV | Senior DWQ Advisor - South | 2017-09-06 09:00 | Senior DWQ Advisor - South | Y
Moogerah WTP | South | 10412 | TMG - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - high pH Medium (8) (MOO5) | Risk Treatment: Lack of alum flow monitoring is an unacceptable risk due to periods of low RW pH. Alum flow monitoring required (and injection point flow switch or meter if carrier water used) with interlocks to shutdown the WTP. Raw water pH 5th%iles are <7.5 pH which is s the validated SPV upper critical limit for dosed water pH using alum. Therefore during a rain event when RW pH is low (5% of the time) if alum dosing was lost this would not trigger the upper critical limit of pH 7.5. In the short term a low dosed water pH limit will be used which should detect alum dosing failure in most circumstances. Alum pump fault alarms and lowering dosed water pH limit are interim measures | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2017: Investigate installation of flow switch to detect loss of alum dose. Update R.A 2020: Business Case in development Update 2021: In project delivery and commissioning. | Senior DWQ Advisor - South | 2015-11-04 09:00 | Senior DWQ Advisor - South | Y
Moogerah WTP | South | 10413 | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-16) | Risk Treatment (raised R.A review 2017): Investigate opportunities to address clarifier sludge build up requiring manual draining and hose out on a regular basis. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: P.E to investigate replacement or modification of clarifier. Reference P.E action item | Senior DWQ Advisor - South | 2017-09-06 09:00 | Senior DWQ Advisor - South | Y
Kooralbyn WTP | South | 10446 | TKO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TKO-15) TKO - Coagulation - Incorrect coagulant dose Underdose of alum resulting in contaminated treated water including incorrect dosed water pH Medium (8) (TKO-15) TKO - Coagulation - Incorrect CO2 dose Underdose (absence) of CO2 causing high dosed water pH resulting in contamination of treated water Medium (8) (TKO-15) | TKO - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) (TKO-15) TKO - Flocculation and Settling - Failure or incorrect operation of a bypass valve Failure or incorrect operation of a clarifier bypass valve Medium (8) (TKO-15) TKO - Media Filtration - Filter breakthrough Filter breakthrough Medium (8) (TKO-15) Risk Treatment (raised Kooralbyn WTP - pathgoen treatment assessment report June 2015 - documented R.A 201): Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146 'Note: CO2 injection point available however system is not integrated into SCADA | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19. Update R.A 2020: PID02914 TKO: UV Disinfection Upgrade in APMP for delivery 21/22. | Senior DWQ Advisor - South | 2017-07-19 09:00 | Senior DWQ Advisor - South | Y
Maroon Dam WTP | South | 10461 | TMD - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - low pH in raw water Medium (8) (MAR8) | Risk Treatment: Lack of alum flow monitoring is an unacceptable risk due to periods of low RW pH. Alum flow monitoring required (and injection point flow switch or meter if carrier water used) with interlocks to shutdown the WTP. Raw water pH 5th%iles are <7.5 pH which is the validated SPV upper crtiical limit for dosed water pH using alum. Therefore during a rain event when RW pH is low (5% of the time) if alum dosing was lost this would not trigger the upper crtical limit of pH 7.5. In the short term a low dosed water pH limit will be used which should detect alum dosing failure in most circumstances. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2017: Investigate installation of flow switch to detect loss of alum dose. Update R.A 2020: Business Case in development Update 2021: In project delivery and commissioning. | Senior DWQ Advisor - South | 2015-11-04 09:00 | Senior DWQ Advisor - South | Y
Maroon Dam WTP | South | 10462 | TMD - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMD-18) TMD - Coagulation - Incorrect coagulant dose Underdose of alum including inadequate mixing Medium (8) (TMD-18) TMD - Coagulation - Incorrect coagulant dose Overdose of alum leading to ineffective coagulation affecting treated water quality Medium (8) (TMD-18) | TMD - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMD-18) TMD - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (5) (TMD-18) TMD - Media Filtration - Filter breakthrough Deterioration of Granular Activated Carbon (GAC) media resulting in inadequate removal of TO (primarily) and organics and manganese (secondary) due to: - exceed GAC lifespan Medium (5) (TMD-18) Risk Treatment (raised 2017): HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP likely to required additional protoza removal (i.e UV). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: ION raised for UV installation (ION01469). | Senior DWQ Advisor - South | 2017-09-06 09:00 | Senior DWQ Advisor - South | Y
Maroon Dam WTP | South | 10463 | TMD - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMD-19) | Risk Treatment (raised R.A review 2017): autodesludge on start up would be an operational improvement for this site. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: P.E to raise ION Update 02/03/2020: ION01262 raised for TMG- Auto de-sludge via pump or de-sludge valve. | Senior DWQ Advisor - South | 2017-09-06 09:00 | Senior DWQ Advisor - South | Y
Mudgeeraba WTP | South | 10476 | TMU-RW-A-10476 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. | Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatement capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. TMU - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water (HUI LND) Medium (8) (TMU-29) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81746 Mudgeeraba WTP - HBT Assessment 2018 - Draft Report. Note this does not incorporate review of source water category. Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. | Senior DWQ Advisor - South | 2017-10-27 09:00 | Senior DWQ Advisor - South | Y
Mudgeeraba WTP | South | 10485 | TMU-RW-A-10485 Risk Treatment: Undertake improvements to improve filter performance for filters which don't consistently achieve protozoa LRV log reduction credits due to filter ripening spikes. | Risk Treatment (Raised HACCP internal audit 2014): Review of filtration performance at Mudgeeraba WTP to identify inadequacies to Planning. Following the filter optimisation project the individual filtered data will need to be assessed. If operational changes do not improve filter performance then capital improvements such as addressing the filter to waste restriction or an additional process step (eg UV) should be considered as log removal credits under the Health Based Targets standard cannot be applied based on the current HACCP limits. TMU - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) when required | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-07-31 | In progress |  | Senior DWQ Advisor - Continuous Improvement | 2017-10-27 | Senior DWQ Advisor - South | N
Rathdowney WTP | South | 10499 | TRA - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TRA-30)(ALL16) TRA - Supernatant Return - Superntatnt return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose Medium (8) (TRA-30)(ALL16) | TRA - Coagulation - Incorrect coagulant dose Underdose of ACH (dosed neat) including loss of carrier water Or Ineffective coagulation due to elevated pH High (12) (ALL16) TRA - Coagulation - Incorrect coagulant dose Overdose of ACH (dosed neat) Medium (8) (ALL16) TRA - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) (ALL16) TRA - Media Filtration - Filter breakthrough Fitler breakthrough Medium (8) (ALL16) TRA - Media Filtration - Build up of solids leading to elevated turbidity High turbidity filtered water from backwash water tank used to backwash filter leading to filter breakthrough when filter back online Medium (8) (ALL16) Risk Treatment (raised Rathdowney WTP – pathogen treatment assessment - documented R.A 2017): Refer D15/114408. Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital planning register. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: PID02915 TRA: UV Disinfection Upgrade in APMP for delivery 21/22. | Senior DWQ Advisor - South | 2017-10-27 09:00 | Senior DWQ Advisor - South | Y
Rathdowney WTP | South | 10500 | TRA - Supernatant Return - Supernatant return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose Medium (8) (RAD 23) | Risk Treatment (raised R.A review 2017): Supernatant return flow rate maximum is designed to be controlled by SCADA to not exceed 10% of raw water flow. At the time of conducting the R.A review the automation was not enabled and supernatant return flow rate was manually throttled by Operators. Observation is that automation works when WTP running at 5L/s but struggles at current rate of 4 L/s. Process Engineer to investigate improvements to automation control. In addition a return rate of <5 % of the raw water flow is recommended by the AWWA, Water Treatment Alliance and the WaterRA report 1079 Good Practice Guide to the Operation of Drinking Water Supply Systems for the Management of Microbial Risk 2015. Opportunities to meet this requirement using current assets should be investigated with a view to making recommendations for future upgrades if required to meet this target. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update R.A 2020: Rate of return control Opportunities to meet this requirement using current assets should be investigated with a view to making recommendations for future upgrades if required to meet this target currently not being progressed on PE program. Seqwater currently putting together BC to progess a research project with WaterRA and other utilities to investigate and make recommendations on the 10% supernatant return rule (hyperlink below). https://www.waterra.com.au/research/current-opportunities/2019/investigating-supernatant-return-management-practices-in-drinking-water-treatment/ | Senior DWQ Advisor - South | 2017-03-01 09:00 | Senior DWQ Advisor - South | Y
Rathdowney WTP | South | 10502 | TRA - Coagulation - Incorrect coagulant dose Underdose of ACH (dosed neat) including loss of carrier water Or Ineffective coagulation due to elevated pH High (12) (RAD 18) | 'Risk Treatment (raised R.A review 2015): Install a flow meter on the ACH dosing line with interlocks and pump fault alarms. | Risk Assessment | High | 12 | Senior DWQ Advisor - South | 2020-12-31 | Completed | Update R.A review 2017: Coagulant (589) flow monitoring was installed in Sep 2015 and integrated into SCADA including alarming and WTP interlock functionality. A time of R.A review 2017 the flow trend was assessed as being not reliable for alarming therefore risk remains significant. Update R.A review 2020: ACH trial commenced 26/08/2019. Flow meter found to be adequate for monitoring ACH flow when ACH being dosed however when loss/low coag flow occurs the flow meter fluctuates and was found not to trigger the HACCP critical limit interlock. Refer HACCP Critical Limit Exceedance TRA-RW-I-21474. HACCP limit under review and trial at time of R.A.2020. Validation of delay on start up complete. | Senior DWQ Advisor - South | 2015-04-22 | Senior DWQ Advisor - South | Y
Hinze Dam WTP | South | 11264 | THZ - Distribution Pipeline - Contamination due to pipe break 'Ingress of contaminants into reticulation system affecting treated water quality Medium (8) | 'Risk Treatment (raised R.A review 2019): Reduce frequency of Hinze distribution system pipework breaks/leaks. ION raised. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update 21/07/2020: Hinze Dam Potable Reticulated Water Supply Network replacement project has commenced to BC development | Senior DWQ Advisor - South | 2017-06-22 09:00 | Senior DWQ Advisor - South | Y
Amity Point WTP | South | 11280 | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore 'Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: '- Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk Medium (8) Target risk (5) | Risk Treatment (raised R.A 2017): Undertake Pathogen Assessment of NSI Township WTPs and review of preventative measures and monitoring for managing risk of abstraction of contamination groundwater is required including condition of bore casings, bore location in relation to flood level, condition of seals on above ground assets. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-06-30 09:00 | Completed | Update R.A 2019: Based on having a shallow aquifer and, other than the Seqwater bores, having no control over the confines of the aquifer there has to be an assumed level of interaction whether it be continuous or intermittent. Therefore Amity Point WTP has been assessed as Source Category 2 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 3.0 LRV; protozoa 2.5 LRV under WSAA HBT Manual. Refer Risk Treatment Disinfection (primary) for improvements to C.t (TAP-RW-A-TBC) Protozoa treatment required in the form of UV disinfection to achieve protozoa 2.5 LRV. Update 26/03/2020: Attached email with work order inspections checklists | Senior DWQ Advisor - South | 2017-11-21 09:00 | Senior DWQ Advisor - South | Y
Amity Point WTP | South | 11281 | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: '- Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk Medium (8) Target risk (5) | Risk Treatment (raised R.A 2017): Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity (raised HACCP internal audit 2016) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-06-30 09:00 | Completed | Upgrade R.A 2019: Ingress issued identified. ION 00237 raised. Identified Issues resolved Jan 2019 by Operations Maintenance team. Ongoing inspections of bores (and all WTP assets) to be included in CIS routine work orders. Inspection criteria to be specific as per reservoir inspections checklist. Progression of UV disinfection to treat for hazards is preferable to installing additional online monitoring as standard online monitoring techniques is unlikely to be sensitive enough to detect a surface hazard and ground water interaction. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Update 15/05/2020: ION01366 has been raised for installing on-line turbidty monitoring of the combined raw. | Senior DWQ Advisor - South | 2017-11-21 09:00 | Senior DWQ Advisor - South | Y
Amity Point WTP | South | 11284 | TAP - Disinfection (primary) - Insufficient C.t Insufficient C.t due to: - low chlorine - high pH due to incorrect Stabilisation pH control - insufficient contact time - high treated water turbidity Risk Medium (8) Target risk (5) | Risk Treatment: Calculate C.t and ensure that it is adequate through suitable controls including critical alarms/interlocks. C.t calculation currently includes councils town reservoir located near Amity WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-06-30 09:00 | Completed | Update R.A 2015: C.t is currently not met at the BSP. WTP Planning preparing a draft options assessment report. Update R.A 2017: Concept design complete to achieve C.t and BSP. Consultant engaged. Preliminary design complete. Update R.A 2019: Amity Point WTP has been assessed as Source Category 2 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 3.0 LRV under WSAA HBT Manual. Minimum C.t 8 mg.min/L required to achieve 3.0 LRV virus. PID01902 TAP: Upgrade CWS Tank Capacity - improve contact time and instrumentation for disinfection in delivery for 20/21 21/22. Ref APMP 2019. Update 26/03/2020: Amity Point C.t Options being reviewed. Stakeholder meeting 23/03/2020. Lead WTP Planning leading. | Senior DWQ Advisor - South | 2017-11-21 09:00 | Senior DWQ Advisor - South | Y
Dunwich WTP | South | 11292 | TDU-RW-A 11292 Risk Treatment: Undertake Health Based Target assessment of NSI Township WTPs and upgrade WTPs accordingly. | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: Risk: Medium (8) Target Risk: Medium (5) - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-12-31 | In progress |  | Senior DWQ Advisor - South | 2017-11-21 | Senior DWQ Advisor - South | N
Dunwich WTP | South | 11293 | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore 'Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: '- Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk: Medium (8) Target Risk: Medium (5) | Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned Risk Treatment (raised R.A 2017): Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity (raised HACCP internal audit 2016) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-06-30 09:00 | Completed | Upgrade R.A 2019: ION raised. Ingress issued fixed on production bores 2018/2019? Ongoing inspections to be addressed. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Update 15/05/2020: ION01367 has been raised to install online raw water turbidity monitoring for the purpose of detecting abstraction of contaminated ground water that exceeds treatment capacity. | Senior DWQ Advisor - South | 2017-11-21 09:00 | Senior DWQ Advisor - South | Y
Dunwich WTP | South | 11296 | TDU - Media Filtration - Contamination by ingress Contamination of Media Filter Risk: Medium (8) Target Risk: Medium (5) | Risk Treatment (raised R.A 2019): install adequate cover on top of filter | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-06-30 09:00 | Completed |  | Senior DWQ Advisor - South | 2019-08-07 09:00 | Senior DWQ Advisor - South | Y
Dunwish WTP | South | 11297 | TDU-RW-A-11297 Risk Treatment: Investigate options to meet C.t. Will need to liaise with Redlands due to 'change' that customers will receive in free chlorine levels. Options could include increasing min res level. If not able to be reasonably achieved operationally then issue to be handed over to Planning. | TDU-RW-A-11297 Risk Treatment: Investigate options to meet C.t. Will need to liaise with Redlands due to 'change' that customers will receive in free chlorine levels. Options could include increasing min res level. If not able to be reasonably achieved operationally then issue to be handed over to Planning. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-06-30 | In progress | Update R.A 2019: WTP Planning developing Dunwich WTP Pathogen Contamination Mitigation Preliminary Business Case to address pathogen treatment requirements. Update 26/03/2020: Virus and bacteria log shortfalls being addressed under TDU – Dunwich WTP Secondary Disinfection Preliminary BC | Senior DWQ Advisor - Continuous Improvement | 2020-01-24 | Senior DWQ Advisor - South | N
Point Lookout WTP | South | 11308 | TPL-RW-A-11308 Risk Treatment: Remove CCT bypass | TPL - Disinfection (primary) - Failure or incorrect operation of a bypass valve Failure or incorrect operation of treated water reservoir bypass (dosed water to balance tank to treated water pumps) Risk: Medium (8) Target Risk: Medium (5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-06-30 | In progress | Bypass exists on outlet of 45 kL tank bypassing treated water reservoir. Refer REX 724654 Drawing I-DWG-TPL-601 PID Treated Water Storage. Update R.A 2019: Bypass valve closed 2019. ION raised for valve and intermediate balance tank to be removed. ION00430 | Senior DWQ Advisor - Continuous Improvement | 2020-01-24 | Senior DWQ Advisor - South | N
North Stradbroke Island WTP | South | 11389 | TNS - Coagulation - Incorrect Incorrect Coagulant dose. For Herring Lagoon: Overdose of alum leading to ineffective coagulation For Bores: N/A. Bore water does not pass through Coagulation Process Step Medium (8). (NSI-8 & NSI-13) | Risk Treatment (raised R.A 2018): review anti syphon assets at NSI WTP. Are they effective to mitigate syphon risk. Refer alum dosing pump standard. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-06-30 09:00 | Completed |  | Senior DWQ Advisor - South | 2015-01-28 09:00 | Senior DWQ Advisor - South | Y
Noosa WTP | North | 11397 | TNO- Raw Water Abstraction- Rain event in catchment Contaminant load exceeds treatment capacity Medium (8). (due to crypto short fall) | Risk Treatment (raised R.A 2019): Online visibility at the Mary river and Lake Macdonald intakes is required to enable real time source selection. This could be achieved by using existing remote catchment monitoring devices currently stationed at Coles Crossing(Mary River Intake) and Lake Macdonald, which monitor turbidity, pH conductivity, temperature and dissolved oxygen. Alternatively analyser racks could be installed at both of these intakes. Either option must have the signals from these analysers fed back to SCADA. Long term planning should be looking to add another cryptosporidium barrier such as UV in order to meet the required log credits under the HBT assessment. Update 2021 RA: Long term planning should be looking to add another cryptosporidium barrier to meet the required log credits under the HBT assessment. - contunied development (2021 ra) (create new RW for higher priority) - roll into a tier 1.5 assessment /QMRA for noosa (done before next RA (so <2 years from july 2021) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2023-07-01 09:00 | Completed |  | Senior DWQ Advisor - North | 2019-07-17 09:00 | Senior DWQ Advisor - North | Y
Noosa WTP | North | 11398 | TNO- Coagulation Incorrect lime dose Non-optimised coagulation Medium (8). (due to crypto short fall) | Risk Treatment (raised R.A 2019): investigate lime and alum control with focus on start up and lake only water investigate poly as a floc/settling aid install alum dosing flow meter to verify alum dose investigate CO2 dosing to enable formation of calcium carbonate to a higher degree of reliability includine reactivator importance in coag pH validation and control | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | Completed |  | Senior DWQ Advisor - North | 2019-07-17 09:00 | Senior DWQ Advisor - North | Y
Noosa WTP | North | 11401 | TNO- Media Filtration Filter breakthrough Potential contamination of treated water Medium (8). from crypto short fall | Risk Treatment (raised R.A 2019): Install appropriate instrumentation, monitoring and control systems to enable effective monitoring and control of filtration. Install /improve filter to waste option (2021: filter to waste operational on timers) Investigate poly dosing as a filter-aid. - potential to introduce air scour (2021: completed) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | Completed | raised 2021: link to 11397 Long term planning should be looking to add another cryptosporidium barrier to meet the required log credits under the HBT assessment. - contunied development (2021 ra) (create new RW for higher priority) - roll into a tier 1.5 assessment /QMRA for noosa (done before next RA (so <2 years from july 2021) | Senior DWQ Advisor - North | 2019-07-17 09:00 | Senior DWQ Advisor - North | Y
Kooralbyn WTP | South | 11738 | TKO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TKO-16) | Risk Treatment (raised 2020): low raw water pH HACCP action limit to detect change in pH when on Bigfoot Lagoon. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed |  | Senior DWQ Advisor - South | 2020-05-20 09:00 | Senior DWQ Advisor - South | Y
Kooralbyn WTP | South | 11740 | TKO - Media Filtration- Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (8) (KOO13) | Risk Treatment (raised R.A review 2020): clarify filtered water turbidity asessmen for HBT assessment. E.g four filters or two filters | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed |  | Senior DWQ Advisor - South | 2020-05-20 09:00 | Senior DWQ Advisor - South | Y
Image Flat WTP | North | 11747 | TIF - Raw Water Abstraction Rain event in catchment Increased contaminant loads due to wash-in from the catchments, resulting in contaminated treated water High (12). | Risk Treatment (raised R.A 2020): The plant is difficult to operate, thus the likelihood of failure is higher, leading to the higher risk score. Whilst historical data shows the operators have been able to run the plant effectively, there is grave concern about the ongoing operability of particularly the coagulation and filtration barriers. Therefore, an additional Prozoa Treatment barrier is required to address the shortfall against the HBT tier 1 assessment. All sources are HBT Category 4 and so source selection alone is not good enough to mitigate the shortfall. Consideration should be given to -> Quantitative/tier 2 HBT assessment -> real-time water quality and flow monitoring of raw water sources. This will give the operators the ability to chose the most treatable source and consequently mitigate the associated hazards. If the operators had the capacity to see the change in the river in real time, they could move to Wappa, which has some buffer from the rain, or Poona, if manganese and taste and odour are accounted for. -> Lime dosing system improvement to account for colour and alkalinity from the river and wappa ->Alum Mixing improvement | Risk Assessment | High | 12 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11748 | TIF - Raw Water Abstraction Change in raw water source Contaminant load exceeds treatment capacity (T&O) Medium (9). | Risk Treatment (raised R.A 2020): There is a risk around feed from Wappa Dam direct to plant due to issues with Mn. Valves are physically locked and require a manual changeover to access the Wappa source. Source selection procedures consider the level of all storages and consideration of depth samples on dams is taken into account to assess WQ in conjunction with catchments, intake weir and dams. Therefore, consideration to be given to taste and odour treatment improvements (there is an existing project in place to upgrade PAC dosing plant, but this will only assist in operatability and not in the reduction of TO) and manganese treatment options (there is a BC proposed for reinstating potperm dosing - however it is unlikely to go ahead due to budget constraints). Manganese treatment options would greatly improve the operatability of the plant as if manganese could be dealt with effectively during a TO bloom then the sources can be switched to deal with the manganese. This is currently unavailable and as such most of the time the all of sources cannot be treated effectively | Risk Assessment | Medium | 9 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11749 | TIF - Raw Water Abstraction Change in raw water source Increased contamination load leading to contamination of treated water (T&O) Medium (9). | Risk Treatment (raised R.A 2020): Short term improvements in the taste and odour treatment capability like an ability to batch more PAC (project to upgrade PAC), moving the PAC dosing line further upstream (part of PAC upgrade project), enhanced coagulation to remove intracellular algae prior to the release of the taste and odour compounds (jar tests have shown that up to 70% of 2-metylisoborneol can be intracellular and thus easily be treated with traditional coagulation + filtration). monitoring filter run times - it has been shown that if the filters are left to run too long before a backwash occurs then some taste and odour produces are able to become entrained and release the taste and odour compounds to the filtrate where it is chlorinated (and thus biodegredation can take longer) .Further to this an Ultrasonic device placed in Poona has been found to have a significant impact on the rate of MIB events in Poona and is recommended as a potential intervention into the high geosmin that occurs in Wappa. Additional simple interventions include identifying and preventing or improving sources of nutrients to Poona, such as local industry or the centrifuge centrate (current position is best of the worst case) | Risk Assessment | Medium | 9 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11750 | TIF - Supernatant Return Superntatnt return quality exceeds treatment capacity Increased contaminant load Medium (8). | Risk Treatment (raised R.A 2020): Additional monitoring of the supernatant return for pathogens, nutrients, algae and toxins could identify precursory issues and prevent risks from becoming realised. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11751 | TIF - Powdered Activated Carbon (PAC) Insufficient PAC dose Contamination of treated water Medium (9). | Risk Treatment (raised R.A 2020): long term planning initiatives to enhnced taste and odour treatment capability such as - membrane bioreactor, ozone/bac and/or advanced oxidation could be considered as a potential extra treatment processes to deal with the extremely elevated MIB concentrations experienced in Poona (>1800 ng/L). Other long term planning options to directly intervene with the Poona system are also under consideration. (in the process of starting a strategic business case looking at the northern treatment requirements) | Risk Assessment | Medium | 9 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11752 | TIF - Coagulation Incorrect lime dose Incorrect pH High (12). | Risk Treatment (raised R.A 2020): The lime clarifier system has issues with dosing pump turndown rates - essentially the dosing pumps are too big for the amount of water that is usually being treated by image. The temporary soda ash dosing system put in place several years ago has been restored in order to assist with the additional alkalinity required and at the lower flow that the plant is producing. A long term solution to this problem is to provide another set of dosing pumps that can meet the required turn down for the lower plant production (but also be able to meet the requirements of the high production expected when lake macdonald is taken offline circa 2021-2022) | Risk Assessment | High | 12 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11753 | TIF - Flocculation and Settling Carryonver of floc, sludge or algae in settled water This leads to overloading of the filter and probable filter break through Medium (8). | Risk Treatment (raised R.A 2020): Currently there is only one online settled water instrument for each plant -a single online turbidity analyser on clarifier 3 and a single analyser on the outlet of clarifier 1 that "theoretically" represents the settled water coming off both clarifiers 1 and 2. Adding a third settled water analyser on the outlet of clarifier 2 would enhance operator visibility and early detection of issues as well as enable the operators to measure more accurately individual clarifier performance. (already on the minor works list) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11754 | TIF - Media Filtration Filter breakthrough Potential contamination of treated water Medium (8). | Risk Treatment (raised R.A 2020): 'Filter Master Valve Replacement - the master valves have been replaced an automated however they still occasionally become misaligned. This could be accounted for by an ongoing pro-active maintenance program. (closed - 12 monthly inspection/work order) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11755 | TIF - Disinfection (primary) Insufficient C.t Failure to eliminate chlorine sensitive contaminants Medium (8). | Risk Treatment (raised R.A 2020): Investigate control options for real time C.t. Real time (dynamic) Ct has been installed and is trended and alarmed, however trimming the dose to accommodate the various flow directions (NPI can backfeed to both reservoirs via the nambour offtake) is very difficult. Recommend detailed investigation into options to enable full control over real time Ct. Also of note is the number of mains breaks that occur in the region regularly. Since image flat is a gravity plant, if there is a break, all image can do is not produce water . However this leads to a bad position for recovery (as the reservoir is never "offline"). Recommend a detailed recovery plan to be developed for mains break situations (involving backfeeding from nambour) - draft recovery plan REX ID: XX/XXXX) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11756 | TIF - Disinfection (primary) Contamination by animals Bird and animal droppings contaminating the treated water. Medium (8). | Risk Treatment (raised R.A 2020): Vermin proofing has been undertaken at image flat. A GHD report into the status of the reservoirs has been undertaken (ongoing inspection maintenance inspections - work order/12months) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Image Flat WTP | North | 11757 | TIF - Whole of System Loss of control system Loss of control system Medium (8). | Risk Treatment (raised R.A 2020): 'There is a separate UPS for plant and fluoride PLCs. This has been tested regularly to ensure it can achieve a minimum of 30 minutess power in the event of an outage, giving operators time to react to the power loss. Further, as the Wappa pumpstation draws power from a source independent of the plant, there is a potential for there to be a powerloss at the plant and continued pumping from wappa to the aerators. Since the plant runs on gravity from then there is a potential for the plant to continue operating without dosing. A tactical asset maintenance investigation must be undertaken to remediate the risk of raw water from Wappa going to the plant in the event of a powerloss. An almost identicial situation occured at the old petrie water treatment plant (though in the case of petrie, it was not a gravity plant and so no water left site), where the raw water pump station was on an independent supply to the plant, the plant had ups for the scada and plc (nb - that does not include dosing), and the clarifiers become inundated with uncoagulated water. If a similar series of events were to occur at image flat there is a potential for the water to go through the entire plant and subsequently a much higher risk. NB backup generators can run site completely except for supernatant. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-04-27 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-04-27 09:00 | Senior DWQ Advisor - North | Y
Ewen Maddock WTP | North | 11760 | TEM - Raw Water Abstraction Rain event in catchment Contaminant load exceeds treatment capacity Medium (8). | Risk Treatment (raised R.A 2020): 'Undertake HBT Tier 1.5 Assessment to confirm risk | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-01-17 09:00 | Senior DWQ Advisor - North | Y
Ewen Maddock WTP | North | 11761 | TEM - Raw Water Abstraction Dam turnover Contaminant load exceeds treatment capacity (manganese) Medium (8). | Risk Treatment (raised R.A 2020): The potperm dosing system was moved further upstream and this has assisted with the reduction in manganese and iron. Investigate the option of airation to reduce the iron (which preferentially oxidises over manganese). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-01-17 09:00 | Senior DWQ Advisor - North | Y
Ewen Maddock WTP | North | 11762 | TEM - Coagulation Incorrect lime dose Coagulation process failure Medium (8). | Risk Treatment (raised R.A 2020): Review of pre lime dosing system to include the following: - Not use raw water as service water for pre-lime (still in use - because its prior to treatment) - Change lime makeup water to plant service water instead of raw water (still in use - because its prior to treatment) - Pressure switches on lime makeup water (Mike Burns to check) - Auto shutdown on lime system failure (In place - close out) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-01-17 09:00 | Senior DWQ Advisor - North | Y
Ewen Maddock WTP | North | 11763 | TEM - Supernatant Return Change in raw water source Contamination of treated water Medium (8). | Risk Treatment (raised R.A 2020): ' VSD for the separated water return pumps the return water tank | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-01-17 09:00 | Senior DWQ Advisor - North | Y
Ewen Maddock WTP | North | 11764 | TEM -Supernatant Return Stormwater entering the process Contamination of treated water Medium (8). | Risk Treatment (raised R.A 2020): Online turbidity and pH instruments to be installed on supernatant return line | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-01-17 09:00 | Senior DWQ Advisor - North | Y
Ewen Maddock WTP | North | 11765 | TEM -Ozone (intermediate) Contamination incident - accidental/intentional Introduction of pathogens Medium (8). | Risk Treatment (raised R.A 2020): 'Erect contamination signage on/at the BAC filters. Work instructions for working over the BAC should also consider the risk of accidental contamination | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-01-17 09:00 | Senior DWQ Advisor - North | Y
Ewen Maddock WTP | North | 11766 | TEM -Ozone (intermediate) Contamination incident - accidental/intentional Introduction of pathogens Medium (8). | Risk Treatment (raised R.A 2020): Investigate further prevention of post barrier contamination to the top of the BAC filters (such as ingress, animals, etc). Covering BACs completely is challenging because of the residual ozone present in the atmosphere. Ozone is heavier than air and invisible to the eye. People and animals can become intoxicated quickly if there is too much ozone in the air. However, there is a potential for contamination of the water on top of the BAC filters (water that has just been ozonated). BAC filters do not provide any log reduction credits for protozoa and as such effectively, anything that contaminates the ozonated water prior to BAC filtration could potentially make its way through to the treated water and the public. There are no further barriers to protozoan. Chlorine disinfection does not get any impact on protozoan parasites. Therefore it is imperitive to - ensure there is no ingress points to the ozonated water prior to BAC and provide an additional treatment barrier for protozoa downstream of the BAC. (not in place yet. but speaking to extra protozoan barriers ala other protozoan limiting hazard risk treatments, as well as reducing the likelihood of introducing contamination to the BACs) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-01-17 09:00 | Senior DWQ Advisor - North | Y
Maroon Dam WTP | South | 11773 | TMD - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - low pH in raw water Medium (8) | Risk Treatement (raised R.A review 2020): Investigate causes and opportunities to prevent alum dosing system blockages. P.E investigating options to address mixing/blockage issue e.g swap out devices. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update 28/09/2020: PE unable to progress at this time. Operations are trialing a double contained tubing with an expected longer shelf life. | Senior DWQ Advisor - South | 2019-03-08 09:00 | Senior DWQ Advisor - South | Y
Moogerah WTP | South | 11775 | TMG - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - high pH Medium (8) | Risk Treatment (raised R.A review 2020): Investigate causes and opportunities to prevent alum dosing system blockages. Refer HACCP Critical Limit excursion RW incident 6526. P.E investigating options to prevent blockages e.g earthing of static mixer. Operations supervisor to initiate 3 monthly work order for swap out/replacement of alum dosing line. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed | Update 28/09/2020: PE unable to progress at this time. Operations are trialing a double contained tubing with an expected longer shelf life. | Senior DWQ Advisor - South | 2020-02-28 09:00 | Senior DWQ Advisor - South | Y
Rathdowney WTP | South | 11777 | TRA - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) | Risk Treatment (raised R.A 2020): D15/114408 Rathdowney WTP Pathogen Assessment did not assess performance data for bacteria/virus log credits. It was considered likely that filtration performance is sufficient at Rathdowney WTP to consistently achieve 1 log reduction for bacteria and viruses. However, due to the known floc carryover (poor settling) issues with the use of Magnasol 589 it is considered likely that no credit for settling would be achieved. Bacteria/Virus 6 LRV required: WTP process has capacity to achieve 0 log coag/floc settling, 1 log media filtration, 4 log disinfection primary (min C.t 15 mg.min/L based on pH >8). Total 5.0 LRV. 1 log bacteria/virus shortfall. ACH trial commenced 26/8/2019 and settled water turbidity has improved. Undertake performance assessment to determine log credits for protozoa and bacteria/virus through coag/floc/settling and filtration process steps. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed |  | Senior DWQ Advisor - South | 2020-06-03 09:00 | Senior DWQ Advisor - South | Y
Rathdowney WTP | South | 11781 | TRA - Supernatant Return - Supernatant return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose Medium (8) | Risk Treatment (raised R.A 2020): updates to control system to divert first volume of supernatant return flow to overflow lagoon to address high turbidity on pump start. Process Engineering to review existing logic to determine next steps e.g ION/FD update or SCADA request. Confirm functioning of valve to identify when turbidity high. If valve fails to close/open confirm the supernatant return pump interlock. 28/09/2020: HACCP critical limit excursion Risk Wizard 24410 confirmed supernatant return pumps do interlock if valve fails to close/open. Note: management of current solids handling and instrument flows exceeds WTP capacity to return rate. This issue is exaccerbated in summer. Operations Supervisor to follow up with Environment Team regarding state of issue. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-06-30 09:00 | Completed |  | Senior DWQ Advisor - South | 2020-06-03 09:00 | Senior DWQ Advisor - South | Y
Dayboro WTP | North | 11842 | TDY- Tankering (several hazardous events associated that are the precursor to tankering occurring) (nb will update timeframe when more info on project comes in) Medium (8). | Risk Treatment (raised R.A 2020): Tankering from Samford to Dayboro – operators previously have had to boost the chlorine manually due to the lower chlorine residual in the system – probably because of the high chlorine trial leading to issues with unitywater breakpointing. This was reported to the Queensland Water Supply Regulator. Taking it from north pine post chloramination would’ve required significantly more chlorine to breakpoint and likely reduced water quality comparitively. Propose build dedicated tankering facility at North Pine prior to chloramination, thus enabling permanent access to well controlled free chlorinated water. (Ray Corro) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | Completed |  | Senior DWQ Advisor - North | 2020-06-19 09:00 | Senior DWQ Advisor - North | Y
Mt Crosby Eastbank WTP | Central | 12001 | Eastbank WTP - Supernatant Return - Supernatant return quality exceeds treatment capacity. Supernatant return volumes exceed treatment capacity leading to Protozoa in the treated water. High (12) | 1). It should be determined if it would be advantageous to fit interlocks such that the supernatant pumps cannot run when the raw water pumps are offline or if the turbidity critical limit is triggered - Technical Specialist has identified that this would be advantageous. 2). Consideration should be given to undertaking a mass balance of polyacrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for acrylamide monomer in the treated water. 3). VSDs is to be installed on the supernatant return pumps which in conjunction with raw water flow meters will facilitate improved control to ensure that the supernatant to raw water ratio does not exceed 10% of the raw water flow rate. 4) Make modifications and improvements to the current supernatant return process to minimise the impact to stage 3 and 4 basins. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2025-12-26 09:00 | Completed | Refer to Eastbank Solids Handling Upgrade - CIS project code C201005427 for further information. | Senior DWQ Advisor - Central | 2020-07-15 09:00 | Senior DWQ Advisor - Central | Y
Supply System | Central | 12031 | Supply System - Reservoir - Elevated water age. Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. Medium (8) | Review options around performance, replacement and installation of reservoir mixers in Supply System. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 | Not yet started |  | Senior DWQ Advisor - Central | 2020-07-17 | Senior DWQ Advisor - Central | N
Supply System | Central | 12033 | Supply System - Disinfection (secondary) - Incorrect chlorine dose Under dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water. High (12) | NPI Supply Zone 1. Conduct Process Assessment of Noosa Connection dosing system. 2. Conduct Process Assessment of Caloundra Street WQMF dosing systems. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2025-07-01 | Not yet started |  | Senior DWQ Advisor - Central | 2020-07-20 | Senior DWQ Advisor - Central | N
Supply System | Central | 12034 | Supply System - Disinfection (secondary) - Incorrect ammonia dose. Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water. Medium (8) | Brisbane Supply Zone Implement recommendations from Mt Crosby ICAM investigation for ammonia failure. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-01-31 | In progress | Refer D19/173039 ICAM Investigation Brisbane, Ipswich and Logan Supply Areas Free Chlorinated Water (06/08/19). Individual actions have been identified in this report. Please refer to this for further information and Risk Wizard Actions. All actions investigated.. | Senior DWQ Advisor - Central | 2020-07-20 | Senior DWQ Advisor - Central | N
Supply System | Central | 12035 | Supply System - Disinfection (secondary) - Incorrect ammonia dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water. Medium (8) | NPI Supply Zone Conduct Process Assessment of Caloundra Street WQMF dosing systems. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-12-16 | Not yet started |  | Senior DWQ Advisor - Central | 2020-07-20 | Senior DWQ Advisor - Central | N
Supply System | Central | 12036 | Supply System - Whole of System - Inaccurate online instruments Due to: - maintenance practices/activities; - sample line issues; - instrument and component failure. leading to - potential under or overdosing of treatment chemicals; - failure to notifiy the Control Room of water quailty issues or failures in the system. Medium (8) | Redland Supply Zone Implementation of updated PRO-02120 Corporate HACCP - Management of WQ Online instruments Procedure which now incorporates wet rack cleaning. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-01-31 | Not yet started |  | Senior DWQ Advisor - Central | 2020-07-20 | Senior DWQ Advisor - Central | N
Maroon Dam WTP | South | 12073 | TMD - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - low pH in raw water Medium (8) | Risk Treatment (raised 2020): commence daily settled water UV254 monitoring for the purpose of determining | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2021-06-30 | Completed | Status update 28/09/2020: Process Laboratory to provide instrument capable of monitoring UV254, provide all consumables needed and supply training to competency of UV254 analysis. DWQA to update HACCP documents. | Senior DWQ Advisor - South | 2020-02-28 | Senior DWQ Advisor - South | Y
Maroon Dam WTP | South | 12074 | TMD - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMD-19) | Risk Treatment (raised R.A review 2020): investigate opportunities to mitigate sludge build up in settled water balance tank. WTP Operations to raise works request for inlet pipework modification to improve hydraulic mixing in tank. Trial at Moogerah WTP. | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 | In progress | Operators are familiar with UV254 monitoring as it is being performed at Kalbar WTP. | Senior DWQ Advisor - South | 2020-02-28 | DWQ Advisor - Continuous Improvement | N
Moogerah WTP | South | 12089 | TMG - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMG-15) | Risk Treatment (raised R.A 2020): relocate raw water analyser from raw water pumps at dam to inlet to raw water balance tank as per Maroon Dam WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-02-28 | In progress | 29/8/2022 completed and working well. | Senior DWQ Advisor - South | 2017-09-06 | Senior DWQ Advisor - South | N
Moogerah WTP | South | 12090 | TMG - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - high pH Medium (8) | Risk Treatment (raised 2020): commence daily dosed filtered UV254 monitoring for the purpose of UV disinfection | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2021-06-30 | Completed | UV 254 monitoring implemented. | Senior DWQ Advisor - South | 2020-02-28 | Senior DWQ Advisor - South | Y
Moogerah WTP | South | 12091 | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) | Risk Treatment (raised R.A review 2020): investigate opportunities to mitigate sludge build up in settled water balance tank. WTP Operations to raise works request for inlet pipework modification to improve hydraulic mixing in tank. Trial at Moogerah WTP. | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 | In progress |  | Senior DWQ Advisor - South | 2017-09-06 | DWQ Advisor - Continuous Improvement | N
Hinze Dam WTP | South | 12154 | THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water Medium (8) (HNZ-5) | Risk Treatment (raised R.A review 2019): Instigate dial out alarm if raw water flow detected and WTP not running. SCADA work request or ION to be raised. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-12-31 | In progress |  | Senior DWQ Advisor - South | 2019-12-03 | Senior DWQ Advisor - Continuous Improvement | N
Kooralbyn WTP | South | 12161 | TKO - Coagulation - Incorrect coagulant dose Overdose of alum resulting in contaminated treated water including underdose of caustic Medium (8) (TKO-18) | Risk Treatment (raised R.A 2020): CO2 injection point delivered with alum dosing system however CO2 dosing system not delivered. CO2 system assessed as not being feasible. Coagulation process would benefit from acid dosing when running on Bigfoot Lagoon. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 | Not yet started |  | Senior DWQ Advisor - South | 2017-07-19 | Senior DWQ Advisor - South | N
Kooralbyn WTP | South | 12268 | TKR- Raw Water Abstraction Contaminant load exceeds treatment capacity Medium (8). (due to crypto short fall) | Risk Treatment (raised R.A 2020): Consider re-evaluating/conducting HBT tier 2/1.5 assessment to verify risk and investigate requirements for upgrades. Installation of UV is in the program to be delivered 2022 as part of the KKR project. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 | In progress | Consider re-evaluating/conducting HBT tier 2/1.5 assessment to verify risk and investigate requirments for upgrades. Installation of UV is in the program to be delivered 2022 as part of the KKR project. | Senior DWQ Advisor - North | 2019-07-17 | Senior DWQ Advisor - North | N
Jimna WTP | North | 12269 | TJI- Raw Water Abstraction Intake of raw water that exceeds the treatment capacity of the plant affecting treated water quality. Medium (8). (due to crypto short fall) | TJI- Raw Water Abstraction Intake of raw water that exceeds the treatment capacity of the plant affecting treated water quality. Medium (8). (due to crypto short fall) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 | In progress | Risk Treatment (raised R.A 2020): An additional Prozoa Treatment barrier is required to address the shortfall against the HBT tier 1 assessment. Alternatively investigation into a tier 1.5/2 assessment to verify the risk | Senior DWQ Advisor - North | 2019-07-17 | Senior DWQ Advisor - North | N
Capalaba WTP | South | 12505 | TCP - Disinfection (primary) - Insufficient C.t Formation of disinfection byproducts (DBPs) Medium (9) | Risk Treatment (raised HACCP team meeting Nov 2020): Capalaba WTP is producing water with high THMs that are expected to exceed the ADWG health guideline in the Redland supply system for zone supplied by Capalaba WTP. These results are being achieved despite enhanced coagulation and PAC dosing being applied at elevated doses beyond for which the system was designed. Process Engineering assessment: when considering raw water organics, Capalaba is the worst catchment in Seqwater. During the 2011 and 2013 floods and the Feb 2020 event DOC levels as high as 25mg/L are being recorded and treated water organics currently at a DOC >5mg/L being produced. The current Water Quality Partnership Plan has leading practice at < 3.5mg/L and action limit > 5mg/L. ION 1608 raised. | Risk Assessment | Medium | 9 | Senior DWQ Advisor - Continuous Improvement | 2023-06-30 09:00 | Completed |  | Senior DWQ Advisor - Continuous Improvement | 2020-11-09 09:00 | Senior DWQ Advisor - Continuous Improvement | Y
Landers Shute WTP | North | 12755 | Investigate a quantitative or semi quantitative estimate of the risk to improve the uncertainty and verify the challenge to the plant is correctly estimated by the HBT Tier 1 framework as category 4 requiring 5.5 log credits for protozoan treatment capability. | As discussed at the risk assessment on the 4th of march 2021, whilst Landers Shute has already been assessed under the HBT Tier 1 framework as Category 4 requiring 5.5 Log credits for protozoan treatment, the nature of the risk should be thoroughly understood and quantified as much as possible as it may lead to requiring capital upgrades at what is already an advanced water treatment plant. | Risk Assessment | Medium | 8 | CWQ Advisor - North | 2022-03-09 | Completed |  | Senior Supervisor CWQ | 2021-03-09 | Senior Supervisor CWQ | Y
Landers Shute WTP | North | 12756 | Investigate additional ongoing continuous improvements such as |  | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-06-30 | In progress |  | Senior DWQ Advisor - North | 2021-03-09 | Senior DWQ Advisor - Continuous Improvement | N
Landers Shute WTP | North | 12757 | Investigate the Cryptosporidium spp. log reduction capability of the intermediate ozonation step at Landers Shute | It has been theorised that the interozone can actually provide some log credits for crypto reduction (i.e. see section 8.6 of the SPE-00320 WTP and Supply System Process Validation Standard. The difficulty at Landers Shute system appears to be in the incapacity to be able to measure ozone effectively through the contactor. However, a more detailed investigation into this might reveal an improvement opportunity that can reclassify ozone as a primary barrier for Cryptosporidium spp. This would effectively mitigate the (estimated) short fall of 1.5 log under the HBT tier 1 assessment. | Risk Assessment | Medium | 8 | Lead Water Quality (Public Health) | 2022-03-09 09:00 | Completed |  | Senior DWQ Advisor - North | 2021-03-09 09:00 | Senior DWQ Advisor - North | Y
Lowood WTP | Central | 12845 | Central Region- Somerset South- Lowood WTP- HBT assessment | 16 June - Access to SCADA denied 21 June - Access to data issues in SCADA. Call logged by Hany for Kevin 2 July - Data issues resolved 5 July - Filtered water turbidity data gaps identified by Kevin and reported to Control System Engineers | Risk Assessment | Medium | 8 | Lead Process Engineer - central | 2021-12-31 09:00 | Completed |  | DWQ Advisor - Continuous Improvement | 2021-04-06 09:00 | DWQ Advisor - Continuous Improvement | Y
Lowood Intake Raw Water Pump Station | Central | 12894 | Central Region- Somerset South- Lowood WTP- place back up generator at raw water PS | There is a project in planning stage including the placement of a generator at the raw water PS | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-12-30 | Completed |  | DWQ Advisor - Continuous Improvement | 2021-04-19 09:00 | DWQ Advisor - Continuous Improvement | Y
Lowood WTP | Central | 12897 | Central Region- Somerset South- Lowood WTP- installation of UV to implement additional barrier to meet log removal requirements for protozoans | Project is in planning stage and delivery scheduled for 2021/ 2022 | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2022-05-31 09:00 | Completed |  | DWQ Advisor - Continuous Improvement | 2021-04-19 09:00 | DWQ Advisor - Continuous Improvement | Y
Lowood WTP | Central | 12899 | Central Region- Somerset South- Lowood WTP- Validate and document inhibit timeframe for turbidity instruments. | Review current instrument locations, analysers locations and instrument type to ensure timely and accurate monitoring. | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2022-04-30 09:00 | Completed |  | DWQ Advisor - Continuous Improvement | 2021-04-19 09:00 | DWQ Advisor - Continuous Improvement | Y
Lowood WTP | Central | 12900 | Central Region- Somerset South- Lowood WTP- additional clarifier to mitigate supply and water water quality risks | Additional clarifier is in delivery stage | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2022-04-30 09:00 | Completed |  | DWQ Advisor - Continuous Improvement | 2021-04-19 09:00 | DWQ Advisor - Continuous Improvement | Y
Molendinar WTP | South | 13006 | TMO-RW-A-13006 Risk Treatment: To 1) determine monitoring and alarming to detect high level in the backwash overflow chamber and determine a subsequent response and recovery plan, and 2) progress infrastructure changes required to prevent high level in the backwash overflow chamber. | Refer linked incident. Assigned to WTP Operations Supervisor and WTP Operations Coordinator and team. Prevention of overflow to CCT will require infrastructure change therefore this would require ION or the new EAR (Emerging Asset Risk) process. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-07-31 09:00 | Completed | MoC process to be followed and drawings updated. Will need to be commissioned hydraulically to demonstrate effectiveness in order to close out risk treatment item. In addition, to improve detection of an overflow event, investigate multitrode option. This will enable early determination to drain CCT. 26/11/2021 Works request raised to have reliable alarming with a High and HighHigh system in place using a Multitrode | Senior DWQ Advisor - South | 2021-04-30 09:00 | Senior DWQ Advisor - South | Y
Jimna WTP | North | 13087 | TJI- Disinfection (primary) - Formation of disinfection byproducts (DBPs) - Addition of contaminants impacting upon treated water quality. Medium (9) | Improve coagulation efficacy at Jimna to reduce the likelihood of forming THMs in the network above the guideline values. | Risk Assessment | Medium | 9 | Senior DWQ Advisor - North | 2022-01-01 | Completed |  | Senior DWQ Advisor - North | 2020-08-31 | Senior DWQ Advisor - North | Y
Mt Crosby Eastbank WTP | Central | 13242 | East Bank WTP - Media Filtration - Filter Breakthrough (Medium 8) | Review more data related to new filter performance. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-06-30 09:00 | Completed |  | Senior DWQ Advisor - Central | 2021-08-12 09:38 | Senior DWQ Advisor - Central | Y
Mt Crosby Eastbank WTP | Central | 13243 | Mt Crosby Holts Hill - Disinfection (Secondary) - Incorrect Ammonia Dose - Under dosing of ammonia. (Medium 8) | Planned Ammonia upgrade works for Holts Hill | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-06-30 09:00 | Completed | 1. New ammonia ring main. Replacement of all valves. Flexible hose on dosing tank to ring main replaced. Completed 2. Ammonia dosing tank to be replaced. Stage 2 replacing tank, Design Only Contract awarded to Aurecon. Project currently in design stage. Construct contract PC 30/6/22 | Senior DWQ Advisor - Central | 2021-08-12 09:55 | Senior DWQ Advisor - Central | Y
Mt Crosby Eastbank WTP | Central | 13244 | East Bank WTP - Whole of System - Loss of SCADA system or loss of PLC (Medium 8) | Upgrade of system platform across all sites. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-12-31 09:00 | Completed | Training for operations or Manual? | Senior DWQ Advisor - Central | 2021-08-12 10:27 | Senior DWQ Advisor - Central | Y
Landers Shute WTP | North | 13523 | Investigate options for control of biomass growth in filters. - pre ozonation replacement project including prefilter chlorine - project underway - plant trials underway. Still in asset planning. | There is a common outlet channel. No individual flow meters. Filter control valve position is displayed on the SCADA. There is a setpoint for filter control rate which determines if filters come on or off. Filter rate control mode is auto or manual. All filters that are to be backwashed go offline and into a queue. This step is followed by inter ozone, BAC filtration and disinfection. super chlorination no longer used. operations to drain and dry filters for fungi removal is done when production periods allow. - Filtered Water Turbidity - Out of 2190 samples, the minimum was 0.011 NTU the 5th percentile was 0.04 (0.04, 0.04) NTU, the mean was 0.071 (0.07, 0.072) NTU, the 95th percentile was 0.12 (0.11, 0.12) NTU and the maximum result was 0.55 NTU. σ = 0.0266 (0.0258,0.0274). Data:Jan-2015 to Jan-2021. 95% Confidence Intervals in brackets. Presently - In the event of breakthrough: the inlet will close and the filter will go into autobackwash. The volume of the filter will still pass through the broken filter should this occur. Ideally, the outlet should close and the filter should drain to waste/SWR. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-12-14 | Completed |  | Senior DWQ Advisor - North | 2026-12-14 | Senior DWQ Advisor - North | Y
Landers Shute WTP | North | 13524 | Investigate options for collection of chemical waste from site labs. (Complete) install turbidity and pH instrument on return water line. ( see ION https://waternet.corporate.local/forms/Pages/ION.aspx?formId=458) Improvement to stop >10% seperated water return. MOC: https://waternet.corporate.local/forms/Pages/ION.aspx?formId=479 Alysha - mass balance acrylamide - potential for contamination | The following feeds back to the head of the plant in the separated water return: Centrate, thickener superantant, backwash recovery supernatant, BAC ripening filter to waste, polishing lagoon, headwall stormwater, analyser sample water, chemical spills from headwall, lab sink waste. - Residual lime and poly dosing is undertaken in this step; - Filter clogging algae numbers can increase quickly in the separated water return and this water is returned to the head of the plant . No turbidity or pH monitoring on the seperated water return. Flow can be monitored. intent is to introduce poly as a flocc aid to turn off or limit pre ozone. This can introduce the potential for contamination with acrylamide. Ozone is an effective barrier for acrylamide, so there shouldnt be an excess risk, as long as ozone is operational. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-12-14 | Completed |  | Senior DWQ Advisor - North | 2026-12-14 | Senior DWQ Advisor - North | Y

## Overarching DWQMP
Drinking Water Quality Improvement Plan - Overarching DWQMP and Supporting Programs
Site | Improvement # | Other Ref | Process Step | Issue | Description | Origin of Improvement | Significant Risk | Responsibility | Due for completion | Completed? Y/N | Comments
All WTPs with UV | DWQ1 | DWQ1 | UV Disinfection | UV System Alarming | Investigate the risk of mercury contamination due to UV lamp breakage and apply the findings to the 2017 risk assessment reviews for those plants that have UV disinfection. | Research | N/A | D. Middleton | 2017-01-31 | Y | Investigation completed. Past on to DWQ Coordinators. Risk is site specific.
Overarching | DWQ2 | Aquality A1.1 | Supporting Programs | A1.1 New CEO (after commencement) person to sign WQ Policy. Updated document to go on Q-Pulse and WTP/SS sites (office/foyers) |  | Aquality | N/A | Governance, Compliance & Internal Audit | 2020-06-30 | Y | Update30 June 2020: New water quality policy endorsed by CEO and Board 28 January 2020. Displayed at WTP and SS sites.
Overarching | DWQ3 | Aquality A1.2 | Supporting Programs | A1.2 Ongoing rollout of CRM across relevant sections of Seqwater |  | Aquality | N/A | Manager, Community Relations | 2016-12-31 | Y | Ongoing roll out program. Achieved. No in continuous improvement.
Overarching | DWQ4 | Aquality A2.1 | Supporting Programs | A2.1 Catchment modelling training for Wivenhoe and Northpine. This will reduce reliance on external consultants. The catchment modelling isn't necessarily water quality based, but can be used to model differing scenarios. |  | Aquality | N/A | Morag Stewart, SPPU | 2016-12-31 | Y | Completed. Point of contact Chris Thompson
Overarching | DWQ5 | Aquality A2.2 | Supporting Programs | A2.2 A new Water Quality Data Solution (i.e. LIMS) is being procured to replace LIMS1, which better supports Seqwater's water quality data needs and internal laboratory system management. This new LIMS will continue data integration from the multiple historic systems, with the exception of WISKI data, and be a key facilitator to the capture of Operator grab sample data in to a water quality database (refer to A10.3). |  | Aquality | N/A | Manager Techncical Support and Improvement | 2021-12-31 | Y | New LIMS (Labware) commissioned and in use.
Overarching | DWQ6 | Aquality A2.3 | Supporting Programs | A2.3 Improvement - prioritised input into the Asset Planning process (well underway) |  | Aquality | N/A | Duncan Middleton / Brian Hester | 2016-12-31 | Y | Completed. A prioritised system now implemented. WQ reports informing asset investment are now utilised by asset planning to prioritise upgrades and other works.
Overarching | DWQ7 | Aquality A2.4 | Supporting Programs | A2.4 Procedure/trigger in our RA process where risks or high uncertainties are brought to the attention of the health authority; either from an event or routine process. |  | Aquality | N/A | Duncan Shillito | 2017-12-31 | Y | 2017 Risk Assessment schedule completed
Overarching | DWQ8 | Aquality A4.1 | Supporting Programs | A4.1 Resource and develop operations manuals and supporting procedures |  | Aquality | N/A | Operational Excellence Lead | 2024-06-30 | N | Update: Due date extended due to review of project requirements. Roll out time frame for all operations manuals to be defined.
Overarching | DWQ9 | Aquality A4.2 Aquality A4.3 | Supporting Programs | A4.2 Recording operator competency TNA implementation actions A4.3 Need to investigate if lapses in HACCP reporting occurring |  | Aquality | N/A | Dan Healy, DWQ | 2018-12-31 | Y | Completed by Learning OD HACCP excursion confidence is current high
Overarching | DWQ10 | Aquality A4.4 | Supporting Programs | A4.4 Moving to a commercial-of-the-shelf database system (e.g. WIMS or using CIS) |  | Aquality | N/A | TBC | TBC | Y | Refer to the LIMS line item above - bringing systems together
Overarching | DWQ11 | Aquality A4.5 Aquality A4.6 | Supporting Programs | A4.5 Support operations staff update plant data sheets with conditional formating for key parameters A4.6 Standardising plant data sheets - plant data log project |  | Aquality | N/A | DWQ Regional Coords Frank Liu | 2016-12-31 | Y | Completed
Overarching | DWQ12 | Aquality A4.7 | Supporting Programs | A4.7 After hours sampling - needs to be addressed with staff issues, equipment and ability to perform sampling in aderse weather (purpose built ute set up), availaility (using Brisbane SAS lab) |  | Aquality | N/A | Kelvin O'Halloran | 2016-12-31 | Y | Completed. AH sampling arrangements in place. Sampling requests through an online form has been established.
Overarching | DWQ13 | Aquality A4.8 | Supporting Programs | A4.8 Investigation procedure/process (prevent recurrence) |  | Aquality | N/A | Helen Warburton | 2016-12-31 | Y | Completed. PRO-00793.
Overarching | DWQ14 | Aquality A4.9 | Supporting Programs | A4.9 Improve HACCP excursion reporting (by sub-region/HACCP region) |  | Aquality | N/A | Regional DWQ Coord | 2016-12-31 | Y | DWQ operator training completed
Overarching | DWQ15 | Aquality A4.10 | Supporting Programs | A4.10 Developing standards at the moment (Engineering support) - still ongoing Ensure standards etc are applied across business (no one is enforcing the standards that we already have developed). Consider use of variation requests/approvals. |  | Aquality | N/A | Dapo K Luke Hellowell Brian Hester | 2016-12-31 | Y | Well established standards library now exists. Ongoing improvement is occurring.
Overarching | DWQ16 | Aquality A4.11 | Supporting Programs | A4.11 Formulate the process from the instrumentation project - trial, acceptance and documentation handover can be improved |  | Aquality | N/A | Dapo K | 2016-12-31 | Y | Completed
Overarching | DWQ17 | Aquality A4.12 | Supporting Programs | A4.12 DWQ/IMS audits and review of accessibility of historical data and compliance |  | Aquality | N/A | Dan Healy Pierre van der Mere | 2016-12-31 | Y | All records are now entered into Risk Wizard database and can be reviewed there.
Overarching | DWQ18 | Aquality A4.13 | Supporting Programs | A4.13 Confirmation that alarm set points are correct and test to esnure they work |  | Aquality | N/A | Matt Bartholemew Dan Healy | 2016-12-31 | Y | Regular audit and interlock-maintenance testing schedules
Overarching | DWQ19 | Aquality A4.14 | Supporting Programs | A4.14 Follow up on Process assessments - process for getting improvements into Seqwater's various systems |  | Aquality | N/A | Principal Process Engineering | 2023-06-30 | N | Update: Due date extended. Improvement planning in progress to implement a project delivery prioritisation framework.
Overarching | DWQ20 | Aquality A4.15 | Supporting Programs | A4.15 Project handover / commissioning to include documentation, schedules and critical spares |  | Aquality | N/A | Brian Dagg John Gallea Kathleen Thatcher | 2016-12-31 | Y | Completed
Overarching | DWQ21 | Aquality A4.16 | Supporting Programs | A4.16 Determine whether analysers/meters need to be done consistently |  | Aquality | N/A | Manager Asset Management | 2019-12-31 | Y | Completed. Refer PRO-02120
Overarching | DWQ22 | Aquality A4.17 | Supporting Programs | A4.17 CIS records to be improved for strategic asset maintenance and operational record keeping - simplify the recording arrangement |  | Aquality | N/A | Manager Asset Management | 2019-12-31 | Y | Data capture using mobile platform is in place for Maintainers, simplifying the recording of required inforamtion.
Overarching | DWQ23 | Aquality A4.18 | Supporting Programs | A4.18 Improve processes for proactive budgeting and replacement of agining and failing equipment |  | Aquality | N/A | Manager Asset Management Manager Asset Planning | 2019-12-31 | Y | Issue & Opportunity Notification (ION) systems implemented and 3 year rolling asset renewal program. Management of Change process implemented
Overarching | DWQ24 | Aquality A4.19 | Supporting Programs | A4.19 Specify Interlock testing - not fully implemented other than fluoridation systems |  | Aquality | N/A | Duncan Shillito Dapo K | 2019-12-31 | Y | Maintenance program in place.
Overarching | DWQ25 | Aquality A4.20 | Supporting Programs | A4.20 Improve the supply and handling of small (20L) quantities to ensure they come from approved suppliers, fr e.g. disinfection SOPs for maintenance and project work when recomissioning assets |  | Aquality | N/A | Sonia Edwards | 2019-12-31 | Y | Disinfection procedures established. Chemical supply contractual arrangements weell established
Overarching | DWQ26 | Aquality A4.21 Aquality A4.22 | Supporting Programs | A4.21 Ensure compliance with standards tha are developed by ETS - projects, contracts and work orders A4.22 Add materials requirements to maintenance and project staff DWQ awareness training |  | Aquality | N/A | Luke Hellowell Dan Healy (training) | 2019-12-31 | Y | Refer DWQ15. DWQ training has a well established program with 2-yearly refresher training.
Overarching | DWQ27 | Aquality A4.23 | Supporting Programs | A4.23 Come up with a checking process that is achieveable with the current staff and recourses, for e.g. using LIMS by having uploadable formats from suppliers and alerts in LIMS for any exceedances. External audit/review |  | Aquality | N/A | Kelvin O'Halloran Sonia Edwards | 2019-12-31 | Y | LIMS alerts system implemented and remains in use.
Overarching | DWQ28 | Aquality A4.24 | Supporting Programs | A4.24 Finalise implementation of chemical delivery procedures across Seqwater assets |  | Aquality | N/A | Manager Techncial Support & Improvement | 2020-05-30 | Y | PRO-02383 Receiving Bulk Chemical Deliveries, FRM-01070 Receiving Bulk Cehmical Deliveries Checklist and site specific chemical receival work instructions have been developed and rolled out. Described in DWQMP
Overarching | DWQ29 | Aquality A4.25 | Supporting Programs | A4.25 Review couplings requirements (chemical delivery operations) and signage/labelling requirements. Make suggested improvements. |  | Aquality | N/A | David Roberts Duncan Shillito Vince Granahan | 2019-12-31 | Y | Completed. Refer DWQ28
Overarching | DWQ30 | Aquality A4.26 | Supporting Programs | A4.26 Finalise implementation of disinfection SOPs and materials that come into contact with DW training |  | Aquality | N/A | Dan Healy | 2019-12-31 | Y | Training has been completed. Ongoing refresher/new start program.
Overarching | DWQ31 | Aquality A5.1 | Supporting Programs | A5.1 WQ awareness for reception staff |  | Aquality | N/A | Principal Water Quality | 2021-12-31 | Y | Update: Water quaity awareness training framework developed for all Seqwater staff. This includes a general awareness training in the 'on-boarding' process for all new staff.
Overarching | DWQ32 | Aquality A5.2 | Supporting Programs | A5.2 Non-conformance response procedure to be developed *now linked to investgation procedure* |  | Aquality | N/A | Principal Water Quality | 2019-12-31 | Y | Integrated Incident Investigation Procedure PRO-00793 in place
Overarching | DWQ33 | Aquality A6.1 Aquality A6.2 Aquality A6.3 | Supporting Programs | A6.1 On-call DWQ pers to communicate to line management as per Incident Controller training. Continue to rollout this training. A6.2 Update incident and communication rocesses in line with the Regional Operations model A6.3 Process for email-OCA Acknowledgement |  | Aquality | N/A | Duncan Shillito Jason Boldeman | 2019-12-31 | Y | All OCA and Incident controller training has been completed by DWQ staff that are on-call. Incident communication processes are now well established and fully implemented. DWQ staff are further developing their emergency management skills by participating in major incident-emergency exercises.
Overarching | DWQ34 | Aquality A6.4 | Supporting Programs | A6.4 Disinfection SOPs to be finalised and applied across the business |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | Y | Refer to DWQ30. Completed
Overarching | DWQ35 | Aquality A6.5 | Supporting Programs | A6.5 Finalise Seqwater Incident investigation procedure (draft) which includes ICAM |  | Aquality | N/A | Helen Warburton | 2019-12-31 | Y | Refer to DWQ2. Completed. PRO-00793
Overarching | DWQ36 | Aquality A7.1 | Supporting Programs | A7.1 Re-look at training for senior leadership and PM positions |  | Aquality | N/A | Principal Water Quality | 2021-12-31 | Y | Water quaity awareness training for senior leadership conducted by WQ Principal.
Overarching | DWQ37 | Aquality A7.2 Aquality A7.3 | Supporting Programs | A7.2 Establish a detailed HACCP team charter with team member responsibilties A7.3 Complete maintenance/PM rollout of training |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | Y | Completed
Overarching | DWQ38 | Aquality A7.4 | Supporting Programs | A7.4 Feedback in next round of DWQ awareness training through Learning OD (independent party) |  | Aquality | N/A | Learning OD | 2019-12-31 | Y | Completed
Overarching | DWQ39 | Aquality A9.1 Aquality A9.2 | Supporting Programs | A9.1 Strategy being developed for capturing knowledge gaps A9.2 Development of the WQ partnership to capture risks and identify research needs |  | Aquality | N/A | A. Roux D. Shillito | 2019-12-31 | Y | Completed. WQ Partnership now exists
Overarching | DWQ40 | Aquality A9.3 | Supporting Programs | A9.3 Knowledge management - consider establishing a library or portal to share research proposals and outcomes |  | Aquality | N/A | Manager PSRI | 2019-12-31 | Y | Research summaries and 'story books' are developed and available on REX. Updates on research project progression and outcomes discussed on Yammer and through 'Lunch and Learns'.
Overarching | DWQ41 | Aquality A9.4 | Supporting Programs | A9.4 Add the Supply System to the DWQMP Validation Report |  | Aquality | N/A | D. Middleton | 2019-12-31 | Y | Completed. Updated document registered on Qpulse.
Overarching | DWQ42 | Aquality A9.5 | Supporting Programs | A9.5 Formal process for communicating changes and any related validation to the Regulator |  | Aquality | N/A | D. Shillito | 2019-12-31 | Y | Completed. Refer to DWQMP submitted to the Regulator as an amendment application during 2016.
Overarching | DWQ43 | Aquality A9.6 | Supporting Programs | A9.6 Establish a Process risk register |  | Aquality | N/A | Dapo | 2019-12-31 | Y | Completed. Process issues register exists/is in use
Overarching | DWQ44 | Aquality A10.1 | Supporting Programs | A10.1 Finalise roll out and formal processes/procedures for records management |  | Aquality | N/A | Records/ICT | 2019-12-31 | Y | Completed. REX (formerly TRIM) is no rolled out.
Overarching | DWQ45 | Aquality A10.2 | Supporting Programs | A10.2 Supply System Operator training including excursion reporting Re-instate use of intranet as a portal to documents/spreadsheets |  | Aquality | N/A | S Oldridge | 2019-12-31 | Y | Completed. Ongoing training and feedback to continue to improve excursion reporting.
Overarching | DWQ46 | Aquality A10.3 | Supporting Programs | A10.3 Operator experience/set up in business use of TRIM so that all records/spreadsheets can migrate from G:drive to TRIM |  | Aquality | N/A | Manager Technical Support & Improvement | 2024-06-30 | N | Update: Due date extended. This Improvement is to be addressed through a new database 'Pi Historian' (formerly refered to as Plant Operator Data Management System). The system is being rolled out in stages. First stage is currently in progress with a a trial at selected WTPs.
Overarching | DWQ47 | Aquality A11.1 | Supporting Programs | A11.1 Business Intelligence Project |  | Aquality | N/A | ICT Manager | 2020-06-30 | Y | Update 30 June 2020 - Tableau has been implemented as the Business Inteligence platform across Seqwater.
Overarching | DWQ48 | Aquality A12.1 | Supporting Programs | A12.1 Incorporate Senior Executive Review into DWQMP and HACCP team meetings |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | Y | Completed. Any feedback (if provided) from the senior executive review (management review) conducted annually is able to be included in the HACCP team meeting talking points and published on the DWQ intranet.
Overarching | DWQ49 | Aquality A12.2 | Supporting Programs | A12.2 Route for all DWQ improvement items and 'WQ Reports' through Process Engineering |  | Aquality | N/A | Dapo and Dunc M | 2019-12-31 | Y | All capital and operational improvements are now managed through Management of Change, which includes review by Process Engineering representatives
Overarching | DWQ50 | Aquality A12.3 | Supporting Programs | A12.3 The DWQIP for a site is also reviewed at internal audits and HACCP team meetings. |  | Aquality | N/A | Dan Healy | 2016-03-31 | Y | Completed. Standing item at HACCP team meetings
Overarching | DWQ51 | Audit / INIR 3939 | Supporting Programs | Water Treatment Plant data sheets to move from G:drive to TRIM |  | Audit | N/A | Records/ICT | 2017-06-01 | Y | Refer to A10.3 (duplicate item)
Overarching | DWQ52 | Audit / INIR 3942 | Supporting Programs | The current oPRP table is incomplete and a review of the oPRP table is required.(D15/6241). Information regarding the following items are to be included in the table in order to comply with ISO 22000:2005 requirements: • Monitoring procedures that demonstrates that the oPRP is implemented • Corrections and corrective actions to be taken if monitoring shows that the oPRPs are not in control • Responsibilities and authorities • Records of monitoring |  | Audit | N/A | Dan Healy | 2017-06-01 | Y | Completed. oPRPs are now detailed in HACCP plans
Overarching | DWQ53 | Audit / INIR 3946 | Supporting Programs | HACCP documentation- determine a process to achieve a unified process step definition and alignment for all HACCP documentation Define and align the process steps in the HACCP documentation. The affected documents are: Validation standard, HACCP plan- definition of the operating philosophy including the process steps, risk assessment, monitoring plan, wall chart and plant data sheets. |  | Audit | N/A | Regional DWQ Coord | 2017-06-01 | Y | HACCP plan consistency issues have been resolved. Completed.
Overarching | DWQ54 | Audit / INIR 3947 | Supporting Programs | Establishing limits for discrepancy/tollerance between Operator Grab sample results and corresponding online analyser measurements. There is a need for discussions around defining acceptable limits for online vs grab samples in order to determine whether calibration or other corrective actions are required. |  | Audit | N/A | Regional DWQ Coord | 2017-06-01 | Y | Operator and collaborative maintenance contract processes, including the maintenance and calibration of onlien instruments across all operational areas, is now well established.
Overarching | DWQ55 | Audit / INIR 3928 | Supporting Programs | Establish program (e.g work orders in CIS as per fluoride system) for verifying preventative measures for CCP e.g verfication that water quality alarms and interlocks and other preventative measures listed in the HACCP Risk Registers are adequately monitored, enabled and effective. |  | HACCP Critical Limit Excursion | N/A | Dan Healy | 2017-06-01 | Y | Completed. Now regularly reviewed during HACCP team meetings and verified during audits.