## North
Northern Operational Region - Register of changes to HACCP plans, procedures or related documents
Northern Operational Region - Register of changes to HACCP plans, procedures or related documents
# | Document Ref | WTP/System | HACCP Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | WSR Amendment Required (by Principal DWQ)
1 | REG-00116 | North Pine WTP | HACCP Plan Wall Chart | Raw Water, Coagulation, Supernatant Return, Filtration | Updates to raw water to the effect of removing critical limits pertaining to the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). The PAC system at North Pine is run continuously in "cover mode" with a minimum dose of 2 mg/L. During the summer months, the dose is generally increased substantially to counter any taste and odour compounds arising from blooms. The dosed water pH limits were adjusted as per PRO-00327. The filtered water turbidity limits were adjusted as per PRO-00346 and the supernatant return step was removed due to an ongoing hightened risk present from the aging on site STP. |  | N Emblow | 2014-09-19 | Y
2 | PLN-00066 | Dayboro WTP | HACCP Plan | Title Page, 2.1 Operational Challenges | Removed Month Year title from title page. Replaced with standard document control window. In 2.1.3 under Operational Challenges, documented that large floods have scoured large chunks of the river bank both down and toward well 2. Consequently, Well 2 does not recharge as quickly as it used to. Well 2 is downstream of terrors creek, which is irrigated with secondary effluent from a nearby STP. The effect of this can be seen in event sampling, particular after large rain events, whereby both total coliforms and e.coli spike directly following such an event in the sampling point next to Well 2. Also from this section, the information regarding the requirement of an operations manual was removed, as the operators are now all fully trained and competent to run Dayboro (and as a wider, organisational drive to develop unified operations procedures). | The fact that Dayboro had zero validated log reduction for protozoans, has led to a UV system being installed on the treated water, which has a validated efficacy of 2LRV for cryptosporiddium spp. Further improvements are under consideration by planning, including determining the hydrology of the groundwater/river water influence, the potential for a pipeline from North Pine zone or the addition of further protozoan barriers, such as coagulation and pressure filtration. | N Emblow | 2014-10-08 | Y
3 | PLN-00045 | Landers Shute WTP | HACCP Plan | Title Page, 2.1.3 Operational Challenges | Removed Month Year title from title page. Replaced with standard document control window. Added information regarding the (un)reliability of the current ozone system and the potential challenges regarding it's ongoing maintenance and operation, with a particular focus on the processes required to run the plant should ozone become non-operational for more than the critical limit time frames. | In the latest revisions of the plan, this has been further enhanced, and the critical limit time frames have been significantly increased (up to 48 hours). | N Emblow | 2014-10-20 | Y
4 | PRO-00346 | North Pine WTP | Filtration CCP Procedure | Section 5 - Limits | Filtered water turbidity Critical Limit adjusted to align with SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard (<0.3 NTU, 15 minutes) |  | N Emblow | 2014-10-20 | Y
5 | PRO-00327 | North Pine WTP | Clarification CCP Procedure | Section 5 - Limits | Dosed water pH critical limit adjusted to align more closely with SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard (6.0 -7.5 for 30 minutes - extra time frame required due to configuration of plant) | The variance in time for dosed water pH cinoared to SPE-00320 is required due to the nature of the way in which the plant currently handles pH correction. Installation of a new pH correction system utilising faster reacting chemicals such as NaOH will improve the situation | N Emblow | 2014-10-20 | Y
6 | PRO-00314 | North Pine WTP | Raw Water CCP Procedure | Section 5 - Limits | Removed references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3". However, these results would have been at least a week old, which exceeds the timely response required for corrective action for a critical limit exceedance. Once the revision of the CMP is complete, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways). This is also in accordance to the highly developed SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. The turbidity limits were adjusted slightly, coming up from 12 NTU for 30 minutes to 15 NTU for 30 minutes. This is in order to reflect the less dynamic nature of the system (ie a lake, rather than a river) and in principle further adjustments likely should be made. | Adjusting the raw water turbidity limit to be a range or variance rather than a static limit will enhance the practicality of this particular limit. | N Emblow | 2014-10-20 | Y
7 | PRO-00976 | Dayboro WTP | Filtration CCP Procedure | Section 5 - Limits | Due to the nature of the filters (greensand, non-primary filtration) and the fact that they are not validated for log removal of protozoan pathogens, and the fact that there is no coagulant dosed, operations requested an increase of the filtered water turbidity limit from 0.5 NTU for 30 minutes to 0.8 NTU for 15 minutes. This decreases the need to run filters to scour and increase production capacity. In conjunction with this change, PRO-01068 Raw Water CCP Procedure was enhanced by reducing the turbidity limit from 1 NTU down to 0.8 NTU in the raw water well (since in theory, the river bank acts as the primary filtration step at this site, this is where any reduction in pathogens would occur). Also added a filtered water free chlorine limit so as to assist with the process of greensand filter to filter out oxidised manganese and iron (the primary purpose of the greensand filters is to remove manganese and iron, and pre-filtration chlorination assists the filters to that effect. This is in addition to what used to be the usual practice of potassium permanganate regeneration, of which the plant is still capable, but with the pre-filter chlorine is likely to not be necassary.) |  | N Emblow | 2014-10-30 | Y
8 | PRO-01068 | Dayboro WTP | Raw Water CCP Procedure | Section 5 - Limits | As described in the description for PRO-00976, the raw water turbidity (as in, the turbidity in the raw water well, after it has filtered through the river bank) is the primary filtration step at this site. Consequently, the limits were reviewed and tightened, in order to reflect the importance of the control of this critical step. The Critical Limit changed from >1NTU for >20 minutes to >0.8 NTU for >15 minutes and the Action Limit changed from >0.7 NTU for >1 hour to >0.6 NTU for >30 minutes. | Whilst this did not change the validated efficacy of the primary filtration step (eg riverbank filtration) quantitatively, it is still a relatively important improvement that would benefit the water quality outcomes for the people of Dayboro. The eventual aim would be to have a critical limit in the raw water well of >0.5 NTU for >15 minutes, in accordance with most international guidance with regard to the efficacy of riverbank filtration. | N Emblow | 2014-10-30 | Y
9 | REG-00117 | Dayboro WTP | HACCP Plan Wall Chart | Raw Water Step, Filtration Step, Fluoridation Step | Updates to the wall chart to reflect the chnages made in the procedures PRO-00976, PRO-01068 and PRO-01068 |  | N Emblow | 2014-10-30 | Y
10 | REG-00437 | Petrie WTP | HACCP Plan Wall Chart | Raw Water, Clarification, Filtration, Manganese Removal | Limits updated to reflect information in PRO-00628, PRO-00629, PRO-00634, PRO-00630, PRO-01081. |  | N Emblow | 2014-10-30 | Y
11 | PRO-00628 | Petrie WTP | Raw Water CCP Procedure | Section 5 - Limits | Removed references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3", however, these results would have been at least a week old, which is antithetical to the timely response required for corrective action resultant from a critical limit exceedance. Once the revision of the CMP is complete, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways). This is also in accordance to the highly developed SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. The raw water turbidity limits were adjusted from 30 NTU (grab) to 30 NTU for 15 minutes, in accordance with SPE-00320 |  | N Emblow | 2014-10-30 | Y
12 | PRO-00629 | Petrie WTP | Clarification CCP Procedure | Section 5 - Limits | The dosed water pH critical limit was adjusted to better align with SPE-00320, (6.0 - 7.5, 15 minutes) |  | N Emblow | 2014-10-30 | Y
13 | PRO-00634 | Petrie WTP | Filtration CCP Procedure | Section 5 - Limits | The filter water turbidity critical limit was adjusted to better align with SPE-00320, (<0.3, 15 minutes) |  | N Emblow | 2014-10-30 | Y
14 | PRO-00630 | Petrie WTP | Manganese QCP Procedure | Section 3 - Background Section 5 - Limits | Raw water soluble manganese limit introduced of >50 µg/L per grab per day. Some information regarding the lysing of cells when exposed to potassium permanganete was introduced in Section 3, however, this information will be superceded by the revised CMP ALF. |  | N Emblow | 2014-10-30 | Y
15 | PRO-01081 | Petrie WTP | Fluoridation CCP Procedure | Section 5 - Limits | Updates to reflect the new interpretation from the Code of Practice, namely tightening the critical limit of 1.2 mg/L down to 1.1 mg/L. |  | N Emblow | 2014-10-30 | Y
16 | PRO-01068 | Dayboro WTP | Fluoridation CCP Procedure | Section 5 - Limits | Updates to reflect the new interpretation from the Code of Practice, namely tightening the critical limit of 1.2 mg/L down to 1.1 mg/L. |  | N Emblow | 2014-10-30 | Y
17 | REG-00163 | Borumba WTP | HACCP Plan Wall Chart | Raw Water step, Filtration Step | - Updates to the raw water step to remove references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3", however, these results would have been at least a week old, which is antithetical to the timely response required for corrective action resultant from a critical limit exceedance. Once the revision of the CMP is complete, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways), as opposed to the binary ultimatum provided by including such risk identification as a Critical Limit. This is also in accordance to SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. Updates to the filtration step were made to align critical limit time frames (30 minutes down to 15 minutes) and values (0.5 NTU down to 0.3 NTU) with the validation standard, as agreed at the HACCP team meeting and subsequent Critical Limit review. The SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard provides ample evidence as to the reasoning the new values are necassary to significantly reduce risk and ensure adequate barrier performance. | Updates to the specific CCP procedures and HACCP plan are to be made upon the implementation of the newly developed integrated HACCP Plan and Wall chart system (eg streamlining. | N Emblow | 2014-11-13 | Y
18 | REG-00111 | Image Flat WTP | HACCP Plan Wall Chart |  | - updates to the raw water step to remove references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3", however, these results would have been at least a week old, which is antithetical to the timely response required for corrective action resultant from a critical limit exceedance. Once the revision of the CMP is complete, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways), as opposed to the binary ultimatum provided by including such risk identification as a Critical Limit. This is also in accordance to the highly developed SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. This is particular important at sites that are able to reduce the risk associated with algal biovolume and toxins significantly, due to the presence of one or more primary barriers (such as Ozone/BAC or PAC, or free chlorine for many cyanotoxins (except saxitoxins) or secondary barriers (such as DAF or DAFF)). The PAC system at Image Flat has been shown previously to be able to deal with significant concentrations of 2-methylisoborneol and geosmin in the raw waters, which is a good indicator of the processes ability to be able to provide some reduction in concentration of toxins, such as saxitoxin (a chlorine resistant toxin usually present from the same species that produce geosmin) Updates to the filtration step were made to align critical limit time frames (30 minutes down to 15 minutes) with the validation standard, as agreed at the HACCP team meeting and subsequent Critical Limit review. The SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard provides ample evidence as to the reasoning the new values are necassary to significantly reduce risk and ensure adequate barrier performance. Also at this site, since fluoridation is occuring, in order to align with the new interpreation of the fluoride code of practice 2010, the critical limit for fluoride was brought down from 1.2 mg/L to 1.1 mg/L | Updates to the specific CCP procedures and HACCP plan are to be made upon the implementation of the newly developed integrated HACCP Plan and Wall chart system.(eg streamlining. The interlocks on all fluoridated plants were set to 1.1 mg/L from 1.2 mg/L during 2013/2014. | N Emblow | 2014-11-13 | Y
19 | REG-00107 | Landers Shute WTP | HACCP Plan Wall Chart | Raw Water, Coagulation, Filtration, Fluoridation | The raw water turbidity analyser was not performing so it was temporarily replaced with operator grab samples Dosed water pH limit aligned to SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard (5.8 - 7.5, 15 minutes) Filtered water turbidity limit aligned to SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard (>0.3 for >15 minutes) | The raw water analyser was positioned poorly and continually blocked causing false alarms. Subsequently operators became complacent to the alarm. Grab samples ensure the diligience continues until the instrument could be relocated or a higher velocity sample line installed. | N Emblow | 2014-11-13 | Y
20 | PRO-00646 | Landers Shute WTP | Clarification CCP Procedure | Section 5 - Limits | Coagulation (flashmixer pH) critical limit adjusted to align with SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard (5.8-7.5, 15 minutes) |  | N Emblow | 2014-11-14 | Y
21 | PRO-00647 | Landers Shute WTP | Intermediate Ozone CCP Procedure | Section 5 - Limits | Update to include limit pertaining to PLN-00045 2.1.3 operational challenges, namely around the operation of the plant without intermediate ozonation (the addition of an action limit for ozonation plant operational/non-operational) | This procedure has since been combined with the BAC filtration procedure and moved to a QCP due to the unreliability of the ozonation system and inability to validate log removal for pathogen reduction/ | N Emblow | 2014-11-14 | Y
22 | PRO-00651 | Landers Shute WTP | Filtration CCP Procedure | Section 5 - Limits | Filtered water turbidity Critical Limit adjusted to align with SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard (<0.3 NTU, 15 minutes) |  | N Emblow | 2014-11-14 | Y
23 | PRO-00654 | Landers Shute WTP | Fluoridation CCP Procedure | Section 5 - Limits | Updates to reflect the new interpretation from the Code of Practice, namely tightening the critical limit of 1.2 mg/L down to 1.1 mg/L. |  | N Emblow | 2014-11-14 | Y
24 | PRO-01141 | Landers Shute WTP | Raw Water CCP Procedure | Section 5 - Limits | Removed references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3", however, these results would have been at least a week old, which is antithetical to the timely response required for corrective action resultant from a critical limit exceedance. Once the revision of the CMP is complete, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways). This is also in accordance to the highly developed SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. |  | N Emblow | 2014-11-14 | Y
25 | REG-00156 | Jimna WTP | HACCP Plan Wall Chart | Raw Water, Coagulation, Filtration | - Updates to the raw water step to remove references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3", however, these results would have been at least a week old, which is antithetical to the timely response required for corrective action resultant from a critical limit exceedance. Once the revision of the CMP is complete, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways), as opposed to the binary ultimatum provided by including such risk identification as a Critical Limit (ie consider the juxtaposition as follows;- the plant is either off or on in the first scenario and at least a week of water with potentially hightened algal risk has been sent to town, wheras in with the risk interwoven into the way the plant works, the plant is almost always on, it merely adjusts for the appropriate level of risk, and the plant is vigilantly able to reduce any algal risk appropriately, decreasing the net risk to the public). This is also in accordance to the highly developed SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. The introduction of many new online analysers to the Jimna WTP process meant enhanced visibility and also as in accordance with the SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard required critical limits associated with the critical monitoring of the critical control points. Substantially, the dosed water pH (a measure of the affect of alum and a manner to ensure coagualtion is performing well) was updated to be within the validation specification (5.8 - 7.5 pH units, 15 minutes). Whilst the SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard did not explicit call for it, a measure of sedimentation efficacy measured by turbidity can be a secondary indicator of coagulation performance (however, it mustn't be relied upon, as raw water turbidity might be masking what appears to be well settled water). Consequently a further criticial limit (since the analyser was there) was agreed to of >5 NTU for >15 minutes on the settled water. True colour grab samples were and continue to be taken as a tertiary line of evidence to support the processes of coagulation, flocculation and settling. Updates to the filtration step were made to align critical limit time frames (30 minutes down to 15 minutes) and values (0.5 NTU down to 0.3 NTU) with the validation standard, as agreed at the HACCP team meeting and subsequent Critical Limit review. The SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard provides ample evidence as to the reasoning the new values are necassary to significantly reduce risk and ensure adequate barrier performance. | Updates to the specific CCP procedures and HACCP plan are to be made upon the implementation of the newly developed integrated HACCP Plan and Wall chart system. Further proposed enhancements to the coagulation process include the introduction monitoring the dosing of coagulant itself, via a dosing line flow meter interlock | N Emblow | 2014-12-10 | Y
26 | REG-00542 | Kilcoy WTP | HACCP Plan Wall Chart |  | - Updates to the raw water step to remove references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3", however, these results would have been at least a week old, which is antithetical to the timely response required for corrective action resultant from a critical limit exceedance. Consequently, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways), as opposed to the binary ultimatum provided by including such risk identification as a Critical Limit. This is also in accordance to the highly developed SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. This is particular important at sites that are able to reduce the risk associated with algal biovolume and toxins significantly, due to the presence of one or more primary barriers (such as Ozone/BAC or PAC, or free chlorine for many cyanotoxins (except saxitoxins) or secondary barriers (such as DAF or DAFF)). The PAC system at Kilcoy is run continuously in cover mode, with both the normal clarifier and the DAF run in series. There is also limited evidence of any significant cyanobacterial risk at this new offtake location. | Updates to the specific CCP procedures and HACCP plan are to be made upon the implementation of the newly developed integrated HACCP Plan and Wall chart system. | N Emblow | 2014-12-10 | Y
27 | REG-00158 | Kirkleagh WTP | HACCP Plan Wall Chart |  | - Updates to the raw water step to remove references to the critical limits regarding the Alert Level Framework (ALF) from the now superceded cyanobacterial management plan (CMP). For example, there was the provision to shut the plant down upon an "alert level 3", however, these results would have been at least a week old, which is antithetical to the timely response required for corrective action resultant from a critical limit exceedance. Once the revision of the CMP is complete, the ALF information will be woven into the HACCP plan, procedures via the Risk Assessment as a source of risk information (ie under alert level 3 circumstances, certain processes should be run in certain ways), as opposed to the binary ultimatum provided by including such risk identification as a Critical Limit (ie consider the juxtaposition as follows;- the plant is either off or on in the first scenario and at least a week of water with potentially hightened algal risk has been sent to town, wheras in with the risk interwoven into the way the plant works, the plant is almost always on, it merely adjusts for the appropriate level of risk, and the plant is vigilantly able to reduce any algal risk appropriately, decreasing the net risk to the public). This is also in accordance to the highly developed SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard for WTP Processes, which suggest the only Critical Limit for WTPs should be Turbidity, as it is the only parameter that is both able to be monitored in a timely fashion, and representative of a signficant and immediate increase in risk. The critical limit for raw water turbidity was tightened to >100 NTU for >15 minutes (in accordance with the validation standard) The introduction of many new online analysers to the Kirkleagh WTP process meant enhanced visibility and also as in accordance with the SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard required critical limits associated with the critical monitoring of the critical control points. Substantially, the dosed water pH (a measure of the affect of alum and a manner to ensure coagualtion is performing well) was updated to be within the validation specification (5.8 - 7.5 pH units, 15 minutes). Updates to the filtration step were made to align critical limit time frames (30 minutes down to 15 minutes) and values (0.5 NTU down to 0.3 NTU) with the validation standard, as agreed at the HACCP team meeting and subsequent Critical Limit review. The SPE-00320 - DWQMP Appendix 9.1 - Water Treatment Process Validation Standard provides ample evidence as to the reasoning the new values are necassary to significantly reduce risk and ensure adequate barrier performance. | Updates to the specific CCP procedures and HACCP plan are to be made upon the implementation of the newly developed integrated HACCP Plan and Wall chart system.(eg streamlining. | N Emblow | 2014-12-10 | Y
28 | PLN-00067 | Dayboro WTP | Monitoring Plan | All | Added additional Column "Purpose". Reviewed frequency of monitoring and made changes as necessary | Refer to TRIM document D14/140896 which illustrates the changes and TRIM document xxx to be submitted to the Regulator. | K McCulloch | 2015-03-01 | Y
29 | PLN-00099 | Borumba WTP | Monitoring Plan | All | Added additional Column "Purpose". Reviewed frequency of monitoring and made changes as necessary | Refer to TRIM document D14/140896 which illustrates the changes and TRIM document xxx to be submitted to the Regulator. | K McCulloch | 2015-03-01 | Y
30 | PLN-00029 | Kenilworth WTP | Monitoring Plan | All | Added additional Column "Purpose". Reviewed frequency of monitoring and made changes as necessary | Refer to TRIM document D14/140896 which illustrates the changes and TRIM document xxx to be submitted to the Regulator. | K McCulloch | 2015-03-01 | Y
31 | PLN-00197 | Noosa WTP | Monitoring Plan | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
32 | PRO-01565 | Noosa WTP | Raw Water CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
33 | PRO-01566 | Noosa WTP | Clarification CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
34 | PRO-01567 | Noosa WTP | Filtration CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
35 | PRO-01570 | Noosa WTP | Disinfection CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
36 | PRO-01572 | Noosa WTP | Fluoridation CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
37 | PRO-01208 | Noosa WTP | Bulk Supply Monitoring Point Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
38 | PRO-01568 | Noosa WTP | Intermediate Ozone CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
39 | PRO-01569 | Noosa WTP | BAC CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
40 | PLN-00198 | Noosa WTP | HACCP Plan | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. Authorisation signature box added to HACCP Flow Diagram. Signed by appropriate people. |  | K McCulloch | 2015-04-01 | Y
41 | REG-00551 | Noosa WTP | HACCP Plan Wall Chart | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
42 | PRO-01571 | Noosa WTP | Manganese QCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-04-01 | Y
43 | PRO-00660 | Image Flat WTP | Raw Water CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-05-01 | Y
44 | PRO-00662 | Image Flat WTP | Clarification CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-05-01 | Y
45 | PRO-00658 | Image Flat WTP | Filtration CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-05-01 | Y
46 | PRO-00659 | Image Flat WTP | Disinfection CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-05-01 | Y
47 | PRO-01343 | Image Flat WTP | Fluoridation CCP Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-05-01 | Y
48 | PRO-01163 | Image Flat WTP | Bulk Supply Monitoring Point Procedure | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-05-01 | Y
49 | PLN-00046 | Image Flat WTP | HACCP Plan | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. Authorisation signature box added to HACCP Flow Diagram. Signed by appropriate people. |  | K McCulloch | 2015-05-01 | Y
50 | REG-00111 | Image Flat WTP | HACCP Plan Wall Chart | All | Minor typographical changes and adjustments in preparation for external ISO 2200 audit by SAI Global. |  | K McCulloch | 2015-05-01 | Y
51 | REG-00307 | Kenilworth WTP | HACCP Risk Register | All | - Mitigated and unmigtigated sections updated as per Risk Assessment Review. Summary page has been updated with all changes. Attendees section has been updated. Raw and Treated Water summary Pages have been added. |  | KM | 2015-09-01 | Y
52 | PLN-00051 | North Pine WTP | HACCP Plan | HACCP Flow Diagram | Added green input arrows and chemicals to HACCP Flow diagram. Added brown arrow and waste water to HACCP Flow Diagram. Authorisation signature box added to HACCP Flow Diagram. Signed by appropriate people. |  | KM | 2015-10-01 | Y
53 | REG-00362 | North Pine WTP | HACCP Risk Register | All | - Mitigated and unmigtigated sections updated as per Risk Assessment Review. Summary page has been updated with all changes. Attendees section has been updated. Raw and Treated Water summary Pages have been added. |  | KM | 2015-10-01 | Y
54 | REG-00435 | Image Flat WTP | HACCP Risk Register | All | - Mitigated and unmigtigated sections updated as per Risk Assessment Review. Summary page has been updated with all changes. Attendees section has been updated. Raw and Treated Water summary Pages have been added. |  | KM | 2015-11-01 | Y
55 | REG-00552 | Noosa WTP | HACCP Risk Register | All | - Mitigated and unmigtigated sections updated as per Risk Assessment Review. Summary page has been updated with all changes. Attendees section has been updated. Raw and Treated Water summary Pages have been added. |  | KM | 2015-11-01 | Y
56 | REG-00340 | Landers Shute WTP | HACCP Risk Register | All | - Mitigated and unmigtigated sections updated as per Risk Assessment Review. Summary page has been updated with all changes. Attendees section has been updated. Raw and Treated Water summary Pages have been added. |  | KM | 2015-11-01 | Y
57 | REG-00107 | Landers Shute WTP | HACCP Wall Chart | All | Updated limits for ozone, BAC and disinfection pH |  | KM | 2015-11-01 | Y
58 | PRO-00653 | Landers Shute WTP | Disinfection CCP Procedure | All | Updated limits for disinfection pH |  | KM | 2015-11-01 | Y
59 | PRO-00647 | Landers Shute WTP | Ozone and BAC CCP Procedure | All | Moved BAC info into ozone procedure. Updated limits for ozone and BAC. |  | KM | 2015-11-01 | Y
60 | PRO-00650 | Landers Shute WTP | BAC CCP Procedure | All | Made obsolete and combined woth ozone procedure |  | KM | 2015-11-01 | Y
61 | PLN-00045 | Landers Shute WTP | HACCP Plan | HACCP Flow Diagram | Added green input arrows and chemicals to HACCP Flow diagram. Added brown arrow and waste water to HACCP Flow Diagram. Authorisation signature box added to HACCP Flow Diagram. Signed by appropriate people. |  | KM | 2015-11-01 | Y
62 | REG-00355 | Dayboro WTP | HACCP Risk Register | All | - Mitigated and unmigtigated sections updated as per Risk Assessment Review. Summary page has been updated with all changes. Attendees section has been updated. Raw and Treated Water summary Pages have been added. UV has also been added to the risk assessment. |  | KM | 2015-12-01 | Y
63 | REG-00157 | Jimna WTP | HACCP Risk Register | All | - Mitigated and unmigtigated sections updated as per Risk Assessment Review. Summary page has been updated with all changes. Attendees section has been updated. Raw and Treated Water summary Pages have been added. |  | KM | 2015-12-01 | Y
64 | REG-00435 | Image Flat WTP | HACCP Risk Register | Mitigated RA | Updated all process names to align with HACCP Flow Diagram. QCP reference removed from PAC and decision tree questions updated. |  | KM | 2016-04-01 | Y
65 | REG-00107 | Landers Shute WTP | HACCP Wall Chart Register | Disinfection | Updated disinfection section to include bypass mode. New limits developed. | N/A | KM | 2016-04-01 | Y
67 | REG-00107 | Landers Shute WTP | HACCP Wall Chart Register | Fluoride | Updated inlet fluoride limits. 2 new inlet limits included. | N/A | KM | 2016-04-01 | Y
68 | REG-00552 | Noosa WTP | HACCP Wall Chart Register | Disinfection | Updated disinfection limits to include option of runnning plant without rechlorination. | N/A | KM | 2016-05-01 | Y
69 | GDE-00047 | Image Flat WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-05-01 | Y
70 | GDE-00081 | Jimna WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-05-01 | Y
71 | GDE-00038 | Dayboro WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
72 | GDE-00043 | Borumba WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
73 | GDE-00048 | Kenilworth WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
74 | GDE-00050 | Noosa WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
75 | GDE-00077 | Kirkleagh WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
76 | GDE-00124 | Kilcoy WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
77 | GDE-00052 | Petrie WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
78 | GDE-00051 | North Pine WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-06-01 | Y
79 | GDE-00049 | Landers Shute WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2016-07-01 | Y
80 | PLN-00066 | Dayboro WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. Updated all process names to align with Risk Assessment and Wall Chart Procedure. Updated document to incorporate some internal audit findings in plant description section. Added UV to HACCP Flow Diagram, Schematic Diagram and plant description. | Refer to TRIM D16/93744 which highlights markups | KM | 2016-07-01 | Y
81 | PRO-00975 | Dayboro WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
82 | PRO-00976 | Dayboro WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
83 | PRO-00977 | Dayboro WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
84 | PRO-01068 | Dayboro WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
85 | PRO-01162 | Dayboro WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
86 | REG-00355 | Dayboro WTP | HACCP Risk Register | N/A | Updated all process names to align with HACCP Flow Diagram, HACCP Wall Chart Procedure and HACCP Plan. Added UV process step in risk asssessment. Included underdosing of fluoride line. | N/A | KM | 2016-07-01 | Y
87 | PLN-00067 | Dayboro WTP | Operational Monitoring Plan | All | Reviewed and updated testing for all process steps. Aligned process names with other HACCP documentation. Added UV testing. | N/A | KM | 2016-07-01 | Y
88 | PRO-02026 | Dayboro WTP | HACCP Plan Wall Chart Procedure | All | Removed Hazards and Preventive Measures columns. Split Action Limit and Critical Limit corrective actions into separate columns. Reviewed and updated all operational targets, action limits and critical limits to ensure alignment with SCADA and to incorporate recent internal audit findings. Document number changed fro REG to PRO. Added UV process and limits. | N/A | KM | 2016-07-01 | Y
89 | PLN-00050 | Kenilworth WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. Updated all process names to align with Risk Assessment and Wall Chart Procedure. Updated document to incorporate some internal audit findings in plant description section. Added UV to HACCP Flow Diagram, Schematic Diagram and plant description. | Refer to TRIM D16/93744 which highlights markups | KM | 2016-07-01 | Y
90 | PRO-01452 | Kenilworth WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
91 | PRO-00703 | Kenilworth WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
92 | PRO-00704 | Kenilworth WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
93 | PRO-01161 | Kenilworth WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
94 | REG-00307 | Kenilworth WTP | HACCP Risk Register | N/A | Updated all process names to align with HACCP Flow Diagram, HACCP Wall Chart Procedure and HACCP Plan. Added UV process step in risk asssessment. | N/A | KM | 2016-07-01 | Y
95 | PLN-00029 | Kenilworth WTP | Operational Monitoring Plan | All | Reviewed and updated testing for all process steps. Aligned process names with other HACCP documentation. Added UV testing. | N/A | KM | 2016-07-01 | Y
96 | PRO-01930 | Kenilworth WTP | HACCP Plan Wall Chart Procedure | All | Removed Hazards and Preventive Measures columns. Split Action Limit and Critical Limit corrective actions into separate columns. Reviewed and updated all operational targets, action limits and critical limits to ensure alignment with SCADA and to incorporate recent internal audit findings. Document number changed fro REG to PRO. Added UV process and limits. | N/A | KM | 2016-07-01 | Y
97 | PLN-00046 | Image Flat WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. Updated all process names to align with Risk Assessment and Wall Chart Procedure. Updated document to incorporate some internal audit findings in plant description section. | Refer to TRIM D16/93744 which highlights markups | KM | 2016-07-01 | Y
98 | PRO-00660 | Image Flat WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
99 | PRO-000662 | Image Flat WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
100 | PRO-00658 | Image Flat WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
101 | PRO-00659 | Image Flat WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
102 | PRO-01343 | Image Flat WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
103 | PRO-001163 | Image Flat WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
104 | REG-00435 | Image Flat WTP | HACCP Risk Register | N/A | Updated all process names to align with HACCP Flow Diagram, HACCP Wall Chart Procedure and HACCP Plan. Included underdosing of fluoride line. | N/A | KM | 2016-07-01 | Y
105 | PLN-00027 | Image Flat WTP | Operational Monitoring Plan | N/A | Reviewed and updated testing for all process steps. Aligned process names with other HACCP documentation. | N/A | KM | 2016-07-01 | Y
106 | PRO-02025 | Image Flat WTP | HACCP Plan Wall Chart Procedure | All | Removed Hazards and Preventive Measures columns. Split Action Limit and Critical Limit corrective actions into separate columns. Reviewed and updated all operational targets, action limits and critical limits to ensure alignment with SCADA and to incorporate recent internal audit findings. Document number changed from REG to PRO. | N/A | KM | 2016-07-01 | Y
107 | PLN-00198 | Noosa WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. Updated all process names to align with Risk Assessment and Wall Chart Procedure. Updated document to incorporate some internal audit findings in plant description section. | Refer to TRIM D16/93744 which highlights markups | KM | 2016-07-01 | Y
108 | PRO-01565 | Noosa WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
109 | PRO-01566 | Noosa WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
110 | PRO-01567 | Noosa WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
111 | PRO-01570 | Noosa WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
112 | PRO-01572 | Noosa WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
113 | PRO-01568 | Noosa WTP | Ozone CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
114 | PRO-01569 | Noosa WTP | BAC CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
115 | PRO-01571 | Noosa WTP | Manganese QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
116 | PRO-01208 | Noosa WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
117 | REG-00552 | Noosa WTP | HACCP Risk Register | N/A | Updated all process names to align with HACCP Flow Diagram, HACCP Wall Chart Procedure and HACCP Plan. Included underdosing of fluoride line. | N/A | KM | 2016-07-01 | Y
118 | PLN-00197 | Noosa WTP | Operational Monitoring Plan | N/A | Reviewed and updated testing for all process steps. Aligned process names with other HACCP documentation. | N/A | KM | 2016-07-01 | Y
119 | PRO-02074 | Noosa WTP | HACCP Plan Wall Chart Procedure | All | Removed Hazards and Preventive Measures columns. Split Action Limit and Critical Limit corrective actions into separate columns. Reviewed and updated all operational targets, action limits and critical limits to ensure alignment with SCADA and to incorporate recent internal audit findings. Document number changed from REG to PRO. | N/A | KM | 2016-07-01 | Y
120 | PLN-00045 | Landers Shute WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. Updated all process names to align with Risk Assessment and Wall Chart Procedure. Updated document to incorporate some internal audit findings in plant description section. | Refer to TRIM D16/93744 which highlights markups | KM | 2016-07-01 | Y
121 | PRO-01141 | Landers Shute WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
122 | PRO-00646 | Landers Shute WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
123 | PRO-00651 | Landers Shute WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
124 | PRO-00653 | Landers Shute WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
125 | PRO-00654 | Landers Shute WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
126 | PRO-00647 | Landers Shute WTP | Intermediate Ozone and BAC QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
127 | PRO-00649 | Landers Shute WTP | Manganese Treatment QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
128 | PRO-01159 | Landers Shute WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-07-01 | Y
129 | REG-00340 | Landers Shute WTP | HACCP Risk Register | N/A | Updated all process names to align with HACCP Flow Diagram, HACCP Wall Chart Procedure and HACCP Plan. Included underdosing of fluoride line. | N/A | KM | 2016-07-01 | Y
130 | PLN-00033 | Landers Shute WTP | Operational Monitoring Plan | N/A | Reviewed and updated testing for all process steps. Aligned process names with other HACCP documentation. | N/A | KM | 2016-07-01 | Y
131 | PRO-02107 | Landers Shute WTP | HACCP Plan Wall Chart Procedure | All | Removed Hazards and Preventive Measures columns. Split Action Limit and Critical Limit corrective actions into separate columns. Reviewed and updated all operational targets, action limits and critical limits to ensure alignment with SCADA and to incorporate recent internal audit findings. Document number changed from REG to PRO. | N/A | KM | 2016-07-01 | Y
132 | PLN-00051 | North Pine WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. Updated all process names to align with Risk Assessment and Wall Chart Procedure. Updated document to incorporate some internal audit findings in plant description section. | Refer to TRIM D16/93744 which highlights markups | KM | 2016-08-01 | Y
133 | PRO-00314 | North Pine WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
134 | PRO-00327 | North Pine WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
135 | PRO-00346 | North Pine WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
136 | PRO-00364 | North Pine WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
137 | PRO-00170 | North Pine WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
138 | PRO-00355 | North Pine WTP | Supernatant Return CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
139 | PRO-00367 | North Pine WTP | Manganese QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
140 | PRO-01164 | North Pine WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2016-08-01 | Y
141 | REG-00578 | North Pine WTP | HACCP Risk Register | N/A | Updated all process names to align with HACCP Flow Diagram, HACCP Wall Chart Procedure and HACCP Plan. Included underdosing of fluoride line. | N/A | KM | 2016-08-01 | Y
142 | PLN-00068 | North Pine WTP | Operational Monitoring Plan | N/A | Reviewed and updated testing for all process steps. Aligned process names with other HACCP documentation. | N/A | KM | 2016-08-01 | Y
143 | PRO-02108 | North Pine WTP | HACCP Plan Wall Chart Procedure | All | Removed Hazards and Preventive Measures columns. Split Action Limit and Critical Limit corrective actions into separate columns. Reviewed and updated all operational targets, action limits and critical limits to ensure alignment with SCADA and to incorporate recent internal audit findings. Document number changed from REG to PRO. | N/A | KM | 2016-08-01 | Y
144 | REG-00385 | Ewen Maddock WTP | HACCP Risk Register | ALL | Reviewed Unmitigated and Mitigate Risk Assessment with HACCP Team in preparation for restart. Updated all process names to align with HACCP Flow Diagram, HACCP Wall Chart Procedure and HACCP Plan. Included underdosing of fluoride line. | D17/73063 | KM | 2017-06-01 | Y
145 | GDE-00046 | Ewen Maddock WTP | Verification Sample Point Guide | All | Removed reference to SAWCS and added PASS requirements. | N/A | KM | 2017-07-01 | Y
146 | PLN-00031 | Ewen Maddock WTP | Operational Monitoring Plan | All | Reviewed and updated testing for all process steps. Aligned process names with other HACCP documentation. | N/A | KM | 2017-07-01 | Y
147 | PLN-00053 | Ewen Maddock WTP | HACCP Plan | ALL | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. Updated all process names to align with Risk Assessment and Wall Chart Procedure. Reviewed whole of document and updated details as appropriate. Added paragraph on the use of Dynamic C.t. | N/A | KM | 2017-07-01 | Y
148 | PRO-02184 | Ewen Maddock WTP | HACCP Plan Wall Chart Procedure | All | Removed Hazards and Preventive Measures columns. Split Action Limit and Critical Limit corrective actions into separate columns. Reviewed and updated all operational targets, action limits and critical limits to ensure alignment with SCADA and to incorporate recent internal audit findings. Document number changed from REG to PRO. Added Dynamic C.t. limits. | N/A | KM | 2017-07-01 | Y
149 | PRO-00736 | Ewen Maddock WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
150 | PRO-00734 | Ewen Maddock WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
151 | PRO-00733 | Ewen Maddock WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
152 | PRO-00737 | Ewen Maddock WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
153 | PRO-000586 | Ewen Maddock WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
154 | PRO-00740 | Ewen Maddock WTP | Intermediate Ozone CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
155 | PRO-00739 | Ewen Maddock WTP | BAC QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
156 | PRO-00741 | Ewen Maddock WTP | Manganese QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
157 | PRO-01160 | Ewen Maddock WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | KM | 2017-07-01 | Y
158 | PRO-02074 | Noosa WTP | HACCP Plan Wall Chart Procedure | Disinfection | Changes to the critical limits to facilitate real time ct and remove the requirement for ozone as critical limit for virus log reduction. | changed critical limit for ozone to: Ozonated Water Intermediate Ozone not operational for >48 hours introduced real time ct critical limit Real Time Ct <10 mg.min/L for >10 minutes and action limit <10 mgmin/L for > 2 minutes | NE | 2017-08-05 | Y
159 | PRO-00198 | Noosa WTP | HACCP Plan | Disinfection | Introduction of real time Ct into HACCP plan to reflect introduction into PLC. Uses real time Ct in place of worst case estimate as critical limit, as per the validation standard requirements. Ozone was prior to this a CCP ofr virus log reduction. Since it is now demonstrated that the plant can achieve the required real time Ct of > 10 mgmin/L, the requirement for ozone to be used as a CCP for virus log reduction has been removed. Ozone has moved to a quality control point and now used soley for organics reduction (i.e. taste and odour) and feeding the biological activated carbon filters (BACs). This change has also been reflected in the wall chart (see #158 - PRO-02074). | Inserted into page 21: To achieve C.t 10 mg.min/L, realtime Ct monitoring and interlocks must be operational. The RealTime Ct monitoring calculates the T10 time and multiplies the free chlorine concentration (from the outlet) to evaluate the free chlorine contact time in real time. This provides assurance that the required 10mg.min/L is met which is required to achieve the log challenge presented by the raw water. Updated HACCP flow diagram on page 22. | NE | 2017-08-05 | Y
160 | REG-00542 | Kilcoy WTP | HACCP Plan Wall Chart Procedure | Disinfection | Updates to facilitate the introduction of rteal time Ct into the HACCP system. Consequently, dosed filtered water flow limits have been removed (unnecassary) critical pH limits on the inlet and outlet have changed to action limits The treated water flow critical limit has changed to an to an action limit The 4 log reduction target was removed (as it was no longer valid under the new methodology) |  | NE | 2018-01-15 | Y
161 | REG-00542 | Kilcoy WTP | HACCP Plan Wall Chart Procedure | UV Irradiation | added uv dose of 5.8 mj/cm^2 as a target and action, since this is what the plant was capable of achieving (2 log protozoan under the HBT manual) and 2.5 as a critical (eg 1 log under the HBT). | Given this is a category 4 site, and 3.5 log can be achieved by the processes up to the UV, 2 log is enough to cover the log reduction requirements, and with the DAF running the plant achieves 4.5 lrv without the UV. | NE | 2018-01-15 | Y
162 | PLN-00267 | Kilcoy WTP | HACCP Plan | Section 2.1 | Expanded upon the system descriptions in order to facilitate the obsoletion of the CCP procedures. |  | NE | 2018-01-15 | Y
163 | PLN-00267 | Kilcoy WTP | HACCP Plan | Section 2.1 | Introduction of real time Ct into HACCP plan to reflect introduction into PLC. Uses real time Ct in place of worst case estimate as critical limit, as per the validation standard requirements |  | NE | 2018-01-15 | Y
164 | PLN-00267 | Kilcoy WTP | HACCP Plan | Section 2.1 | Introduced the Health Based Target Assessment |  | NE | 2018-01-15 | Y
165 | PLN-00267 | Kilcoy WTP | HACCP Plan | Section 4.1 | removed obsolete references |  | NE | 2018-01-15 | Y
166 | PLN-00267 | Kilcoy WTP | HACCP Plan | Section 4.2 (old 4.3) | Listed hydrochloric acid and supplier (used for cleaning) |  | NE | 2018-01-15 | Y
167 | PLN-00050 | Kenilworth WTP | HACCP Plan | Associated Documents | Removed reference to obsolete CCP procedures |  | NE | 2018-01-16 | Y
168 | PLN-00050 | Kenilworth WTP | HACCP Plan | Section 2.1.3.1 | Updated HBT inference to include current philosophy (i.e. removed reference to tier 2 assessment, inferred HBT Cat 4 to Cat 3 via river bank filtratioin, as per instructions from technical specialists) |  | NE | 2018-01-16 | Y
169 | PLN-00050 | Kenilworth WTP | HACCP Plan | Section 2.1.3.4 | Updated Ct calculation to include an actual chlorine concentration Introduction of real time Ct into HACCP plan to reflect introduction into PLC. Uses real time Ct in place of worst case estimate as critical limit, as per the validation standard requirements |  | NE | 2018-01-16 | Y
170 | PRO-01930 | Kenilworth WTP | HACCP Plan Wall Chart Procedure | Disinfection | Inclusion of Real Time Ct target, action and critical limits. |  | NE | 2018-01-16 | Y
171 | PRO-00084 | Kirkleagh WTP | HACCP Plan | Section 2.1.1 | Updated HACCP team members |  | NE | 2018-01-16 | Y
172 | PRO-00084 | Kirkleagh WTP | HACCP Plan | Section 2.1.3 | Added HBT assessment to System Overview Added system information from CCP procedures Added free chlorine Ct calculation for 10mg.min/L Updated operational challenges - removed reference to not having online analysers on certain CCPs |  | NE | 2018-01-16 | Y
173 | REG-00158 | Kirkleagh WTP | HACCP Plan Wall Chart | All Steps | Split corrective actions into Action Limit and Critical Limit columns Removed raw water turbidity critical limit Adjusted free chlorine and pH critical limits in order to better accommodate Ct calculation added reservoir level critical limit |  | NE | 2018-01-16 | Y
174 | PLN-00045 | Landers Shute WTP | HACCP Plan | Section 2.1.3.4 | Removal of description of old pre-lime system. Addition of description of new pre-lime (saturator) system. |  | NE | 2018-03-27 | Y
175 | PLN-00045 | Landers Shute WTP | HACCP Plan | Section 2.1.3.13 | addition: post lime treated water ph adjustment |  | NE | 2018-03-27 | Y
176 | PLN-00045 | Landers Shute WTP | HACCP Plan | Section 2.1.3.11 | addition of dynamic ct |  | NE | 2018-03-27 | Y
185 | pln-00198 | Noosa WTP | HACCP Plan | Throughout | Typographical corrections. Updated Section 5 to reference REG-000250 |  | ne | 2018-05-01 | Y
187 | PLN-00053 | Ewen Maddock WTP | haccp plan | Disinfection | Update to include dynamic ct. Updated Section 5 to reference REG-000250. removed references to old RA. Added references to new RA. |  | ne | 2018-07-03 | Y
177 | PLN-00045 | Landers Shute WTP | HACCP Plan | Section 2 | Recalculated Ct requirements. |  | NE | 2018-07-05 | Y
178 | PRO-00355 | North Pine WTP | HACCP Plan | System Description | Update to include brief functional description of the caustic system. |  | NE | 2018-07-05 | Y
179 | PLN-00267 | Kilcoy WTP | HACCP Plan | Throughout | Referenced the new risk assessment, removed reference to old risk assessment. Various typographical corrections |  | NE | 2018-07-10 | Y
182 | PLN-00066 | Dayboro WTP | HACCP Plan | Section 5 | Updated Section 5 to reference REG-000250 |  | NE | 2018-07-24 | Y
183 | PLN-00051 | North Pine WTP | HACCP Plan | Section 5 | Updated Section 5 to reference REG-000250 |  | NE | 2018-07-24 | Y
188 | PLN-00045 | Landers Shute WTP | HACCP Plan | Section 5 Disinfection Plant Overview | Updated Section 5 to reference REG-000250 Updated Ct calculations for when Dynamic Ct is unavailable Update plant aerial photo Updated schematic to include centrifuges |  | ne | 2018-07-24 | Y
181 | PLN-00084 | Kirkleagh WTP | HACCP Plan | Throughout | Referenced the new risk assessment, removed reference to old risk assessment. Various typographical corrections. Updated Section 5 to reference REG-000250 |  | NE | 2018-07-25 | Y
180 | PLN-00046 | Image Flat WTP | HACCP Plan | Disinfection | Recalculated Ct requirements based upon updated information regarding Reservoir 1 volume. Updated Section 5 to reference REG-000250 |  | NE | 2018-07-30 | Y
184 | PLN-00082 | Jimna WTP | HACCP Plan | Throughout | Referenced the new risk assessment, removed reference to old risk assessment. Various typographical corrections. Updated Section 5 to reference REG-000250. Update to process description. Recalculation of Ct based on true instantaneous flow. True instantaneous flow updated to reflect what is achievable. Updated sections to match HACCP templates. |  | NE | 2018-07-30 | Y
186 | PLN-00050 | Kenilworth WTP | HACCP Plan | Section 5 | Updated Section 5 to reference REG-000250 |  | ne | 2018-07-31 | Y
187 | PLN-00046 | Image Flat WTP | HACCP Plan | Section 5 update | Corrected minor typographical errors |  | ne | 2018-07-31 | Y
188 | PLN-00267 | Kilcoy WTP | HACCP Plan | Section 5 update | Corrected minor typographical errors |  | ne | 2018-07-31 | Y
189 | PLN-00198 | Noosa WTP | HACCP Plan | Section 5 update | Corrected minor typographical errors |  | ne | 2018-07-31 | Y
190 | PLN-00050 | Kenilworth WTP | HACCP Plan | Section 5 update | Corrected minor typographical errors |  | ne | 2018-07-31 | Y
191 | PLN-00053 | Ewen Maddock WTP | HACCP Plan | Section 5 update | Corrected minor typographical errors |  | ne | 2018-07-31 | Y
192 | REG-00340 | Landers Shute WTP | HACCP Risk Register | Disinfection | Bypass mode under disinfection step risk assessed and included in risk assessment. | N/A | KM | 2018-07-31 | Y
193 | PLN-00068 | North Pine WTP | Operational Monitoring Plan | Throughout | As a part of the recent audit at Noosa, it was identified that there were some inconsistencies in the OMP compared to what is monitored (eg http://riskwizard/Modules/Risk/Risk.aspx?action=ActionForm&id=9804). I have corrected the OMP to match what is currently being monitored. |  |  | 2018-07-31 | Y
194 | PRO-01930 | Kenilworth WTP | HACCP Plan Wall Chart Procedure |  | the time for the inlet free chlorine from 15 min to 30 min. This will be fine as long as the outlet chlorine ccp and real time ct ccps are still met. |  | ne | 2018-10-29 | Y
195 | PLN-00050 | Kenilworth WTP | HACCP Plan | Throughout | Introduction of aluminium sulphate for seeding the filters in the operational challenges section and aluminium sulphate to the list of approved chemicals Change of validation around filtration (we cant claim log reduction on green sand filters) Introduction of text extending the validation on real time ct, and the indication that if real time ct is met, then the critical limit for outlet free chlorine risk is reduced giving an allowance of 30 minutes under the critical limit at the outlet if the real time ct is still met. |  | ne | 2018-10-29 | Y
196 | PRO-01780 | Dayboro and Kenilworth WTPs | Supporting Procedure | Throughout | Added text: Seed the filter with a small quantity of aluminium sulphate to speed up the process |  | ne | 2018-11-01 | Y
197 | PLN-00053 | Ewen Maddock WTP | HACCP Plan | Section 2.1.3 | change of two words in section 2.1.3.13 from Sodium hypochlorite to Chlorine gas |  | ne | 2018-11-20 | Y
198 | PLN-00045 | Landers Shute WTP | HACCP Plan | Section 3.2 | update to landers HACCP plan addressing the findings from audit RW 12498 (specifically – adding limits directly into validation table). |  | ne | 2018-12-17 | Y
199 | PRO-02108 | North Pine WTP | HACCP Plan | Critical Limit for Res Level | The only change is the critical limit for the treated water reservoir level is now given in absolute terms instead of percentage. This limit ensures Ct is met even during times when a single cell is online. |  | ne | 2019-01-09 | Y
200 | PLN-00031 | Ewen Maddock WTP | Operational Monitoring Plan | Throughout | removed DO from the program |  | ne | 2019-01-14 | Y
201 | PRO-02107 | Landers Shute WTP | HACCP Plan Wall Chart Procedure | Disinfection | pH dosed filtered water and treated water target adjusted to 7.3 to better reflect operational capability |  | ne | 2019-01-17 | Y
202 | PLN-00066 | Dayboro WTP | HACCP Plan | Schematic update | This change is in response to Risk Wizard Action 8364. Ensure that the HACCP schematic reflects reality. Some questions around location of chlorine monitoring There was some discrepancies identified on the schematic diagram (the prefilter chlorine is monitored via grab, not online, and the raw ph grab samples are taken prior to dosing, not after) |  | ne | 2019-01-17 | Y
203 | PRO-02108 | North Pine WTP | HACCP Plan Wall Chart Procedure | Disinfection | corrected reservoir level description |  | ne | 2019-01-21 | Y
204 | PRO-02225 | Jimna WTP | HACCP Plan Wall Chart Procedure | Disinfection | This update highlights the limit for the treated water reservoir (<30% for >15 min) as per the ct calculations in the HACCP plan |  | ne | 2019-03-19 | Y
205 | PLN-00046 | Image Flat WTP | HACCP Plan | Throughout | updated the schematic and the photo to have res1 labelled as 1.14 ML (i.e. ¼ million gallons) which is consistent with the rest of the doc and with what we know about res1 (now) |  | ne | 2019-03-28 | Y
206 | PLN-00198 | Noosa WTP | HACCP Plan | section 3.2 | updated text in validation table |  | ne | 2019-05-01 | Y
207 | GDE-00050 | Noosa WTP | Verification Sample Point Guide | final page | The main change is the final page, that now describes the blended water sample tap (NOO-SP915) |  | ne | 2019-05-03 | Y
208 | PRO-02225 | Jimna WTP | HACCP Plan Wall Chart Procedure | Throughout | Corrected minor typographical errors |  | ne | 2019-05-16 | Y
209 | PRO-02184 | Ewen Maddock WTP | HACCP Plan Wall Chart Procedure | Disinfection | increased dosed filtered water free chlorine ccp to 3.3 from 2 due to customer requirements |  | ne | 2019-06-05 | Y
210 | PLN-00045 | Landers Shute WTP | HACCP Plan | Throughout | The changes are to the description of the reservoirs and improvements/corrections to the Ct calculations. |  | ne | 2019-07-26 | Y
211 | PLN-00197 | Noosa WTP | Operational Monitoring Plan | Throughout | As a part of the recent audit at Noosa, it was identified that there were some inconsistencies in the OMP compared to what is monitored (eg http://riskwizard/Modules/Risk/Risk.aspx?action=ActionForm&id=9804). I have corrected the OMP to match what is currently being monitored. |  | ne | 2019-08-22 | Y
212 | PLN-00198 | Noosa WTP | HACCP Plan | Throughout | Changing raw water critical limit from 60 NTU to 140 NTU Changing oPRPs list Updated system description and photos Updated challenges |  | ne | 2019-09-06 | Y
213 | PRO-02074 | Noosa WTP | HACCP Plan Wall Chart Procedure | Raw water | Updates to reflect the new critical limit for raw water turbidity |  | ne | 2019-09-06 | Y
214 | PRO-02419 | Linville WTP | HACCP Plan Wall Chart procedure | Throughout | New wall chart for new plant at linville. Supercedes REG-00115 Linville WTP – Haccp Plan Wall Chart Register |  | ne | 2019-09-18 | Y
215 | PRO-02108 | North Pine WTP | HACCP wall chart procedure | Throughout | removed supernatant return line, included "no alum dose" in wall chart |  | ne | 2019-11-19 | Y
216 | PLN-00051 | North Pine WTP | HACCP Plan | Throughout | Updated document format, Updated max flow and max instantaneous flow updated HACCP flow diagram updated schematic diagram updated aerial photo of north pine updated raw water 2.1.3.2 removed supernatant return added flocculation and settling, removed sedimentation replaced filtration with media filtration described polydadmac filteraid updated haccp limit validation updated oPRPs updated chemicals at site |  | ne | 2019-11-19 | Y
217 | PLN-00046 | Image Flat WTP | HACCP Plan | Disinfection | corrected typographical error |  | ne | 2019-12-30 | Y
218 | PLN-00031 | Ewen Maddock WTP | Operational Monitoring Plan | filtered water | Removed the requirement to do grab samples off combined filtered water, which is superseded by the (existing) requirement to do individual filter turbidity grabs. |  | ne | 2020-01-21 | Y
219 | PLN-00083 | Jimna WTP | Operational Monitoring Plan | raw and treated | Changes: Removed Iron monitoring requirement as per RW 10998 | RW 10998 | ne | 2020-02-19 | Y
220 | PLN-00050 | Kenilworth WTP | HACCP Plan | Raw Water | update to raw water turbidity limits | ION01247 | ne | 2020-02-20 | Y
221 | PRO-01930 | Kenilworth WTP | Wall Chart Procedure | Raw Water | update to raw water turbidity limits | ION01247 | ne | 2020-02-20 | Y
222 | PRO-02108 | North Pine WTP | Wall Chart Procedure | Disinfection | Updated disinfection limits for high chlorine trial |  | ne | 2020-03-03 | Y
223 | PRO-00080 | Linville WTP | HACCP Plan | Throughout | new haccp plan for new plant |  | ne | 2020-04-17 | Y
224 | PRO-02419 | Linville WTP | Wall Chart Procedure | Disinfection and Flows | updates to Ct updates to change units of flows to m3/hr |  |  | 2020-04-21 | Y
225 | PRO-00080 | Linville WTP | HACCP Plan | Disinfection and Flows | updates to Ct (introduced Dynamic Ct equation) updates to change units of flows to m3/hr |  | ne | 2020-04-21 | Y
226 | PLN-00267 | Kilcoy WTP | HACCP Plan | Throughout | Updated HACCP Schemated to incorporate changes identified in Audit Task 15561 updates to the haccp team members and the maximum flow under the conditions of operation |  | NE | 2020-08-03 | Y
Submission to Regulator - Amendment Application August 2020
227 | PLN-00045 | Landers Shute WTP | HACCP Plan | Disinfection | The introduction of a bypass res1 mode that provides for critical limits when operating without Reservoir 1. and calculating the required Ct for maximum flow of 1535 L/s and the validation of the limits section |  | NE | 2020-09-02 | Y
228 | PRO-02107 | Landers Shute WTP | HACCP Plan Wall Chart Procedure | Disinfection | The introduction of a bypass res1 mode that provides for critical limits when operating without Reservoir 1. |  | NE | 2020-09-02 | Y
229 | PLN-00050 | Kenilworth WTP | HACCP Plan | Throughout | In pH correction of haccp plan: removal of soda ash and inclusion of caustic soda dosing system. Various references to soda ash replaced with caustic soda |  | NE | 2020-10-06 | Y
230 | PLN-01930 | Kenilworth WTP | HACCP Plan Wall Chart Procedure | Throughout | Slight update to wall chart to also remove reference to old form 27 and include risk wizard reference Various references to soda ash replaced with caustic soda |  | NE | 2020-10-06 | Y
231 | PLN-02107 | Landers Shute WTP | HACCP Plan | Validation | • Removal of raw water turbidity action limit (as there is no raw water haccp alarms on scada and raw water turbidity is variable according to prevailing conditions) • Alteration of dynamic Ct critical limit to >10 mg.min/L for >1min and removal of dynamic ct action limit. (the previous AL was >10 for >2min and previous CL was >10 for 10min, however the SCADA does not have the capability to store these limits presently). |  | NE | 2020-10-16 | Y
232 | PRO-02107 | Landers Shute WTP | HACCP Plan Wall Chart Procedure | Raw Water, Disinfection | • Removal of raw water turbidity action limit (as there is no raw water haccp alarms on scada and raw water turbidity is variable according to prevailing conditions) • Alteration |  | NE | 2020-10-16 | Y
233 | PLN-00198 | Noosa WTP | HACCP Plan | Validation | In order to facilitate an alignment with SCADA: - Critical limit of 140 NTU raw becomes 60 NTU raw - 0.7 action limit on fluoride inlet becomes 0.6. |  | NE | 2020-10-19 | Y
234 | PRO-02074 | Noosa WTP | HACCP Plan Wall Chart Procedure | Raw Water Fluoridation | In order to facilitate an alignment with SCADA: - Critical limit of 140 NTU raw becomes 60 NTU raw - 0.7 action limit on fluoride inlet becomes 0.6. |  | NE | 2020-10-19 | Y
235 | PRO-02107 | Landers Shute WTP | HACCP Plan Wall Chart Procedure | Raw Water | Typographical corrections |  | NE | 2020-10-23 | Y
236 | PRO-00045 | Landers Shute WTP | HACCP Plan | Sludge Handling, Schematic and HACCP Diagram | Updates to better reflect the centrifuge arrangmenet in the sludge handling system |  | NE | 2020-10-30 | Y
237 | PLN-02224 | Kirkleagh WTP | HACCP Plan | Throughout | Disinfection pH action limit moved to 7.6 from 7.3 Schematic and haccp diagram updated to remove 1 settled water tank and sludge holding tank Site layout aerial image updated Removed references to obsolete documents Flocculation & sedimentation becomes flocculation and settling as per process validation standard Flocculation & settling step separated from coagulation as per process validation standard Raw water, flocculation & settling, and distribution become oPRPs Settled water turbidity action limit reduced from 5 (grab) to 2 for >1 hour (online) |  | NE | 2020-11-05 | Y
238 | PRO-02224 | Kirkleagh WTP | HACCP Plan Wall Chart Procedure | Throughout | Disinfection pH action limit moved to 7.6 from 7.3 Flocculation & sedimentation becomes flocculation and settling as per process validation standard Flocculation & settling step separated from coagulation as per process validation standard Raw water, flocculation & settling, and distribution become oPRPs Settled water turbidity action limit reduced from 5 (grab) to 2 for >1 hour (online) Removed irrelevant bulk supply monitoring point communications triggers table at the end of the wall chart procedure (no comms triggers for site) |  | NE | 2020-11-05 | Y
239 | PLN-00051 | North Pine WTP | HACCP Plan | Validation | HACCP limit validation for total chlorine at the chloramination step – increase action limit to 4.5 mg/L and increase critical limit to 4.7 mg/L. These changes are also reflected in the wall chart (attached). These changes are to facilitate the chloramination trial kicking off on Monday, so we need the documents to be live by then. |  | NE | 2020-11-12 | Y
240 | PRO-02108 | North Pine WTP | HACCP Plan Wall Chart Procedure | Chloramination | HACCP limit validation for total chlorine at the chloramination step – increase action limit to 4.5 mg/L and increase critical limit to 4.7 mg/L. These changes are also reflected in the wall chart (attached). These changes are to facilitate the chloramination trial kicking off on Monday, so we need the documents to be live by then. |  | NE | 2020-11-12 | Y
241 | PLN-00080 | Linville WTP | HACCP Plan | Validation | move to calling bank filtration QCP raw water abstraction oPRP in alignment with current practices change the minimum res level to 35% critical, 40% action, and updated Ct and free chlorine critical and action limits to match An additional critical limit added to the biofilm control step of >3.5 mg/L for >15 minutes on the dosed irradiated water. |  | NE | 2020-11-12 | Y
242 | PRO-02419 | Linville WTP | HACCP Plan Wall Chart Procedure | Raw Water, Disinfection | move to calling bank filtration QCP raw water abstraction oPRP in alignment with current practices change the minimum res level to 35% critical, 40% action, and updated Ct and free chlorine critical and action limits to match An additional critical limit added to the biofilm control step of >3.5 mg/L for >15 minutes on the dosed irradiated water. |  | NE | 2020-11-12 | Y
243 | PLN-00267 | Kilcoy WTP | HACCP Plan | Validation | The changes are – removal of reference to the curtain baffle, including recalculating the minimum free chlorine required assuming baffle factor of 0.1 These changes are now permanent as it will have been 10 days since the temporary change took effect on Sunday. They are having no issues meeting the new minimum chlorine CCP (which assumes no baffling). |  | NE | 2020-11-26 | Y
244 | PRO-02223 | Kilcoy WTP | HACCP Plan Wall Chart Procedure | Disinfection | The changes are – removal of reference to the curtain baffle, including recalculating the minimum free chlorine required assuming baffle factor of 0.1 These changes are now permanent as it will have been 10 days since the temporary change took effect on Sunday. They are having no issues meeting the new minimum chlorine CCP (which assumes no baffling). |  | NE | 2020-11-26 | Y
245 | PLN-00051 | North Pine WTP | HACCP Plan | Materials and Chemicals | Changes are – improvement to the naming consistency in the materials and chemicals section. Replacement of LT20 with SNF905. |  | NE | 2020-12-16 | Y
246 | PLN-00046 | Image Flat WTP | HACCP Plan | Materials and Chemicals | – improvement to the naming consistency in the materials and chemicals section. Replacement of fluoride with sodium fluorosilicate and various typographical improvements. |  | NE | 2020-12-17 | Y
247 | PLN-00045 | Landers Shute WTP | HACCP Plan | Materials and Chemicals | improvement to the naming consistency in the materials and chemicals section. Replacement of LT22 with LT25. Various typographical improvements |  | NE | 2020-12-17 | Y
248 | PLN-00053 | Ewen Maddock WTP | HACCP Plan | Materials and Chemicals | improvement to the naming consistency in the materials and chemicals section. Addition of LT25 and various typographical improvements |  | NE | 2020-12-17 | Y
249 | PLN-00267 &PRO-02223 | Kilcoy WTP | HACCP Plan & Wall chart | Disinfection & limits | The changes are – removal of reference to the curtain baffle, including recalculating the minimum free chlorine required assuming baffle factor of 0.1 These changes are now permanent as it will have been 10 days since the temporary change took effect on Sunday. They are having no issues meeting the new minimum chlorine CCP (which assumes no baffling). |  | NE | 2020-11-26 | Y
250 | PLN-00066 & PRO-02026 | Dayboro WTP | HACCP Plan & Wall chart | Various | Renaming of ”bank filtration” step to “Raw water abstraction via bank filtration” Renaming of “filtration” step to “filtration (manganese removal)” A description of the reason the raw water step is critical (reducing the HBT category from 4 to 3) Made it more clear that the filtration step at the site is only for manganese and iron (no coag/green sand filters only) Also - Updated wall chart to reference risk wizard and updated “team leader” to “operations supervisor” These actions are to address the findings in the recent HACCP audit. |  | NE | 2021-02-08 | Y
251 | PLN-00051 & PRO-02108 | North Pine WTP | HACCP Plan & Wall chart | Validation and limits secondary disinfection | Post chlorine free chlorine time limit on critical changed from 15 min to 5 min and action limit changed from 30 min down to 20 min. AND Chloramination CCP – Treated Water Total Chlorine Previously Updated Target 4 mg/L 3.3 mg/L Action limit 4.5 mg/L for >30 min 3.5 mg/L for >30 min Critical Limit 4.7 mg/L for >15 min 3.6 mg/L for >15 min |  | NE | 2021-02-12 | Y
252 | PLN-00045 & PRO-02107 | Landers Shute WTP | HACCP Plan & Wall chart | Validation and limits, some language change throughout | • Introduction of oPRP steps raw water, sedimentation and ozonation • Increase in pH limit by +0.2 units • Change from 10 mg.min/L scheme to 15 mg.min/L Ct scheme (to facility the increase in pH) - including changing limit to real time Ct to 15mg.min/L from 10mg.min/L • Updated document to new template • Updated HACCP team table • Update to schematic and flow diagram to correctly locate the res1 bypass after fluoride dosing • Introduction of oPRP steps raw water, sedimentation and ozonation • Increase in pH limit by +0.2 units • Change from 10 mg.min/L scheme to 15 mg.min/L Ct scheme (to facility the increase in pH) - including changing limit to real time Ct to 15mg.min/L from 10mg.min/L • Updated document to new template • Updated HACCP team table • Update to schematic and flow diagram to correctly locate the res1 bypass after fluoride dosing |  | NE | 2021-03-11 | Y
253 | PRO-02026 | Dayboro WTP | HACCP wall chart procedure | Limits | Introduced 90% UVT action limit Altered 90% UVT critical limit to 85% |  | NE | 2021-04-07 | Y
254 | PLN-00051 & PRO-02108 | North Pine WTP | HACCP Plan and Wall Chart | Validation and limits | the current target of 3.3 is to be revised to a range of 3.3-4, the current action limit of 3.5 mg/L for >30 min is to be revised to 4.3 mg/L for >30 min, and the current critical limit of 3.6 mg/L for >15 mins is to be revised to 4.5 mg/L for >15 min. This change has occurred in the chloramination section of the wall chart and the validation section of the haccp plan. |  | NE | 2021-05-06 | Y
255 | PLN-00198 & PRO-02074 | Noosa WTP | HACCP Plan and Wall Chart | Validation and limits and language througout | Minor update to reinclude/redefine oPRPs. Primary change is there is now no raw water turbidity critical limit (since raw water abstraction is an oPRP). Ozone/BAC have been combined in a similar fashion to the landers update and relabelled as an oPRP as per the validation standard in the validation section of the plan. |  | NE | 2021-05-25 | Y
256 | PRO-02108 & PLN-00051 | North Pine WTP | HACCP Plan and Wall Chart | oPRPs, validation and limits | Minor update to reinclude/redefine oPRPs. Primary change is there is now no raw water turbidity critical limit (since raw water abstraction is an oPRP). |  | NE | 2021-05-25 | Y
257 | GDE-00038, GDE-00046, GDE-00047, GDE-00048, GDE-00049, GDE-00080, GDE-00081, GDE-00124, GDE-00050, GDE-00051, GDE-00077 | Kirkleagh, North Pine, Noosa, Kilcoy, Jimna, Linville, Landers Shute, Kenilworth, Image Flat, Ewen Maddock & Dayboro WTP | Verification Sampling Point Guides | New sample point codes | Updates to include new sampling point codes |  | KL | 2021-06-10 | Y
Submission to Regulator - DWQMP Report 2021
258 | PLN-00051 & PRO-02108 | North Pine WTP | HACCP Plan and Wall Chart | schematic, haccp diagram, oPRPs, validation and limits. | Changes to north pine haccp plan and wall chart 1. Updates to the schematic and diagram to add the correct location of dosing caustic (schematic) and oPRPs (diagram) 2. Updates to the validation section of the HACCP plan which include some new limits: a. New – treated water monochloramine, as read by the ChemScan unit. b. Range/Action/Critical Treated Water Monochloramine >3.3 mg/L and <4.0 mg/L Treated Water Monochloramine <2.7 mg/L or >4.2 mg/L for > 30 minutes (i.e. 2 ChemScan reads) Treated Water Monochloramine <2.2 mg/L or >4.5 mg/L for >15 minutes (ie 1 ChemScan read) c. New – filtered water turbidity >0.99 NTU for >1 minute (an additional limit on filtered water turbidity) 3. Updated oPRPs in HACCP plan 4. Updated chloramination limits to more closely match the limits at Mt Crosby (including the introduction of an action limit of treated water free ammonia) 5. The new limits for the chloramination step are: Treated Water Total Chlorine 3.3 – 4.0 mg/L Treated Water Total Chlorine <3.0 or >4.5 mg/L for >30 minutes Treated Water Total Chlorine <2.5 or >4.9 mg/L for >15 minutes Treated Water Free Chlorine <0.2 mg/L Treated Water Free Chlorine >0.2 mg/L for >30 minutes Treated Water Free Chlorine >0.3 mg/L for >30 minutes Treated Water Monochloramine >3.3 mg/L and <4.0 mg/L Treated Water Monochloramine <2.7 mg/L or >4.2 mg/L for > 30 minutes (i.e. 2 ChemScan reads) Treated Water Monochloramine <2.2 mg/L or >4.5 mg/L for >15 minutes (ie 1 ChemScan read) Treated Water Free Ammonia <0.1 mg/L Treated Water Free Ammonia >1 mg/L (grab) N/A |  | NE | 2021-06-22 | Y
259 | PLN-00084 | Kirkleagh WTP | HACCP Plan | further system description | number of visitors for recreational plant update |  | NE | 2021-07-27 | Y
260 | PLN-00046, PLN-00027 & PRO-02025 | Image Flat WTP | HACCP Plan, Wall Chart and Operational Monitoring Plan | Various/througout | Changes are: OMP: Raw water section: removed duplicate colour in raw water section added uv254 added alkalinity clarification section: removed colour added uv254 removed ph filtration section: removed ph added uv254 treated water section: added uv254 added alkalinity -all sections – relabelled to match descriptions of processes in SPE-00320 HACCP Plan: HACCP Flow chart (aka red circles chart) : added line showing arrangements for all raw water sources removed poly and soda ash relabelled to match section descriptions in SPE-00320 HACCP limit validation: Raw Water Abstraction: Added more information to raw water validation section regarding choice of CCP v oPRP as per SPE-00320 s8.1 Clarification: (now known as Flocculation & Settling) Removed colour from clarification section, replaced with UV254 Set UV254 settled water action limit of 0.07 as per required under SPE-00320 s8.2.4 Filtration (now known as media filtration): Added limit of >0.99 NTU for > 1 minute, as per required under the SPE-00320 s8.4.4 HACCP Wall Chart Procedure: Reformatted to new standardised format Identified interlocks and alarms under each parameter Updated clarification step to include UV254 settled water action limit of >0.07 |  | NE | 2021-07-29 | Y
261 | PRO-01780, PRO-02571 | Dayboro WTP & Kenilworth WTP | Reinstatement procedure | removal of reference to kenilworth | PRO-02571 procedure introduced specifically for Kenilworth reinstatement. updated PRO-01780 to remove references to Kenilworth. The end result: PRO-01780 is now just for Dayboro and PRO-02571 for Kenilworth |  | NE | 2021-09-29 | Y
262 | pln-00081 | Linville WTP | Operational Monitoring Plan | Various | • Move to specify 4/7 day attendance as per analysis : D21/135371 Linville OOT stats and required visitation OMP revision proposal • Removed daily manganese and iron monitoring (now just “as required”) |  | NE | 2021-10-08 | Y
263 | PRO-02419 | Linville WTP | HACCP Plan Wall Chart Procedure | Various | The changes are to address recent audit findings (and various BAU updates): Moved to the new wall chart template Changed biofilm control to oPRP Changed filtered water turbidity limit to 0.2 NTU (from 0.15 NTU) - 1. These filters were not validated for crypto log removal on the basis of any turbidity performance (so turbidity limits do not reflect crypto validation and 2. The LOR for turbidity is 0.1 NTU. The tolerance in PRO-02120 for filtered water is 0.1 NTU, thus there can be a maximum discrepancy of 0.2 NTU before an OOT event is recorded. Added info about upstream water quality monitoring in raw water oPRP Removed critical limit of 5 NTU for 15 minutes on raw water oPRP Changed raw water turbidity action limit to 0.3 NTU for 15 minutes (was 1 NTU for 15 min). the minimum chlorine on 6AE019 goes from 0.89 mg/L to 0.9 mg/L, this is due to some changes in the Ct calculations that were brought up by the auditor. The new calculation will have to be updated in the SCADA dynamic Ct calculation |  | NE | 2021-10-08 | Y
264 | pln-00080 | Linville WTP | HACCP Plan | Various | • updates to the schematic and flow diagrams • Updates to the oPRP table • Updates to the disinfection Ct calculations • Updates to the validation section (as per the previously communicated wall chart changes) • Updates to the conditions of application |  | NE | 2021-10-08 | Y
265 | gde-00080 | Linville WTP | Verification Monitoring Guide | Photos and Labels | • Updates to reflect new plant (i.e. new photos of raw water tap and treated water tap) |  | NE | 2021-10-08 | Y
266 | pro-02184 | Ewen Maddock WTP | HACCP plan wall chart procedure | limits | Previously had <0.2 NTU for >30 min as action limit on bac filtered water turbidity but scada (and correct) thing to say is >0.2 NTU for >30 min |  | NE | 2021-11-08 | Y
267 | PLN-00050 & PRO-01930 | kenilworth WTP | HACCP Plan and Wall Chart | various | removed reference to UV wipers increased filtered water turbidity limits to 0.5 NTU due to filters being greensand/QCP mn only update to format of plan and wall chart added interlock/alarm descriptors to wall chart |  | NE | 2022-02-04 | Y
268 | PLN-00046 & PRO-02025 | Image Flat WTP | HACCP Plan and Wall Chart | Varous | Implementation to the standard of the Crosby templates, including adding the constraints section to each subsection. Updates to the validation section and improvements to the process description. Change from raw water CCP to oPRP. Inclusion of detailed info on the chemicals at site including delivery and storage methodologies. |  | NE | 2022-03-31 | Y
269 | PLN-00197 | Noosa WTP | Operational Monitoring Plan | Extension of preamble text | "Daily meaning once during plant operation" |  | NE | 2022-04-22 | Y
270 | PLN-00046 | Image Flat WTP | HACCP Plan | Table of contents Associated Documents HACCP TeamSystem Overview PRP Materials and Chemicals Reporting | Updated table of contents Updated Associated documents Removed HACCP Team table and referred to PLN-00004 Updated System Overview with new minin lease info Removed oPRP table Updated Chemical information Updated reporting to the new requirements |  | NE | 2022-05-03 | Y
271 | PRO-02225 | Jimna WTP | HACCP plan wall chart procedure | Tables (last page) | Updated BWSA table to reflect new BWSA and Customer Service Standards Updated DWQ on-call number |  | NE | 2022-06-28 | Y
Submission to Regulator - July 2022

## Central
Central Operational Region - Register of changes to HACCP plans, procedures or related documents
# | Document Ref | WTP/System | HACCP Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | WSR Amendment Required (by Principal DWQ)
Example | PRO-00747 | Kuta WTP | Disinfection CCP Procedure | s7, para2 & table | Validation updated for consistency with DWQMP Appendix 9.1 - Water Treatment Plant Process Validation Report | Validation alS Oldridge updated to reflect the disinfection C.t required due to increasing tourism activities upstream of the WTP | Suharto | 2014-02-14 | N
1 | REG-00630 | Supply System | Supply System – Critical Targets Register | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in Supply System HACCP Plan (PLN-00263) and the Wall Chart (PRO-02089). | Procedure archived in Qpulse | S Oldridge | 2016-06-16 | Y
2 | PRO-00132 | Mt Crosby WTPs | Mt Crosby Weir - Raw Water CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
3 | PRO-00447 | Mt Crosby Eastbank WTP | Clarification CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
4 | PRO-00445 | Mt Crosby Eastbank WTP | Supernatant Return QCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
5 | PRO-00450 | Mt Crosby Eastbank WTP | Filtration CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
6 | PRO-00452 | Mt Crosby Eastbank WTP | Disinfection CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
7 | PRO-00453 | Mt Crosby Eastbank WTP | Fluoridation CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
8 | PRO-00454 | Mt Crosby Eastbank WTP | Manganese Control QCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
9 | PLN-00014 | Mt Crosby Eastbank WTP | Plan Operational Monitoring | Table | Removed second last paragraph and updated Table - references to the BSMP/KIP procedure (i.e. obsolete); include reference to PRO-00711 Mt Crosby Westbank WTP - Ipswich Supply through Kholo BSMPs Procedure. Structure reworked to reflect the |  | S Oldridge | 2016-08-04 | Y
10 | REG-00150 | Mt Crosby Eastbank WTP | HACCP Wall Chart Procedure | N/A | Procedure replaced by PRO-01985. | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
11 | PRO-01985 | Mt Crosby Eastbank WTP | HACCP Wall Chart Procedure | Table | Updated the Wall Chart to reflect changes and achieve consistency across regions. |  | S Oldridge | 2016-08-04 | Y
12 | PRO-01150 | Mt Crosby Eastbank WTP | KIP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
13 | REG-00153 | Mt Crosby WTPs | HACCP Risk Register | Table | Updated based on the outcome of the Internal Audit - inclusion of Backflow prevention. |  | S Oldridge | 2016-08-04 | Y
14 | PRO-00448 | Mt Crosby Westbank WTP | Clarification CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
15 | PRO-00446 | Mt Crosby Westbank WTP | Supernatant Return QCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
16 | PRO-00451 | Mt Crosby Westbank WTP | Filtration CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
17 | PRO-00941 | Mt Crosby Westbank WTP | Disinfection CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
18 | PRO-00453 | Mt Crosby Westbank WTP | Fluoridation CCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
19 | PRO-00457 | Mt Crosby Westbank WTP | Manganese Control QCP Procedure | N/A | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
20 | PLN-00013 | Mt Crosby Westbank WTP | Plan Operational Monitoring | Table | Removed second last paragraph and updated Table - references to the BSMP/KIP procedure (i.e. obsolete); include reference to PRO-00711 Mt Crosby Westbank WTP - Ipswich Supply through Kholo BSMPs Procedure. |  | S Oldridge | 2016-08-04 | Y
21 | REG-00151 | Mt Crosby Westbank WTP | HACCP Wall Chart Procedure | N/A | Procedure replaced by PRO-01986. | Procedure archived in Qpulse | S Oldridge | 2015-10-01 | Y
22 | PRO-01986 | Mt Crosby Westbank WTP | HACCP Wall Chart Procedure | Table | Updated the Wall Chart to reflect changes and achieve consistency across regions. |  | S Oldridge | 2016-08-04 | Y
23 | FRM-00586 | Supply System | Alexandra Hills - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
24 | FRM-00587 | Supply System | Aspley Reservoir - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
25 | FRM-00588 | Supply System | Gold Coast and NIP - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
26 | FRM-00589 | Supply System | Green Hill Reservoir - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
27 | FRM-00590 | Supply System | Heinemann Rd - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
28 | FRM-00591 | Supply System | Kimberley Park Reservoir - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
29 | FRM-00592 | Supply System | Kuraby Reservoir - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
30 | FRM-00593 | Supply System | Mt Cotton - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
31 | FRM-00594 | Supply System | Mt. Crosby and SRWP - Mixed Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
32 | FRM-00595 | Supply System | Narangba Reservoirs - Combined Outlet Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
33 | FRM-00596 | Supply System | NPI1 - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
34 | FRM-00597 | Supply System | NPI2 - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
35 | FRM-00598 | Supply System | OTW - EPI Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
36 | FRM-00599 | Supply System | Sparkes Hill Reservoir - Combined Inlet Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
37 | FRM-00600 | Supply System | Sparkes Hill Reservoir - Combined Outlet Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
38 | FRM-00602 | Supply System | Wellers Hill Reservoir - Outlet Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
39 | FRM-00601 | Supply System | OTW - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
40 | FRM-00788 | Supply System | OTW SRWP - Instrument Verification Record Form | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
41 | PRO-01558 | Supply System | Maintaining Chlorine Residual Procedure | All | Update to reflect current conditions. |  | S Oldridge | 2015-10-01 | Y
42 | PRO-01988 | Mt Crosby Eastbank WTP | Jar Test Procedure | New | In line worth the requirements and procedure outlined in the Mt Crosby Eastbank Wall Chart. |  | S Oldridge | 2015-10-01 | Y
43 | PRO-01989 | Mt Crosby Westbank WTP | Jar Test Procedure | New | In line worth the requirements and procedure outlined in the Mt Crosby Westbank Wall Chart. |  | S Oldridge | 2015-10-01 | Y
44 | FRM-00793 | Supply System | PIK Instrument Verification Form | New | Identified as potential area of concern (internal audit) - developed to address that and Ventia ops practices. |  | S Oldridge | 2015-10-01 | Y
45 | PRO-01745 | Supply System | General Calibration of Online Instruments Operating Procedure | All | Identified as potential area of concern (internal audit) - developed to address ops practices. |  | S Oldridge | 2016-04-18 | Y
46 | PRO-01550 | Supply System | General Verifications of Online Instruments Operating Procedure | All | Change required to address ops practices and to include a requirement to notify the Control Room when the adjustment made goes above the acceptable tolerances (Section 3). |  | S Oldridge | 2016-04-18 | Y
47 | GDE-00176 | Supply System | Northern Pipeline Interconnector Supply System Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
48 | PLN-00048 | Mt Crosby Eastbank WTP | HACCP Plan | All | Document updated to reflect/address finding (i.e.areas of concern) identified at the SAI Audit and update any changes to process, chemicals used (suppliers) and on-line monitoring. |  | S Oldridge | 2016-08-04 | Y
49 | PLN-00049 | Mt Crosby Westbank WTP | HACCP Plan | All | Document updated to reflect/address finding (i.e. areas of concern) identified at the SAI Audit and update any changes to process, chemicals used (suppliers) and on-line monitoring. |  | S Oldridge | 2016-08-04 | Y
50 | PRO-01149 | Wivenhoe Dam WTP | KIP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
51 | PRO-02011 | Wivenhoe Dam WTP | HACCP Wall Chart Procedure | Table | Updated the Wall Chart to reflect changes and achieve consistency across regions. |  | S Oldridge | 2016-08-04 | Y
52 | PRO-02012 | Somerset Dam Township WTP | HACCP Wall Chart Procedure | Table | Updated the Wall Chart to reflect changes and achieve consistency across region; additionally, pre-filter dosing included (as optional) process step - reflected through the HACCP documentation. |  | S Oldridge | 2016-08-04 | Y
53 | REG-00169 | Wivenhoe Dam WTP | HACCP Risk Register | Table | Updated based on the outcome of the risk assessment workshop. |  | S Oldridge | 2016-04-01 | Y
54 | REG-00167 | Somerset Dam Township WTP | HACCP Risk Register | Table | Updated based on the outcome of the risk assessment workshop. |  | S Oldridge | 2016-04-01 | Y
55 | PLN-00149 | Somerset Dam Township WTP | Operational Monitoring Plan | Table | Removed second last paragraph and updated Table - references to the BSMP/KIP procedure (i.e. obsolete); additionally, pre-filter dosing included (as optional) process step - reflected through the HACCP documentation. |  | S Oldridge | 2016-06-14 | Y
56 | PRO-01174 | Somerset Dam Township WTP | Bulk Supply Monitoring Point Procedures | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
57 | PLN-00086 | Somerset Dam Township WTP | HACCP Plan | Flow Chart/Plan | Document updated to reflect/address finding (i.e. areas of concern) identified at the Internal and SAI Audit; and update any changes to process, chemicals used (suppliers) and on-line monitoring; additionally, pre-filter dosing included (as optional) process step - reflected through the HACCP documentation. |  | S Oldridge | 2016-06-14 | Y
58 | PLN-00105 | Wivenhoe Dam WTP | Operational Monitoring Plan | Table | Removed second last paragraph and updated Table - references to the BSMP/KIP procedure (i.e. obsolete). |  | S Oldridge | 2015-12-01 | Y
59 | PLN-00104 | Wivenhoe Dam WTP | HACCP Plan | Flow Chart/Plan | Document updated to reflect/address finding (i.e. areas of concern) identified at the Internal and SAI Audit, and update any changes to process, chemicals used (suppliers) and on-line monitoring. |  | S Oldridge | 2016-06-03 | Y
60 | REG-00578 | Supply System | HACCP Risk Register | Table | Updated based on the outcome of the risk assessment workshop and to include hazardous events associated with the Pipeline asset group (the pipeline inclusion developed in consultation with D. Shillito, D. Middleton and S Oldridge. |  | S Oldridge | 2016-04-19 | Y
61 | REG-00179 | Lowood WTP | HACCP Risk Register | Table | Updated based on the outcome of the risk assessment workshop. |  | S Oldridge | 2016-04-01 | Y
62 | REG-00180 | Esk WTP | HACCP Risk Register | Table | Updated based on the outcome of the risk assessment workshop. |  | S Oldridge | 2016-04-01 | Y
63 | PRO-01013 | Somerset Dam Township WTP | Raw Water CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
64 | PRO-01014 | Somerset Dam Township WTP | Clarification CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
65 | PRO-01015 | Somerset Dam Township WTP | Filtration CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
66 | PRO-01016 | Somerset Dam Township WTP | Disinfection procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
67 | PRO-01017 | Somerset Dam Township WTP | Distribution system CCP procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
68 | REG-00096 | Atkinson Dam WTP | HACCP Risk Register | NA | WTP offline. | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
69 | PRO-01018 | Wivenhoe Dam WTP | Raw Water CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
70 | PRO-01019 | Wivenhoe Dam WTP | Clarification CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
71 | PRO-01020 | Wivenhoe Dam WTP | Filtration CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
72 | PRO-01021 | Wivenhoe Dam WTP | Disinfection procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
73 | PRO-01022 | Wivenhoe Dam WTP | Distribution system CCP procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2015-12-01 | Y
74 | PRO-00354 | Esk WTP | Clarification CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
75 | PRO-00352 | Esk WTP | Disinfection CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
76 | PRO-00313 | Esk WTP | Filtration CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
77 | PRO-00310 | Esk WTP | Raw Water CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
78 | PRO-01147 | Esk WTP | KIP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
79 | PRO-01071 | Esk WTP | Fluoridation CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
80 | PRO-00354 | Esk WTP | Clarification CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
81 | PLN-00062 | Esk WTP | Operational Monitoring Plan | Table | Removed second last paragraph and updated Table - references to the BSMP/KIP procedure (i.e. obsolete). |  | S Oldridge | 2016-05-31 | Y
82 | PRO-02016 | Esk WTP | HACCP Wall Chart Procedure | Table | Updated the Wall Chart to reflect changes and achieve consistency across regions. |  | S Oldridge | 2016-08-04 | Y
83 | PRO-00351 | Lowood WTP | Raw Water CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
84 | PRO-00366 | Lowood WTP | Clarification CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
85 | PRO-01536 | Lowood WTP | Direct Filtration CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
86 | PRO-00413 | Lowood WTP | Filtration CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
87 | PRO-00389 | Lowood WTP | Disinfection CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
88 | PRO-01069 | Lowood WTP | Fluoridation CCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
89 | PRO-01464 | Lowood WTP | Manganese Control QCP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
90 | PRO-01148 | Lowood WTP | BSMP Procedure | NA | Procedure to become obsolete based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in other HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | S Oldridge | 2016-01-01 | Y
91 | PLN-00064 | Lowood WTP | Operational Monitoring Plan | Table | Removed second last paragraph and updated Table - references to the BSMP/KIP procedure (i.e. obsolete). |  | S Oldridge | 2016-01-01 | Y
92 | PRO-02015 | Lowood WTP | HACCP Wall Chart Procedure | Table | Updated the Wall Chart to reflect changes and achieve consistency across regions. |  | S Oldridge | 2016-01-01 | Y
93 | PLN-00063 | Lowood WTP | HACCP Plan | Flow Chart/Plan | Document updated to reflect/address finding (i.e. areas of concern) identified at the SAI Audit and update any changes to process, chemicals used (suppliers) and on-line monitoring. |  | S Oldridge | 2016-04-01 | Y
94 | PLN-00061 | Esk WTP | HACCP Plan | Flow Chart/Plan | Document updated to reflect/address finding (i.e. areas of concern) identified at the Internal and SAI Audit; and update any changes to process, chemicals used (suppliers) and on-line monitoring. |  | S Oldridge | 2016-08-04 | Y
95 | PRO-00711 | Mt Crosby Westbank WTP | Ipswich Supply through Kholo BSMPs | All | The procedure PRO-00711 Mt Crosby Westbank WTP - Bulk Supply Monitoring Procedure has been updated/revised – to reflect changes made. Please note the change of the title of this procedure to PRO-00711 Mt Crosby Westbank WTP - Ipswich Supply through Kholo BSMPs. |  | S Oldridge | 2015-01-01 | Y
96 | PRO-01747 | Supply System | Supply System - General Chemical Dosing Facility Inspection Procedure | All | The procedure was amended to reflect the current Chemical Dosing Facility Inspections carried by Seqwater and a service provider. |  | S Oldridge | 2016-02-01 | Y
97 | PRO-01557 | Supply System | Supply System - General Chemical Dosing Facility Inspection Procedure | NA | This procedure was made obsolete due to a double-up with PRO-01747. | Procedure archived in Qpulse | S Oldridge | 2016-02-01 | Y
98 | GDE-00182 | Supply System | Brisbane Bulk Transfer Network - Supply System Verification Sample Point Guide | Section 2.12 and Section 1 | ─ Inclusion of Sparkes Hill of the Sparkes Hill Reservoirs Combined Inlet (LW-BTA01-R026) sampling point; ─ Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-04 | Y
99 | GDE-00070 | Mt Crosby WTPs | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
100 | GDE-00072 | Lowood WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-27 | Y
101 | GDE-00073 | Esk WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
102 | GDE-00074 | Atkinson Dam WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
103 | GDE-00075 | Wivenhoe Dam WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-27 | Y
104 | GDE-00076 | Somerset Dam Township WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-27 | Y
105 | GDE-00183 | Supply System | Eastern Pipeline Interconnector - Supply System Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
106 | GDE-00184 | Supply System | Gold Coast Bulk Transfer - Supply System Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
107 | GDE-00185 | Supply System | Logan Bulk Transfer - Supply System Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
108 | GDE-00186 | Supply System | Network Integrated Pipeline - Supply System Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
109 | GDE-00188 | Supply System | Redlands Bulk Transfer - Supply System Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-01 | Y
110 | GDE-00189 | Supply System | Southern Regional Pipeline - Supply System Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. |  | S Oldridge | 2016-05-04 | Y
111 | PRO-02070 | Supply System | Supply System Bactiquant Sampling and Reporting Work Instruction | New | This work instruction provides a rapid assessment of total bacteria in water samples using the Bactiquant ® method. |  | S Oldridge | 2016-05-30 | Y
112 | PRO-01742 | Supply System | General Instrument Wet Rack Maintenance Procedure | All | The procedure was amended to reflect the instrument wet rack maintenance carried by Seqwater and a service provider. |  | S Oldridge | 2016-06-07 | Y
113 | PRO-01743 | Supply System | General Special Services to Online Instruments Procedure | All | The procedure was amended to reflect the special services to online instruments carried by Seqwater and a service provider. |  | S Oldridge | 2016-06-07 | Y
114 | PRO-01744 | Supply System | General Cleaning and Maintenance of Online Instruments Procedure | All | The procedure was amended to reflect the cleaning and maintenance of online Instruments carried by Seqwater and a service provider. |  | S Oldridge | 2016-06-07 | Y
115 | PRO-02089 | Supply System | HACCP Plan Wall Chart Procedure | New | The Wall Chart reflects changes and achieves consistency across regions and WTPs; it also replaces PRO-01549 and REG-00630. |  | S Oldridge | 2016-06-16 | Y
116 | PLN-00263 | Supply System | HACCP Plan | All | The HACCP Plan reflects changes (incl. Internal and SAI Global Audits) and achieves consistency across regions and WTPs. |  | S Oldridge | 2016-06-16 | Y
117 | REG-00579 | Supply System | Water Quality Alarm Response Register | Nil | The procedure did not require any changes. | Formal review and renewal. | S Oldridge | 2016-06-22 | Y
118 | PRO-01746 | Supply System | Operations Centre Escalation of WaterQuality Incidents | Nil | This procedure was made obsolete due to a double-up with PRO-00656. | Procedure archived in Qpulse | S Oldridge | 2016-06-22 | Y
119 | PRO-01552 | Supply System | WQM Incident Reporting, Investigation and Close-out | Nil | This procedure was made obsolete due to a double-up with PRO-00707. | Procedure archived in Qpulse | S Oldridge | 2016-06-22 | Y
248 | PRO-01986 | Westbank WTP | HACCP Plan Wall Chart Procedure | Raw Water, Coagulation, Manganese Removal | • Raw turbidity action limit slightly decreased. • Raw water conductivity removed limit and extended into a Summer and Winter limit • Alum deviation alarm time extended from 2 mins to 5 mins for action and critical limit. • Manganese removal free chlorine action limit increased slightly. • Grab samples identified in chart. | Changes made to assist with enhanced coagulation. | KM | 2017-06-30 | Y
249 | PRO-01985 | Eastbank WTP | HACCP Plan Wall Chart Procedure | Kholo Early Warning Station Raw Water, Coagulation, Manganese Removal, Primary Disinfection, Secondary Disinfection, Treated Water. | • Kholo Early Warning Station - Raw turbidity action limit slightly decreased. • Kholo Early Warning Station - Raw water conductivity removed limit and extended into a Summer and Winter limit • Eastbank raw turbidity action limit slightly decreased. • Eastbank raw water conductivity removed limit and extended into a Summer and Winter limit. • Alum deviation alarm time extended from 2 mins to 5 mins for action and critical limit. • Manganese removal free chlorine action limit increased slightly. • New primary disinfection turbidity limit added (inlet to Camerons Hill 1 & 2). • Time frame added to secondary disinfection pH limit. • Treated water turbidity action limit added for Camerons Hill 1 & 2. | Changes made to assist with enhanced coagulation. | KM | 2017-06-30 | Y
250 | REG-00179 | Lowood WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 28/07/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | KM | 2017-10-06 | Y
251 | REG-00153 | Mt Crosby WTPS | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop for Eastbank 25/09/17 and Westbank 9/10/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | KM | 2017-12-08 | Y
252 | REG-00180 | Esk WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop for Esk 09/11/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | KM | 2017-12-15 | Y
253 | REG-00180 | Somerset Dam Township WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop for Somerset Dam (Township) WTP 09/11/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | KM | 2018-01-19 | Y
254 | REG-00169 | Wivenhoe Dam WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop for Wivenhoe Dam (Recreation) WTP 20/11/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | KM | 2018-01-29 | Y
255 | REG-00578 | Supply System | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop for Supply System 21/11/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | KM | 2018-02-09 | Y
256 | PLN-00064 | Lowood WTP | Operational Monitoring Plan | Whole document | Reviewed and updated Sample Location description and Purpose as required. Updated the Introduction paragraph. Changed the process descriptions to align with the Risk Assessment. Changed the frequency of filtered water free chlorine to 'daily' from 'as required'. Changed manganese (soluble) to 'weekly' from 'As Required'. |  | KM | 2018-07-17 | Y
257 | PRO-02015 | Lowood WTP | Lowood WTP - HACCP Wall chart Procedure | Whole document | Raw Water • Have removed the critical limit for turbidity as it is no longer a critical limit. • Have added a soluble manganese action limit for raw water. • Have added an action limit for raw water Colour as per the Validation Standard. Coagulation • Coag pH – Have widened the range of the action limit so it has gone from 6.4 – 7.2 to 6.4– 7.0. Also shortened the timeframe for the critical limit from 30 mins to 15. • Added another line item/critical limit for no coagulant dose >5 mins. • Added settled water colour to coag section and removed from Floc and settling section. Limit is the same. Pre-Filter Hypo • Move to separate section before “Media Filtration” section called “Iron and Manganese Removal”. Increased target to 0.5 from 0.2 as per the validation plan. Added upper and lower chlorine limits to AL and CL. Disinfection • Changed CL res level from 30 to 55%. Previous figure was incorrect. Changed dosed filtered water free chlorine CL timeframe from 15 to 10 mins to align with C.t calc. • Added a treated water turbidity action limit. • Increased dosed filtered water chlorine critical limit upper limit from 4.0 mg/L to 4.5 mg/L. Reduced free chlorine action limit from 4.5 mg/L to 4mg/L. the action and critical limit values were around the wrong way. Supernatant • Turbidity critical limit was changed from 50 to 20 NTU to align with validation standard. Changed operational target from <5 to <10. • Added supernatant return flow rate critical limit. Operating Protocols on back table Updated operating protocol limits on back table as most of them were incorrect. |  | KM | 2018-08-01 | Y
258 | PLN-00063 | Lowood WTP | HACCP Plan |  | 2.1.3.8 Disinfection Updated C.t caclulation as it was incorrect. Section 3.2 HACCP Limit Validation Totally re-wrote table and added another 24 rows. Section 4.3 Materials and Chemicals Totally re-wrote section. |  |  | 2018-08-02 | Y
259 | PLN-00048 | Eastbank WTP | HACCP Plan | Section 3.2 HACCP Limit Validation | Totally re-wrote table and added additional detail. |  | KM | 2018-08-03 | Y
260 | PLN-00048 | Eastbank WTP | HACCP Plan | Section 4.3 Materials and Chemicals | Totally re-wrote section. |  | KM | 2018-08-03 | Y
261 | PLN-00049 | Westbank WTP | HACCP Plan | Section 3.2 HACCP Limit Validation | Totally re-wrote table and added additional detail. |  | KM | 2018-08-03 | Y
262 | PLN-00049 | Westbank WTP | HACCP Plan | Section 4.3 Materials and Chemicals | Totally re-wrote section. |  | KM | 2018-08-03 | Y
263 | PLN-00049 | Esk WTP | HACCP Plan | Section 3.2 HACCP Limit Validation | Totally re-wrote table and added additional detail. |  | KM | 2018-08-06 | Y
264 | PLN-00049 | Esk WTP | HACCP Plan | Section 4.3 Materials and Chemicals | Totally re-wrote section. |  | KM | 2018-08-06 | Y
263 | PLN-00104 | Wivenhoe Dam WTP | HACCP Plan | Section 3.2 HACCP Limit Validation | Totally re-wrote table and added additional detail. |  | KM | 2018-08-07 | Y
264 | PLN-00104 | Wivenhoe Dam WTP | HACCP Plan | Section 4.3 Materials and Chemicals | Totally re-wrote section. |  | KM | 2018-08-07 | Y
265 | PLN-00086 | Somerset Dam Township WTP | HACCP Plan | Section 3.2 HACCP Limit Validation | Totally re-wrote table and added additional detail. |  | KM | 2018-08-07 | Y
266 | PLN-00086 | Somerset Dam Township WTP | HACCP Plan | Section 4.3 Materials and Chemicals | Totally re-wrote section. |  | KM | 2018-08-07 | Y
267 | PLN-00086 | Somerset Dam Township WTP | HACCP Plan | Section 1.2 Conditions of Operation | Updated flow rates in the maximum and minimum sections of the table |  | KM | 2018-08-07 | Y
Submission to Regulator - Amendment Application August 2016
268 | PLN-00263 | Supply System | HACCP Plan | Front Page | Changed photo. |  | KM | 2018-11-08 | Y
269 | PLN-00263 | Supply System | HACCP Plan | Associated Documents Page 2 | Below added to Associated Documents section: Added all sample point guides. Added Chemical Panel List Register. Added Register of Prerequisite Programs (PRPs). |  | KM | 2018-11-08 | Y
270 | PLN-00263 | Supply System | HACCP Plan | Whole Document | Changed Risk Register reference to Water Quality Risk Dashboard 2017 throughout document. |  | KM | 2018-11-08 | Y
271 | PLN-00263 | Supply System | HACCP Plan | Figure 9. Schematic Drawing of Molendinar 3, 4, 5, 6 and 7 Reservoirs p32 | Added schematic of Molendinar Reservoirs to show piping and valving configuration. |  | KM | 2019-05-09 | Y
272 | [8 empty] | Y
273 | [8 empty] | Y
274 | PLN-00263 | Supply System | HACCP Plan | Figure 3 Brisbane Zone NorthProcess Flow Diagram p13 | Updated Figure 3 Brisbane Zone North Process Flow Diagram to include new doing infrastructure at Aspley WQMF |  | BH | 2019-05-28 | Y
275 | PLN-00263 | Supply System | HACCP Plan | Table 2 Brisbane Zone Process Flow Summary p15 | Created Aspley WQMF line in table. |  | BH | 2019-05-28 | Y
276 | PLN-00263 | Supply System | HACCP Plan | Section 4.4 Materials and Chemicals | Added 2 line items for chemicals to be used at Aspley. |  | BH | 2019-05-28 | Y
277 | PRO-02089 | Supply System | HACCP Wall Chart Procedure | Wall Chart Tab | Added Sections for Aspley WQMF South West and North East Panels including targets action and critical limits. |  | BH | 2019-05-28 | Y
278 | PRO-02089 | Supply System | HACCP Wall Chart Procedure | Corrective Actions Tab | Updated sections to incorporate Aspley corrective actions. |  | BH | 2019-05-28 | Y
279 | PRO-02089 | Supply System | HACCP Wall Chart Procedure | Cheat Sheet Corrective Actions Tab | Updated information to incorporate Aspley corrective actions in dosing facility section. Added information for Security Breeches Alarmed Hatches and Pipe Depressurisation sections. |  | BH | 2019-05-28 | Y
280 |  |  | Water Quality Risk Dashboard | Supply System Nov 17 Disinfection (Secondary) Risk Assessment rows 38 to 48 | Added Reference to Aspley WQMF in comments section |  | KM | 2019-05-24 | Y
281 | PLN-00063 | Lowood WTP | HACCP Plan | All sections | complete review |  | AC | 2019-07-09 | Y
282 | PRO-02015 | Lowood WTP | HACCP Wall Chart | All sections | review to reflect current SCADA capabilities |  | AC | 2019-07-09 | Y
283 | GDE-00076 | Somerset Dam Township WTP | WTP - Guide Verification Sample Point | Removed requirements for reticualted area sampling | Area is declared non porable and no more Seqwater testing required |  | AC | 2019-09-03 | Y
284 | PLN-00086 | Somerset Dam Township WTP | HACCP plan | All sections | complete review |  | AC | 2019-12-17 | Y
285 | PRO-02012 | Somerset Dam Township WTP | wallchart | All sections to reflect SCADA limitations | SCADA is unable to support AL and relevant corrective actions. |  | AC | 2019-12-17 | Y
286 | PLN-00149 | Somerset Dam Township WTP | monitoring plan | coagulation | to reflect advanced coagulation/ and conventional coagulation mode |  | AC | 2019-12-17 | Y
287 | GDE-00076 | Somerset Dam Township WTP | WTP - Guide Verification Sample Point | updated procedure descriptions | check of all related procedures and forms |  | AC | 2019-12-17 | Y
288 | PLN-00104 | Wivenhoe Dam WTP | HACCP plan | All sections | complete review |  | AC | 2019-11-28 | Y
289 | PRO-02011 | Wivenhoe Dam WTP | wallchart | All sections to reflect SCADA limitations | SCADA is unable to support AL and relevant corrective actions. |  | AC | 2019-11-28 | Y
290 | PLN-00105 | Wivenhoe Dam WTP | monitoring plan | All sections | complete review |  | AC | 2019-11-28 | Y
291 | GDE-00075 | Wivenhoe Dam WTP | WTP - Guide Verification Sample Point | updated procedure descriptions | check of all related procedures and forms |  | AC | 2019-11-28 | Y
292 | PRO-02089 | Supply System | HACCP Wall Chart | Noosa WTP | Changed all operational targets, action limits and critical limits to align with the Noosa WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
293 | PRO-02089 | Supply System | HACCP Wall Chart | Noosa WQBS | Changed all time frames to 15 mins from 30 mins for action and critical limits. |  | KM | 2019-12-01 | Y
294 | PRO-02089 | Supply System | HACCP Wall Chart | Ferntree | Changed turbidity action and critical limits to 15 mins frm 30 mins. |  | KM | 2019-12-01 | Y
295 | PRO-02089 | Supply System | HACCP Wall Chart | Landers Shute WTP | Changed all operational targets, action limits and critical limits to align with the Landers Shute WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
296 | PRO-02089 | Supply System | HACCP Wall Chart | Caloundra Street North | Reviewed and update chlorine operational targets and action limits. Timeframes for chlorine action and critical limits were changed to 15 mins from 30 mins. Reviewed and updated pH operational targets and action limits. Timeframes for pH critical limits were changed to 15 mins from 30 mins. Timeframe for turbidity action limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
297 | PRO-02089 | Supply System | HACCP Wall Chart | Caloundra Street South | Reviewed and update chlorine operational targets and action limits. Timeframes for chlorine critical limits were changed to 15 mins from 30 mins. Timeframes for pH action and critical limits were changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
298 | PRO-02089 | Supply System | HACCP Wall Chart | Morayfield | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
299 | PRO-02089 | Supply System | HACCP Wall Chart | Narangba - Combined Outlet | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
300 | PRO-02089 | Supply System | HACCP Wall Chart | North Pine Offtake | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
301 | PRO-02089 | Supply System | HACCP Wall Chart | North Pine WTP | Changed all operational targets, action limits and critical limits to align with the North Pine WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
302 | PRO-02089 | Supply System | HACCP Wall Chart | Byrnes Road | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
303 | PRO-02089 | Supply System | HACCP Wall Chart | Aspley | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
304 | PRO-02089 | Supply System | HACCP Wall Chart | Aspley WQMF South West | Reviewed and update chlorine operational targets and action limits. Reviewed and updated monochloramine operational targets and action limits. |  | KM | 2019-12-01 | Y
305 | PRO-02089 | Supply System | HACCP Wall Chart | Aspley WQMF North East | Reviewed and update chlorine operational targets and action limits. Reviewed and updated monochloramine operational targets and action limits. |  | KM | 2019-12-01 | Y
306 | PRO-02089 | Supply System | HACCP Wall Chart | Sparkes Hill Inlet | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
307 | PRO-02089 | Supply System | HACCP Wall Chart | Sparkes Hill Outlet | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
308 | PRO-02089 | Supply System | HACCP Wall Chart | Green Hill | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
309 | PRO-02089 | Supply System | HACCP Wall Chart | Wellers Hill | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
310 | PRO-02089 | Supply System | HACCP Wall Chart | Kuraby | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
311 | PRO-02089 | Supply System | HACCP Wall Chart | Mt Crosby WTP | Changed all operational targets, action limits and critical limits to align with the Mt Crosby WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
312 | PRO-02089 | Supply System | HACCP Wall Chart | Camerons Hill Connection | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
313 | PRO-02089 | Supply System | HACCP Wall Chart | Mt Crosby WTP/SRP Mixed Water | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
314 | PRO-02089 | Supply System | HACCP Wall Chart | North Beaudesert Balance Tank 1 (NBBT) | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
315 | PRO-02089 | Supply System | HACCP Wall Chart | North Beaudesert Balance Tank 2 (NBBT) | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
316 | PRO-02089 | Supply System | HACCP Wall Chart | Chambers Flat North | Reviewed and update chlorine operational targets and action limits. Timeframes for chlorine action and critical limits were changed to 15 mins from 30 mins. Reviewed and updated pH operational targets and action limits. Timeframes for pH action and critical limits were changed to 15 mins from 30 mins. Timeframe for turbidity action and critical limits was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
317 | PRO-02089 | Supply System | HACCP Wall Chart | Chambers Flat South | Timeframes for chlorine action and critical limits were changed to 15 mins from 30 mins. Reviewed and updated pH operational targets and action limits. Timeframes for pH action and critical limits were changed to 15 mins from 30 mins. Timeframe for turbidity action and critical limits was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
318 | PRO-02089 | Supply System | HACCP Wall Chart | Stapylton Balance Tank | Timeframes for chlorine action and critical limits were changed to 15 mins from 30 mins. Reviewed and updated pH operational targets and action limits. Timeframes for pH action and critical limits were changed to 15 mins from 30 mins. Timeframe for turbidity action and critical limits was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
319 | PRO-02089 | Supply System | HACCP Wall Chart | Molendinar WTP | Changed all operational targets, action limits and critical limits to align with the Molendinar WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
320 | PRO-02089 | Supply System | HACCP Wall Chart | Mudgeeraba WTP | Changed all operational targets, action limits and critical limits to align with the Mudgeeraba WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
321 | PRO-02089 | Supply System | HACCP Wall Chart | Tugun WTP | Changed all operational targets, action limits and critical limits to align with the Gold Coast Desalination Plant HACCP Treated Water Specification. |  | KM | 2019-12-01 | Y
322 | PRO-02089 | Supply System | HACCP Wall Chart | Capalaba WTP | Changed all operational targets, action limits and critical limits to align with the Capalaba WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
323 | PRO-02089 | Supply System | HACCP Wall Chart | NSI WTP | Changed all operational targets, action limits and critical limits to align with the NSI WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-01 | Y
324 | PRO-02089 | Supply System | HACCP Wall Chart | Gramzow Road East | Timeframes for chlorine action and critical limits were changed to 15 mins from 30 mins. Reviewed and updated pH operational targets and action limits. Timeframes for pH action and critical limits were changed to 15 mins from 30 mins. Timeframe for turbidity action and critical limits was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
325 | PRO-02089 | Supply System | HACCP Wall Chart | Gramzow Road West | Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
326 | PRO-02089 | Supply System | HACCP Wall Chart | Kimberley Park | Reviewed and update chlorine operational targets and action limits. Timeframe for chlorine critical upper limit was changed to 15 mins from 30 mins. |  | KM | 2019-12-01 | Y
327 | PRO-02089 | Supply System | HACCP Wall Chart | Noosa WTP | Changed operational targets and lower action limit for chlorine to align with the Noosa. |  | KM | 2019-12-18 | Y
328 | PRO-02089 | Supply System | HACCP Wall Chart | Noosa WQBS | Changed timeframe for operational targets to 15 mins from 30 mins. |  | KM | 2019-12-18 | Y
329 | PRO-02089 | Supply System | HACCP Wall Chart | Ferntree | Changed all time frames to 15 mins from 30 mins include operational targets. |  | KM | 2019-12-18 | Y
330 | PRO-02089 | Supply System | HACCP Wall Chart | Landers Shute WTP | Changed all operational targets, action limits and critical limits to align with the Landers Shute WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-18 | Y
331 | PRO-02089 | Supply System | HACCP Wall Chart | Caloundra Street North | Changed timeframe for operational targets to 15 mins from 30 mins. Changed pH action limit timeframe to 15 mins from 30 mins. Changed turbidity action limit timeframe to 15 mins from 30 mins. |  | KM | 2019-12-18 | Y
332 | PRO-02089 | Supply System | HACCP Wall Chart | Caloundra Street South | Changed chlorine action limit timeframe to 15 mins from 30 mins. Changed timeframe for operational targets to 15 mins from 30 mins. Changed all turbidity action and critical limit timeframes to 15 mins from 30 mins. |  | KM | 2019-12-18 | Y
333 | PRO-02089 | Supply System | HACCP Wall Chart | Morayfield | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
334 | PRO-02089 | Supply System | HACCP Wall Chart | Narangba - Combined Outlet | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
335 | PRO-02089 | Supply System | HACCP Wall Chart | North Pine OT | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
336 | PRO-02089 | Supply System | HACCP Wall Chart | North Pine WTP | Changed all operational targets, action limits and critical limits to align with the North Pine WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-18 | Y
337 | PRO-02089 | Supply System | HACCP Wall Chart | Byrnes Road | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
338 | PRO-02089 | Supply System | HACCP Wall Chart | Aspley | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
339 | PRO-02089 | Supply System | HACCP Wall Chart | Aspley WQMF South West | Changed timeframe for chlorine operational target and action limit to 15 mins from 30 mins. Changed timeframe for pH operational target and action limit to 15 mins from 30 mins. Changed monochloramine upper critical limit to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
340 | PRO-02089 | Supply System | HACCP Wall Chart | Aspley WQMF North East | Changed timeframe for chlorine operational target and action limit to 15 mins from 30 mins. Changed timeframe for pH operational target and action limit to 15 mins from 30 mins. Changed monochloramine upper critical limit to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
341 | PRO-02089 | Supply System | HACCP Wall Chart | Sparkes Hill Inlet | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
342 | PRO-02089 | Supply System | HACCP Wall Chart | Sparkes Hill Outlet | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
343 | PRO-02089 | Supply System | HACCP Wall Chart | Green Hill | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
344 | PRO-02089 | Supply System | HACCP Wall Chart | Wellers Hill | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
345 | PRO-02089 | Supply System | HACCP Wall Chart | Kuraby | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. pH upper critical limit removed. |  | KM | 2019-12-18 | Y
346 | PRO-02089 | Supply System | HACCP Wall Chart | Mt Crosby WTP | Removed 30 minute timeframe for the chlorine action limit. Added 30 minute timeframe to pH action limits |  | KM | 2019-12-18 | Y
347 | PRO-02089 | Supply System | HACCP Wall Chart | Camerons Hill Connection | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
348 | PRO-02089 | Supply System | HACCP Wall Chart | Mt Crosby WTP/SRP Mixed Water | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
349 | PRO-02089 | Supply System | HACCP Wall Chart | North Beaudesert Balance Tank 1 (NBBT) | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
350 | PRO-02089 | Supply System | HACCP Wall Chart | North Beaudesert Balance Tank 2 (NBBT) | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
351 | PRO-02089 | Supply System | HACCP Wall Chart | Stapylton Balance Tank | Changed lower turbidity timeframe from 30 mins to 15 mins. Changed lower chlorine action limit timeframe from 30 mins to 15 mins. |  | KM | 2019-12-18 | Y
352 | PRO-02089 | Supply System | HACCP Wall Chart | Molendinar WTP | Changed all operational targets, action limits and critical limits (including timeframes) to align with the Molendinar WTP HACCP Wall Chart Procedure. |  | KM | 2019-12-18 | Y
353 | PRO-02089 | Supply System | HACCP Wall Chart | Tugun WTP | Changed all operational targets, action limits and critical limits to align with the Gold Coast Desalination Plant HACCP Treated Water Specification. |  | KM | 2019-12-18 | Y
354 | PRO-02089 | Supply System | HACCP Wall Chart | Alexandra Hills Reservoirs | Changed the chlorine upper operational target, upper action limit and critical upper limit. Changed all timeframes from 30 mins to 15 mins |  | KM | 2019-12-18 | Y
355 | PRO-02089 | Supply System | HACCP Wall Chart | Heineman Road Reservoirs 2 & 3 Outlet | Changed pH action and critical limits to align with Heinemann Road Reservoir 1. |  | KM | 2019-12-18 | Y
356 | PRO-02089 | Supply System | HACCP Wall Chart | Heinemann Road Reservoirs | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
357 | PRO-02089 | Supply System | HACCP Wall Chart | Gramzow Road East | Changed the timeframe from 30 mins to 15 mins for chlorine operational target. |  | KM | 2019-12-18 | Y
358 | PRO-02089 | Supply System | HACCP Wall Chart | Gramzow Road West | Changed the timeframe from 30 mins to 15 mins for all operational targets, action limits and critical limits. |  | KM | 2019-12-18 | Y
359 | PRO-02089 | Supply System | HACCP Wall Chart | Kimberley Park | Changed chlorine upper critical limit timeframe to 30 mins from 15 mins. |  | KM | 2019-12-18 | Y
360 | PLN-00013 | Westbank WTP | Operational Monitoring Plan | Whole document | Format change - swapped around Location and Purpose columns to align with other plans. |  | KM | 2020-02-20 | Y
361 | PLN-00013 | Westbank WTP | Operational Monitoring Plan | Filtration CCP | Removed UV-254 testing from filtration step. |  | KM | 2020-02-20 | Y
362 | PLN-00013 | Westbank WTP | Operational Monitoring Plan | Manganese Control QCP | Removed Manganese (soluble) testing. |  | KM | 2020-02-20 | Y
363 | PLN-00013 | Westbank WTP | Operational Monitoring Plan | Sludge Thickening Tank Feed | Removed this section from the Operational Monitoring Plan as it is no longer required. Monitoring requirements are covered under the Supernatant Return CCP step. |  | KM | 2020-02-20 | Y
364 | PLN-00013 | Westbank WTP | Operational Monitoring Plan | Dewatering Facility | Removed this section from the Operational Monitoring Plan as it is no longer required. Monitoring requirements are covered under the Supernatant Return CCP step. |  | KM | 2020-02-20 | Y
365 | PLN-00063 | Lowood WTP | HACCP Plan | Process validation | Updates to include details around the alarming of alum dosing failures Redifine Action limits and Critical limits around disinfection. Switch AL low alarm to be a CL and high alarm to critical to reflect current SCADA arrangements and to emphasise criticality of low chlorine shutdown. Flows out of the reservoir have been reviewed to support the review of the c.t. |  | AC | 2020-05-11 | Y
366 | PRO-02015 | Lowood WTP | HACCP Wall Chart | Limit review | Alum flow alarm arrangements CL review to reflect SCADA arrangements and to include criticality of low chlorine alarm and shutdown arrangements |  | AC | 2020-05-11 | Y
367 | PLN-00061 | Esk WTP | HACCP Plan | Whole Document | Review of Flow diagram and schematic Defining oPRP raw water abstraction Additions to process description Process Validation including conditions of operations Revision of c.t. |  | AC | 2020-05-11 | Y
368 | PRO-02016 | Esk WTP | HACCP Wall Chart | Limit review | Filtered water turbidity Disinfection CCP |  | AC | 2020-05-11 | Y
369 | PLN-00062 | Esk WTP | monitoring plan | Raw Water | Change of raw water sampling point location |  | AC | 2020-06-03 | Y
370 | GDE-00073 | Esk WTP | Verification Sample Point Guide | Raw water | Sampling point change to Esk-SP121 |  | AC | 2020-06-03 | Y
371 | D17/73063 | Risk Assessment (Mitigated) Tab | Drinking Water Quality - (DWQ) Management Plan - Water Quality Risk Dashboard | Supply System | Full review of Supply System Risk Assessment. Added Supply Zone column and split out supply zones on individual lines where relevant. |  | KM | 2020-06-22 | Y
372 | D17/73063 | Attendees Tab | Drinking Water Quality - (DWQ) Management Plan - Water Quality Risk Dashboard | Whole Document | Added attendees for the Supply System Risk Assessment Review |  | KM | 2020-06-22 | Y
Submission to Regulator - Amendment Application August 2020
373 | PRO-01986 | Mt Crosby West bank WTP | HACCP Wall Chart | Whole document | Reviewed limits against Validation Standard with the following changes being made: - Have made changes to information around determining alum dose in the wall chart as alum look up table is obsolete and has been replaced by another procedure. - Raw water soluble manganese action limit changed from >0.1 mg/L to >0..5 mg/L after review of two years data. Also aligns with Validation Standard - Coagulation pH action limit time frame changed from 10 mins to 30 mins. - Flocculation and Settling true colour target changed from <3 HU to <2 HU. - Settled water turbidity action limit timeframe changed from 30 mins to 60 mins. - Removed action Limit for pH in the Manganese and Iron Control Step. - Have added flow rate critical limit for Supernatant Return of > 10% of the raw water flow. - Added new Critical limit for media filtration of >0.99 NTU for >60 seconds. - Have reviewed and updated Operating Protocol limits in Communications Water Quality Trigger Values table. - Removed From 27 reference throughout document and replaced with Risk Wizard reporting process. |  | KM | 2020-09-03 | Y
374 | PRO-02015 | Lowood WTP | HACCP Wall Chart | Limit review | CL filter turbidity alarm/ filter interlock time limit increased from 5 minutes to 15 minutes |  | AC | 2020-09-15 | Y
375 | PLN-00063 | Lowood WTP | HACCP Plan | 2.1.3 System overview 6 Material and chemicals | Description of chemicals to include chemical strength (as per REG-00250) |  | AC | 2020-12-23 | Y
376 | PLN-00061 | Esk WTP | HACCP Plan | 2.1.3 System overview 6 Material and chemicals | Description of chemicals to include chemical strength (as per REG-00250) |  | AC | 2020-12-23 | Y
377 | PLN-00086 | Somerset Dam Township WTP | HACCP Plan | 2.1.3 System overview 6 Material and chemicals | Description of chemicals to include chemical strength (as per REG-00250) |  | AC | 2020-12-23 | Y
378 | PLN-00104 | Wivenhoe Dam WTP | HACCP Plan | 2.1.3 System overview 6 Material and chemicals | Description of chemicals to include chemical strength (as per REG-00250) |  | AC | 2020-12-23 | Y
379 | PLN-00149 | Somerset Dam Township WTP | Monitoring plan | Parameter | Parameter to match the enhanced coagulation mode requirements |  | AC | 2021-01-04 | Y
380 | GDE-00072 | Lowood WTP | Verification Sample Point Guide | Whole document | Review of details and using new template |  | AC | 2021-01-11 | Y
381 | PRO-02016 | Esk WTP | wallchart | Limit review | Treated water AL set to Free Chlorine <1.5 or >3.0 mg/L for 30 min Alarm and CL Free Chlorine < 1.1 mg/L or >3.5 mg/L for 15 min Alarm and interlock. |  | AC | 2021-01-27 | Y
382 | GDE-00073 | Esk WTP | Verification Sample Point Guide | Whole document | Added new (LabWare) sample point code; updated sample point descriptions; added Fluoride QC sample point. |  | AC | 2021-03-05 | Y
383 | GDE-00072 | Lowood WTP | Verification Sample Point Guide | Whole document | Added new (LabWare) sample point code; updated sample point descriptions; added Fluoride QC sample point. |  | AC | 2021-03-05 | Y
384 | GDE-00076 | Somerset Dam Township WTP | Verification Sample Point Guide | Whole document | Added new (LabWare) sample point code; updated sample point descriptions; |  | AC | 2021-03-05 | Y
385 | GDE-00075 | Wivenhoe Dam WTP | Verification Sample Point Guide | Whole document | Added new (LabWare) sample point code; updated sample point descriptions; |  | AC | 2021-03-05 | Y
386 | PLN-00064 | Lowood WTP | Monitoring plan | Whole document | sampling location for the coag pH moved to clarifier inlet pipe Frequencies for media filtration true colour is monitored daily Sampling point locations to reflect new sampling point codes for raw and treated water |  | AC | 2021-03-15 | Y
387 | PLN-00104 | Wivenhoe Dam WTP | HACCP Plan | 2.1.3 System Overview | Included information around Baseload Population (Low Season) and Seasonal Maximum Population (High Season) |  | AC | 2021-05-12 | Y
388 | PRO-02011 | Wivenhoe Dam WTP | wallchart | Reservoir level | reviewed set points Layout to reflect new Riskwizrd notification requirements |  | AC | 2020-04-02 | Y
Submission to Regulator - DWQMP Annual Report 2021
389 | PRO-02015 | Lowood WTP | HACCP Wall Chart | monitoring column Definition of controls and reporting | Remove monitoring column Corrected typo as per audit findings Reporting requirements (CL) to reflect current practice |  | AC | 2021-07-23 | Y
390 | PLN-00063 | Lowood WTP | HACCP Plan | Element 2 (sections) | references to documentation linked to REX Revised the process descriptions to reflect recent changes and audit findings Revised schematic and process flow diagram |  | AC | 2021-07-27 | Y
391 | PLN-00064 | Lowood WTP | Monitoring plan | Raw, settled and treated water | Included requirements for UV 254 monitoring |  | AC | 2021-07-23 | Y
392 | GDE-00072 | Lowood WTP | Verification Sample Point Guide | 2.3 Lowood WTP Fluoride QC 2.4 Lowood WTP filtered water | Addition of photos of the sampling location Addition of sampling location for filtered water (THMFP) monitoring |  | AC | 2021-07-23 | Y
393 | PLN00048 | East Bank WTP | HACCP Plan | Section 1.2 Conditions of Operation | Reviewed and updated. |  | KM | 2021-08-10 | Y
394 | PLN00048 | East Bank WTP | HACCP Plan | 2.1.1 HACCP Team | Table has been updated. |  | KM | 2021-08-10 | Y
395 | PLN00048 | East Bank WTP | HACCP Plan | 2.1.2 Flow Diagrams | All flow charts, labelled photos and the schematic have been reviewed and updated. |  | KM | 2021-08-10 | Y
396 | PLN00048 | East Bank WTP | HACCP Plan | 2.1.3 System Overview | all parts of this section have been fully re-written. |  | KM | 2021-08-10 | Y
397 | PLN00048 | East Bank WTP | HACCP Plan | 2.2 Operational Changes | Reviewed and updated. |  | KM | 2021-08-10 | Y
398 | PLN00048 | East Bank WTP | HACCP Plan | 4.1 HACCP Limit Validation | Fully reviewed against the SPE-00320 Validation Standard and the HACCP Wall Chart and updated. |  | KM | 2021-08-10 | Y
399 | PLN00048 | East Bank WTP | HACCP Plan | 4.2 Pre-requisite Programs | Table reviewed and updated. |  | KM | 2021-08-10 | Y
400 | PLN00048 | East Bank WTP | HACCP Plan | 4.4 Materials and Chemicals | Section fully updated and re-written |  | KM | 2021-08-10 | Y
401 | PLN-00014 | East Bank WTP | Operational Monitoring Plan | Whole document | Reviewed whole document against the Plant Data Log and SPE-00320 and updated testing frequency, location and process step names. Updated Raw Water Abstraction to an oPRP from a CCP, Flocculation and Settling to an oPRP from QCP. Updated Manganese Control to a CCP from a QCP. |  | KM | 2021-08-11 | Y
402 | PLN-00013 | West Bank WTP | Operational Monitoring Plan | Whole document | Updated Flocculation and Settling to an oPRP from QCP. Updated Manganese Control to a CCP from a QCP. |  | KM | 2021-08-12 | Y
403 | PLN-00049 | West Bank WTP | HACCP Plan | Section 1.2 Conditions of Operation | Reviewed and updated. |  | KM | 2021-08-16 | Y
404 | PLN-00049 | West Bank WTP | HACCP Plan | 2.1.1 HACCP Team | Table has been updated. |  | KM | 2021-08-17 | Y
405 | PLN-00049 | West Bank WTP | HACCP Plan | 2.1.2 Flow Diagrams | All flow charts, labelled photos and the schematic have been reviewed and updated. |  | KM | 2021-08-18 | Y
406 | PLN-00049 | West Bank WTP | HACCP Plan | 2.1.3 System Overview | all parts of this section have been fully re-written. |  | KM | 2021-08-19 | Y
407 | PLN-00049 | West Bank WTP | HACCP Plan | 2.2 Operational Changes | Reviewed and updated. |  | KM | 2021-08-20 | Y
408 | PLN-00049 | West Bank WTP | HACCP Plan | 4.1 HACCP Limit Validation | Fully reviewed against the SPE-00320 Validation Standard and the HACCP Wall Chart and updated. |  | KM | 2021-08-21 | Y
409 | PLN-00049 | West Bank WTP | HACCP Plan | 4.2 Pre-requisite Programs | Table reviewed and updated. |  | KM | 2021-08-22 | Y
410 | PLN-00049 | West Bank WTP | HACCP Plan | 4.4 Materials and Chemicals | Section fully updated and re-written |  | KM | 2021-08-23 | Y
411 | PRO-01986 | West Bank WTP | HACCP Wall Chart Procedure | Whole document | Updated Flocculation and Settling to an oPRP from QCP. Updated Manganese Control to a CCP from a QCP. |  | KM | 2021-08-13 | Y
412 | GDE-00073 | Esk WTP | Verification Sample Point Guide | 2.1 Esk WTP Raw Water | New sampling point Old Code ESK-SP121 New Code TES-RAW-TAP-02 |  | AC | 2021-08-13 | Y
413 | PLN-00062 | Esk WTP | monitoring plan | UV 254 | monitoring included |  | AC | 2021-08-13 | Y
414 | PRO-02016 | Esk WTP | wallchart | Raw water Flocculation and settling | UV 254 monitoring included |  | AC | 2021-08-13 | Y
415 | PRO-02012 | Somerset Dam Township WTP | wallchart | raw coag pH settled water Reporting requirements | • Set limits for UV 254 raw, settled and treated water • Defined the coagulation pH indicating that enhanced coagulation is a the preferred operating mode. • Reviewed corrective action sections relevant to operating of the PAC plant • Settled water turbidity is no longer CL. Moved to AL and defined corrective action details • Reviewed Table 1 to indicate changes in the reporting requirements for AL and CL. |  | AC | 2022-04-12 | Y
416 | PLN-00086 | Somerset Dam Township WTP | HACCP Plan |  | 2.1.3.1 Raw water abstraction to include PAC dosing into oPRP 3.2 HACCP limit validation to reflect changes to: • The coagulation pH range, • Settled water turbidity has now changed to AL • Inclusion of UV 254 into the relevant process steps 6. Materials and chemicals • Inclusion of Carbon Acticarb PS 1000 into the list of approved chemicals. |  | AC | 2022-04-12 | Y
417 | PLN-00149 | Somerset Dam Township WTP | monitoring plan |  | • UV 254 monitoring to raw, settled and treated water |  | AC | 2022-04-12 | Y
418 | PLN-00063 | Lowood WTP | HACCP Plan |  | 1. Review of the validation table to include UV 254 limits 2. Review of approved chemicals: - Polymer Acrylamide Praestol DW25, formerly known as Magnafloc LT25 (25 Kg Bag) 5H4 - Addition of Hydrochloric Acid 32% w/w [as HCl] |  | AC | 2022-04-21 | Y
419 | Pro-02015 | Lowood WTP | Wallchart |  | 1. Inclusion of link to catchment water quality data at the Lowood PS 2. Inclusion of ‘Perform grab sample to verify test result immediately. If confirmed, notify the Operations Supervisor and PE (if further assistance is required)’ into AL corrective action guidance column 3. Sampling/ monitoring locations included into the Target, AL and CL columns 4. Definitions of controls and reporting to include reference to the PDL (AL exceedances) and Risk wizard (CL exceedances) 5. Settled water turbidity has now changed to AL |  | AC | 2022-04-21 | Y
420 | PLN-00104 | Wivenhoe Dam WTP | HACCP Plan |  | 2.1.2 Flow Diagram and schematic to include soda ash dosing 2.1.3.1 Raw water abstraction- to state details on reasons for Soda ash dosing and how it is managed 2.1.3.2 Coagulation, Flocculation and settling- as above 6 Materials and Chemicals Inclusion of Soda Ash Dense DSA-25PAP (25 Kg Bag) into the list of approved chemicals |  | AC | 2022-04-07 | Y
421 | PRO-02011 | Wivenhoe Dam WTP | wallchart |  | Raw water abstraction- to include monitoring for alkalinity changes and guidance on corrective action Reporting requirements to reflect desired practices during CL exceedances events. |  | AC | 2022-04-07 | Y
422 | PLN-00105 | Wivenhoe Dam WTP | monitoring plan |  | Include as required monitoring of alkalinity in settled water |  | AC | 2022-04-07 | Y
423 | PRO-01985 | East Bank WTP | HACCP plan wall chart procedure | Tables (last page) | Updated BWSA table to reflect new BWSA and Customer Service Standards Updated DWQ on-call number |  | DM | 2022-06-15 | Y
424 | PRO-01986 | West Bank WTP | HACCP plan wall chart procedure | Tables (last page) | Updated BWSA table to reflect new BWSA and Customer Service Standards Updated DWQ on-call number |  | DM | 2022-06-15 | Y
425 | PRO-02015 | Lowood WTP | HACCP plan wall chart procedure | Tables (last page) | Settled water process step updated as o-PRP consistent with SPE-00320 Updated BWSA table to reflect new BWSA and Customer Service Standards Updated DWQ on-call number |  | DM | 2022-06-15 | Y
Submission to Regulator - July 2022

## South
Central Operations Region - Register of changes to HACCP plans, procedures or related documents
# | Document Ref | WTP/System | HACCP Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | WSR Amendment Required (by Principal DWQ)
Example | PRO-05689 | Casey WTP | Disinfection CCP Procedure | s7, para2 & table | Validation updated for consistency with DWQMP Appendix 9.1 - Water Treatment Plant Process Validation Report | Validation also updated to reflect the effect of cold conditions at this site on disinfection C.t | Mawson | 2014-02-14 | N
1 | PLN-00071 | Mudgeeraba WTP | HACCP Plan | S. 1.2 Conditions of Operation S.2.1.0 HACCP Team S. 2.1.2 Flow Diagram and schematic diagram S.6 PRPs | - Conditions of Operation - Reduction in max volume from 110 ML/d to 105 ML/d (when bypass open) addition of maximum daily flow of 65 ML/d when bypass is closed which is normal operation. Also page 17 System Description. - Updated HACCP Team - Changes to the HACCP Process Flow Diagram & Schematic Diagram - Addition of clarifier bypass and filter bypass, Removal of references to Linkwater, update Allconnex Water to GCCC, Removal of online level monitoring in Clear Water Storage tank (will be added in upgrade to CWS), Fluoride dosing point changed to U/S res 1, Removal of online pH, Cl etc monitoring at Booster station. - Addition of Section 6 to include PRPs, as per INIR2875. | *Improvement Plan item MUD 20* Determine and document in conditions of operation the limiting process step at max flow (105 ML/d) | T Foote | 2014-05-01 | Y
2 | PRO-00467 | Mudgeeraba WTP | Raw Water CCP Procedure | S4. Monitoring table | - Removal of monitoring parameter - Apparent colour removed from monitoring. Apparent colour is a measure of particulate matter which is already measured as turbidity. Not required for operational monitoring purposes. True colour is sufficient for measuring dissolved organics. - Addition of monitoring paramters - Addition of Flow monitoring - online - continuous. Has always been in place but not listed in the table. - Addition of online VPS monitoring for pH, turbidity, conductivity, temp at Hinze upper intake and Little Nerang Dam. - CWQ monitoring frequency changed from 'weekly/quarterly' to 'monthly'. Frequency has always been monthly. | PLN-00072 Mudgeeraba WTP Monitoring Plan also updated | T Foote | 2014-05-01 | Y
3 | PRO-00472 | Mudgeeraba WTP | Pre-treatment CCP Procedure | S4. Monitoring table | - Lime dosing rate changed from 'Measured Dose Rate' to 'Calculated Dose Rate' calculated on SCADA and recorded daily in the Plantdata spreadsheet. It's not possible to measure (perform a drop down test) on the lime system. | PLN-00072 Mudgeeraba WTP Monitoring Plan also updated *Improvement Opportunity* Consider combining pre-treatment and coag, flocc and settling CCP procedures | T Foote | 2014-05-01 | Y
4 | PRO-00471 | Mudgeeraba WTP | Powdered Activated Carbon Dosing QCP Procedure | S3. Background S4. Monitoring table S5. Limits S7. Validation | - Frequency of Monitoring noted as 'when in use' and NFR is performed by the internal Process Lab. - Action limit change for cyanotoxin from 'CMP ALF Level 2 or 3' to 'CMP ALF ≥ Level 2' - Critical limit added for cyanotoxin 'treated water toxin detected' - Action limit change for T&O from 'CMP ALF Level 2' to 'CMP ALF ≥ Level 2 or Level 3' - Critical limit removed for T&O 'CMP ALF Level 3' - Action Limit now Critical Limit for 'Distributor reports > 10 algal related complaints received in 24 hours'. - Updates to validation to reflect changes to HACCP Limits. | PLN-00072 Mudgeeraba WTP Monitoring Plan also updated REG-00427 HACCP Plan Wall Chart also updated *Improvement Plan item MUD 16* Recommend PAC procedure be reviewed to reflect operation of PAC system rather than triggers associated with turning PAC system on i.e CMP triggers. | T Foote | 2014-05-01 | Y
5 | PRO-00476 | Mudgeeraba WTP | Clarification CCP Procedure | S3. Background S4. Monitoring table | -Note: No changes were required to the Description of coag, flocc and settling at Mudgeeraba WTP following the alum system upgrade. Storage, dosing point, dose rate determination and system dosing range remain unchanged. - Removal of monitoring parameter - Apparent colour removed from monitoring. Apparent colour is a measure of particulate matter which is already measured as turbidity. Not required for operational monitoring purposes. True colour is sufficient for measuring dissolved organics. - Addition of monitoring parameter - Addition of Online settled water turbidity instruments on the clarifier outlets. - Action Limit changed from '> 3 NTU Any test' to '> 3 NTU for > 60 mins'. Online turbidity instruments have been installed and are on SCADA. | PLN-00072 Mudgeeraba WTP Monitoring Plan also updated REG-00427 HACCP Plan Wall Chart also updated *Improvement Plan (NEW MUD 21)* Settled water turbidity instruments continuosly blocking and not considered accurate by Oeprators. Recommend flow through analysers be replaced by surface scatter analysers. | T Foote | 2014-05-01 | Y
6 | PRO-00485 | Mudgeeraba WTP | Filtration CCP Procedure | S4. Monitoring table S5. Limits | - Updates to location of monitoring parameter - Filter run time changed from 'calculated-daily-N/A' to 'online-continuous-SCADA' and Unit filter run volume location changed from 'N/A' to 'SCADA'. - Change to frequency of monitoring paramter - Filter media inspection changed from bi-annually to Annually per Filter. Backwash turbidity - end of filter backwash currently not performed twice weekly but during annual filter media inspection (added to improvement plan for investigation). - Action Limit timeframe updated for individual filtered water turbidity from '> 0.2 NTU For > 15 mins' to '> 0.2 NTU for > 60 mins'. This was a typo. Refer email DH and comment from CB 10/09/13, 30 mins is the agreed timeframe for Action Limit and is cosistent with Molendinar WTP. 'Production of water > 0.2 NTU for > 1 hour increases likelihood of failing the 95th percentile target for 4 log reduction of Cryptosporidium of 0.10 NTU. Triggers a HACCP report.' - Action Limit timeframe updated for combined filtered water turbidity as above from '> 0.2 NTU For > 15 mins' to '> 0.2 NTU for > 30 mins' - Critical Limit timeframe in Wall Chart states 'allow 30 minutes during ripening periods'. This has been added to the CCP procedure for consistency however this needs to be addressed. | *Improvement Plan (NEW MUD 22)* Filter backwash turbidity monitoring not performed twice weekly - performed during annual filter media inspection. Validate frequency of filter media inspections. WTP should be able to meet the standard and accepted HACCP Action limit (>0.2 NTU for 30 mins) and Critical limit (>0.3 NTU for > 15 mins) for individual filtered water turbidity. Review filtered water data and Mudgeeraba’s ability to meet the HACCP limits. Restriction of the filtered water to waste pump exists which extends ripening periods. This may require capital upgrades or operational changes to backwash and return to service sequence. | T Foote | 2014-05-01 | Y
7 | PRO-00486 | Mudgeeraba WTP | Disinfection CCP Procedure | S4. Monitoring | - Updates to location of treated water chlorine and treated water pH from 'Booster Pump station' to 'Outlet of Res # 2'. - Addition of Summer and Winter targets into HACCP plan as per Molendinar WTP. - Removal of estimation of flow split between reservoirs and bypass and inclusion of modelling outcome by KBR. Estimation was 60% through bypass and modelling outcome was 57% through bypass. | REG-00427 HACCP Plan Wall Chart also updated. | T Foote | 2014-05-01 | Y
8 | PRO-00488 | Mudgeeraba WTP | Supernatant Return CCP Procedure | S4. Monitoring S5. Limits S6. Validation | - Removal of monitoring parameter - visual inspection of 'sludge blanket' removed as a sludge blanket is not maintained. Visual inspection of the sludge handling areas are performed daily. - Addition of monitoring parameter - visual inspection of 'clarifier sludge bleed' daily. '- Change to Action and Critical Limit timeframes - the Action and Critical turbidity values for turbidity remain unchanged. Rather than the timeframe appyling continuously it is a cumulative timeframe when the supernatant is returning. It was decided not to base the timeframe on 'supernatant return events' as events vary in duration. | *Improvement Plan MUD 21* Supernatant return turbidity meter is reported as continuously blocking. It is currently an ultraturb flow through cell. Recommendation from Operators and Maintenace is to change it to a surface scatter intstrument. *Improvement Plan MUD 23* Calculation of ACtion and Crtical limit failures for supernatant return is difficult and time consuming. Recommend a 'HACCP Alarm Page' be developed on SCADA to allow automated counting of this and all HACCP limits as the HACCP limit doesn't apply when the supernatant is not returning and it is time consuming for Operators to calculate whether or not a HACCP excursion has occurred. | T Foote | 2014-05-01 | Y
9 | PRO-00483 | Mudgeeraba WTP | Manganese Removal QCP Procedure | S4. Monitoring table | - Notes added to identify that the internal process laboratory performs all Mn monitoring and Operators perform soluble Mn monitoring on raw water and total Mn monitoring on treated water. | PLN-00072 Mudgeeraba WTP Monitoring Plan also updated *Improvement Opportunity* Ensure monitoring to be rolled out by SS&DS using AA meets HACCP operational monitoring requirements. | T Foote | 2014-07-01 | Y
10 | PRO-00260 | Mudgeeraba WTP | Fluoridation CCP Procedure | S4. Monitoring | - Addition of Monitoring - Addition of 'Pre' and 'Post' Res # 2 grab sampling twice daily. Previously only listed online continuous monitoring. | PLN-00072 Mudgeeraba WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
11 | PRO-01184 | Mudgeeraba WTP | Bulk Supply Monitoring Point Procedure | S3. Background S5. Limits | - Change in Bulk Supply Point (BSP) from 'On the treated water main at the northern fenceline of the flow meter compound, approximately 170 m downstream of the WTP site gate on John Rogers Rd' to 'Refer to Schedule 5 – Bulk Water Supply Points which includes numerous the various locations and descriptions of Bulk Supply Points/Interface Points between Seqwater and Gold Coast City Council'. - Downstream entity changed from 'Allconnex Water and Linkwater' to 'Gold Coast City Council'. - Bulk Supply Monitoring Point photo updated from 'Sample tap is inside the fenced compound on the side of John Rogers Rd in vicinity of the entrance gate and the fire fighting equipment' to 'Sample tap is on outlet of Reservoir 2 and is a gooseneck tap. - Communications Triggers updated to reflect changes to the Nov 2013 Operating Protocol. Free chlorine changed from 0.7 mg/L to 0.5 mg/L; pH upper limit changed from 8.0 to 7.8; Removal of verification monitoring for pH - now only Operator Daily; TTHM and turbidity monitoring frequency changed from weekly to monthly, addition of Total Coliforms to table. - WGM - Seqwater Contract triggers updated - True colour sampling frequency changed from weekly to monthly; pH monitoring changed from weekly verification to daily Operator; Mn/Al acid sol/alkalinity monitoring changed from weekly to monthly. | *improvement Opportunity* Section 5. Limits includes the Comms Triggers for Mudgeeraba. The 'Source of Data' for Free Chlorine and Turbidity is listed as including 'Daily - Operator'. DWQ Coord to ensure this process is understood by Operators? | T Foote | 2014-07-01 | Y
12 | REG-00427 | Mudgeeraba WTP | HACCP Plan Wall Chart | Critical Limit summary Table. Bulk Supply Monitoring Point Communicaiton ReportingTable. | - PAC dosing limits changed to reflect upates to PAC CCP procedure above. - Filtered water turbidity limits changed to reflect updates to Filteration CCP procedure above. - Addition of Summer and Winter Operational Targets to reflect outcomes of Disinfection Strategy Trial with GCCC. Inclusion of note re review of residuals in May and Sep in Monitoring column. - Supernatant Return limits changed to reflect updates to Supernatant CCP procedure above. - Updates to Ops Protocols/Communications Triggers | Nil | T Foote | 2014-07-01 | Y
13 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | Table | - Monitoring verified to match QCP/CCP and Bulk Supply Monitoring Point procedures | Nil | T Foote | 2014-07-01 | Y
14 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | Monitoring Table | - Updates made as per CCP/QCP procedure updates for May 2014. | Nil | T Foote | 2014-07-01 | Y
15 | PLN-00069 | Molendinar WTP | HACCP Plan | S.2.1.0 HACCP Team S. 2.1.2 Flow Diagram and schematic diagram S.6 PRPs | - Updated HACCP Team - Changes to the HACCP Process Flow Diagram & Schematic Diagram - Addition of clarifier bypass and plant bypass, Removal of references to Linkwater, update Allconnex Water to GCCC, supernatant is now returned where?? - Operational Challenges - Removal of 'supernatant is returned downstreaqm of coagulant dosing' however this is no longer the case as teh alum and poly dosing is now into the inlet tower weir. - HACCP Process Flow Diagram - Addition of plant and clarifier bypasses, alum and polyDADMAC dosing point changed to Inlet Channel. - Molendinar Site Layout Schematic - info on supply to Southport West Main changed from 'Southport West Gravity Main is isolated and no longer used. The Southport West WSD is now supplied from Reservoir 4, 5, and 6. ' to 'Supply to Southport West is via the pumped main before the treated water enters Reservoirs 5 and 6. The Gravity Main valve to Southport West is closed'. - Addition of Section 6 to include PRPs, as per INIR2875. | *Improvement Plan item (new MOL XX)* Audit finding to confirm conditions of Operation (max daily production) due to inconsistencies between HACCP plan (150ML/d), Daily Sit Rep (144 ML/d) and Ops understanding. | T Foote | 2014-07-01 | Y
16 | PRO-00381 | Molendinar WTP | Raw Water CCP procedure | S.4 Monitoring | - Monitoring frequency changed for all VPS parameters from 3 hourly to hourly, Cyanobacteria changed from 'profile online' to monthly grab, CWQ monitoring frequency changed from 'weekly/quarterly' to 'monthly'. Frequency has always been monthly. '- Removal of monitoring parameter - Apparent colour removed from monitoring. Apparent colour is a measure of particulate matter which is already measured as turbidity. Not required for operational monitoring purposes. True colour is sufficient for measuring dissolved organics. | PLN-00070 Molendinar WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
17 | PRO-00387 | Molendinar WTP | Powdered Activated Carbon Dosing QCP Procedure | S4. Monitoring table S5. Limits S7. Validation | - Frequency of Monitoring for PAC dose changed fro 'Daily - when at PAC facility' to 'Daily - when in use', 'when in use' also added for other parameters and NFR is performed by the internal Process Lab, addition of 'Taste panel' to Taste and Odour testing. - Action limit change for cyanotoxin from 'CMP ALF Level 2 or 3' to 'CMP ALF ≥ Level 2' - Critical limit added for cyanotoxin 'treated water toxin detected' - Action limit change for T&O from 'CMP ALF Level 2' to 'CMP ALF ≥ Level 2 or Level 3' - Critical limit removed for T&O 'CMP ALF Level 3' - Action Limit now Critical Limit for 'Distributor reports > 10 algal related complaints received in 24 hours'. - Updates to validation to reflect changes to HACCP Limits. | PLN-00070 Molendinar WTP Monitoring Plan also updated REG-00425 HACCP Plan Wall Chart also updated *Improvement Plan item MUD 16 (ADD TO MOL)* Recommend PAC procedure be reviewed to reflect operation of PAC system rather than triggers associated with turning PAC system on i.e CMP triggers. *Improvement Plan item MOL XX* The PAC dosing system is not connected to the plant SCADA, rather alarms and basic functionality (dose pump speed) is available through the RADTEL SCADA system (Gold Coast City Council distribution system SCADA) – a legacy of SEQ Water Reform. | T Foote | 2014-07-01 | Y
18 | PRO-00390 | Molendinar WTP | Pre-treatment CCP procedure | S4. Monitoring table | - Lime dosing rate changed from 'Measured Dose Rate' to 'Calculated Dose Rate' calculated on SCADA and recorded daily in the Plantdata spreadsheet. It's not possible to measure (perform a drop down test) on the lime system. - Addition of parameter - addition of alkalinity monitoring twice daily in settled water. | PLN-00070 Molendinar WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
19 | PRO-00411 | Molendinar WTP | Clarification CCP procedure | S.3 Background S.4 Monitoring | - Description of coagulatant dosing point changed from raw water pipe to inlet tower (hydraulic jump). - Location of online dosed water pH monitoring changed from 'inlet channel' to 'inlet tower', location of grab pH monitoring changed from 'inlet channel' to 'settled water'. Turbidity monitoring (online and continuous) noted as being on 'individual' clarifier outlets which is current practice and required. - Removal of parameter - Apparent Colour from settled water, Apparant colour monitoring in treated water changed from Apparant colour to true colour (reflects current monitoring). | PLN-00070 Molendinar WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
20 | PRO-00436 | Molendinar WTP | Filtration CCP procedure | S.4 Monitoring | - Change to Location of monitoring of Filter Run Time and Unit Filter Run Volume from 'NA' to 'SCADA', Filter media inspection Frequency changed from 'bi-annually' to 'annually - each filter'. Previous wording misleading as there are six filters therefore one filter is inspected every two months so frequency of inspections hasn't changed however it reflects current practice more clearly. - Change of frequency of monitoring for filter backwash turbidity. A turbidity backwash profile is performed and recorded during a filter median inspection (annually) and is not performed weekly. | *Improvement Plan (NEW MUD 22) ALSO for MOL* Operators currently don't perform backwash water turbidity as per Monitoing Plan (PLN-00070) and Molendinar WTP Filtration CCP procedure (PRO- | T Foote | 2014-07-01 | Y
21 | PRO-00435 | Molendinar WTP | Disinfection CCP procedure | S.4 Monitoring | - Addittion of paramter - addition of online turbidity monitoring at end of clear water storage, addition of twice daily grab for turbidity at end of clear water storage. Currenlty in place. Addition of daily chlorine residual monitoring on the outlet of Reservoirs 3,4,5,6 as this currently appears in the Operating Protocol which was ratified Nov 2013. Reflect current Operation monitoring. | PLN-00070 Molendinar WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
22 | PRO-00133 | Molendinar WTP | Fluoridation CCP procedure | S.4 Monitoring | - Frequency of Monitoring changed from 'Minimum Daily' to 'twice daily'. Currently Ops performing three grab samples per day and each of the three sample points. Due to online monitoring and interlocks twice daily grab sample monitoring (inc analyser crosscheck) is acceptable. | PLN-00070 Molendinar WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
23 | PRO-00416 | Molendinar WTP | Manganese Removal QCP Procedure | S.4 Monitoring | - Addition of monitoring - addition of free chlorine residual online and grab sample at combined filter effluent. Reflects current monitoring. - Frequency of monitoring for individual filtered water free chlorine residual monitoring twice daily changed to 'twice daily (Mn event).' | PLN-00070 Molendinar WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
24 | PRO-00465 | Molendinar WTP | Supernatant Return CCP procedure | S.4 Monitoring | - Removal of monitoring parameter - visual inspection of 'sludge blanket' removed as a sludge blanket is not maintained. Visual inspection of the sludge handling areas are performed daily. - Addition of monitoring parameter - Addition of online continuos level monitoring. | PLN-00070 Molendinar WTP Monitoring Plan also updated | T Foote | 2014-07-01 | Y
25 | PRO01183 | Molendinar WTP | Bulk Supply Monitoring Point Procedure | S.5 Limits | - Downstream entity changed from 'Allconnex Water and Linkwater' to 'Gold Coast City Council' - Communications Triggers updated to reflect changes to the Nov 2013 Operating Protocol. Free chlorine changed from 0.7 mg/L to 0.5 mg/L; pH upper limit changed from 8.0 to 7.8; Removal of verification monitoring for pH - now only Operator Daily; TTHM and turbidity monitoring frequency changed from weekly to monthly, addition of Total Coliforms to table. Addittion of Free Chlorine Residuals at Reservoir 3,4,5,6 outlets which is <0.5 mg/L as per Ops Protocols Nov 2013. - WGM - Seqwater Contract triggers updated - True colour sampling frequency changed from weekly to monthly; pH monitoring changed from weekly verification to daily Operator; Mn,Al acid sol, alkalinity monitoring frequency changed from weekly to monthly. | *Improvement Opportunity* Section 5. Limits includes the Comms Triggers for Mudgeeraba. The 'Source of Data' for Free Chlorine and Turbidity is listed as including 'Daily - Operator'. DWQ Coord to ensure this process is understood by Operators. Consideration should be given to placing a HACCP limit on Reservoir outlet chlorine <0.5 mg/L as this is now in the Operation Protocols as of Nov 2013. | T Foote | 2014-07-01 | Y
26 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Table | - Monitoring verified to match QCP/CCP and Bulk Supply Monitoring Point procedures | Nil | T Foote | 2014-07-01 | Y
27 | REG-00424 | Molendinar WTP | HACCP Plan Wall Chart | Critical Limit summary Table. Bulk Supply Monitoring Point Communicaiton ReportingTable. | - PAC dosing limits changed to reflect upates to PAC QCP procedure above. - Inclusion of monitoring note in Disinfeciton CCP re review of network residuals in May and Sep in Monitoring column in relation to Summer and Winter setpoints. - Updates to Ops Protocols/Communications Triggers | Nil | T Foote | 2014-07-01 | Y
28 | REG-00427 | Mudgeeraba WTP | HACCP Plan Wall Chart | Critical Limit summary Table. | - Action Limit duration for Individual Filtered Water Turbidity changed from '30 minutes' to '60 minutes' as this was a typo in HACCP Plan Wall Chart. Refer to notes re change item # 6 above to PRO-00485 Mudgeeraba WTP Filtration CCP Procedure. Also refer to Improvement Plan Item MUD 22. | Refer Improvement Plan Item MUD 22 | T Foote | 2014-07-01 | Y
29 | PLN-00069 | Molendinar WTP | HACCP Plan | Pg 8 notes removed | - notes on pg 8 that were incorrectly not deleted before sending updates to Qpulse in May. | Nil | T Foote | 2014-07-01 | Y
30 | PLN-00091 | Beaudesert WTP | HACCP Plan | S 1.1 Scope 2.1.1 HACCP Team 2.1.2 Flow Diagram 5.1 Operational Procedures 5.2 Monitoring NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' | - Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. - HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meetings are recorded in the HACCP Risk Register or in the minutes of the meetings. - Flow Diagram now includes addition of UV dosing, inclusion of clarifier bypass, addition of ammonia monitoring, addition of coagulant flow monitoring. - Beaudesert Water Supply Scheme Schematic updated with South Maclean WTP removed. - Beaudesert WTP Schematic Diagram updated as per HACCP process flow diagram. - Aerial photograph now includes location of UV reactors (photograph doesn't include UV reactors' - System Overview details of each Process Step now includes any relevant information from 'Section 3 Background' of the CCP procedure and UV. - Operational Challenges updated - UV now installed which meets pathogen reduction log removal requirements, removal of requirement to implement Logan River Catchment HACCP Plan, inclusion of challenges around coagulant dosing control and raw water pH monitoring. - NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. - Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. - Overview of monitoring undertaken at WTPs has been transferred from CCP procedures and the Bulk Water Supply Monitoring Procedure. | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-08-01 | Y
31 | REG-00353 | Beaudesert WTP | HACCP Risk Register | Mitigated Risk Assessment & Summary Page | - Notes made to Mitigated Risk Comments for Coagulation and Filtration CCPs with regard to pot perm, pre-filter chlorine and soda ash dosing. This dosing not required at Beaudesert WTP and notes have been included to ‘tidy up’ their removal from the HACCP system. - Iron and manganese added to list of limiting hazards at Filtration and Clarification CCPs. Notes made to Mitigated Risk Comments for Filtration CCP with regard to Mn and Fe treatment and reduction. - Online settled water turbidity added to Clarification CCP Monitoring. - Notes updated in Mitigated Risk Comments for chlorination step with regard to baffle installation and improved baffle factor. - UV disinfection added as a Process Step. Single hazardous event of ‘Low UV dose’ which covers all scenarios such as poor upstream WTP processes and/or UV system fault. Mitigated (residual) Risk Rating was determined as Medium 5 and Process Step is a Critical Control Point (CCP). - Risk Rating for Whole of System Process Step for ‘Raw water contaminant load exceeds treatment capacity’ reduced from High 16 to Medium 5. Notes added re UV. - Fluoridation Preventative Measure alarm/shutdown value updated from 1.2 mg/L to 1.1 mg/L. - Updates to Attendee lists and Summary tabs as required. | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
32 | PLN-00092 | Beaudesert WTP | Operational Monitoring Plan | Monitoring Table | - Addition of 'Purpose' column - Updated to reflect current online and grab sample monitoring requirements based on new online instrumentation and UV system. - Removal of items that appear in checklists (eg coagulatant dose rate calculated). | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
33 | PRO-01186 | Beaudesert WTP | Bulk Supply Monitoring Point Procedure | All | - Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in othe HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
34 | PRO-00966 | Beaudesert WTP | Raw Water CCP Procedure | All | - Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
35 | PRO-00947 | Beaudesert WTP | Clarification CCP Procedure | All | - Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
36 | PRO-00965 | Beaudesert WTP | Filtration CCP Procedure | All | - Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
37 | PRO-00964 | Beaudesert WTP | Disinfection CCP Procedure | All | - Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
38 | PRO-01077 | Beaudesert WTP | Fluoridation CCP Procedure | All | - Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-11-01 | Y
39 | REG-00354 | Beaudesert WTP | HACCP Plan Wall Chart | Format of Table and Limits | - 'Hazards' and 'Preventative measures' columns removed as information already appears in the Risk Register. - Updates to monitoring based on new online instrumentation. - Corrective Actions seperated into 'Action Limit Corrective Actions' and 'Critical Limit Corrective Actions' - Refer to TRIM record D14/141358 for changes to to limits and the reasons for the changes. | Refer to TRIM document D14/140896 which illustrates the changes. | T Foote | 2014-12-01 | Y
40 | REG-00354 | Beaudesert WTP | HACCP Plan Wall Chart | UV Disinfection HACCP target and CL | UVT transmittance reduced to align with UV system controller setting | Refer to TRIM D15/31237 which highlights the changes | TF | 2015-03-01 | Y
41 | PLN-00092 | Beaudesert WTP | Operational Monitoring Plan | Purpose column | HACCP reportable parameter' listed next to parameters that are repotable under the HACCP system | Refer to TRIM D15/31238 which highlights the changes | TF | 2015-03-01 | Y
42 | PLN-00091 | Beaudesert WTP | HACCP Plan | UV Disinfection System overview and Validation | 2.1.3.10 updated to reflect description of UVT value Validation updated in accordance with UVT change. | Refer to TRIM D15/31240 which highlights the changes | TF | 2015-03-01 | Y
43 | PRO-01179 | North Stradbroke Island WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in othe HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | TF | 2015-04-01 | Y
44 | PRO-00824 | North Stradbroke Island WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-04-01 | Y
45 | PRO-01079 | North Stradbroke Island WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-04-01 | Y
46 | PLN-00040 | North Stradbroke Island WTP | HACCP Plan | All | Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meetings are recorded in the HACCP Risk Register or in the minutes of the meetings. Flow Diagram updated. Schematic Diagram updated as per HACCP process flow diagram. System Overview details of each Process Step now includes any relevant information from 'Section 3 NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. | Refer to TRIM document D15/47401 which illustrates the changes | TF | 2015-04-01 | Y
47 | REG-00365 | North Stradbroke Island WTP | HACCP Plan Wall Chart | All | Hazards' and 'Preventative measures' columns removed as information already appears in the Risk Register. List of moniotring replaced with Monitoring Plan reference and Operator Checklist reference Corrective Actions seperated into 'Action Limit Corrective Actions' and 'Critical Limit Corrective Actions' | Refer to TRIM document D15/47398 which illustrates the changes Critical Limit review shceduled for late 2015. Wall Chart Procedure will require updatin again. | TF | 2015-04-01 | Y
48 | PRO-00823 | North Stradbroke Island WTP | DAF QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-04-01 | Y
49 | PRO-00825 | North Stradbroke Island WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-04-01 | Y
50 | PRO-00826 | North Stradbroke Island WTP | Raw Water QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-04-01 | Y
51 | PLN-00076 | North Stradbroke Island WTP | Operational Monitoring Plan | Monitoring Table | Addition of 'Purpose' column Updated to reflect current online and grab sample monitoring requirements Removal of items that appear on operator checklists | Refer to TRIM document D15/47396 which illustrates the changes | TF | 2015-04-01 | Y
52 | REG-00085 | North Stradbroke Island WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks | Refer to TRIM document D15/17499 which illustrates the changes | TF | 2015-04-01 | Y
53 | REG-00377 | Rathdowney WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks Includes addition and Risk Assessment of NEW Supernatant Return Process Step | Refer to TRIM document D15/66141 which illustrates the changes | TF | 2015-08-19 | Y
54 | PLN-00093 | Rathdowney WTP | Operational Monitoring Plan | Monitoring Table | Addition of 'Purpose' column Updated to reflect current online and grab sample monitoring requirements Removal of items that appear on operator checklists Includes addition of NEW Supernatant Return Process Step Monitoring | Refer to TRIM D15/109736 which highlights the changes | TF | 2015-12-01 | Y
55 | REG-00354 | Beaudesert WTP | HACCP Plan Wall Chart | UV Disinfection HACCP target and CL | UVT transmittance reduced to align with UV system controller setting | Refer to TRIM D15/31237 which highlights the changes | TF | 2015-03-01 | Y
56 | PLN-00092 | Beaudesert WTP | Operational Monitoring Plan | Purpose column | HACCP reportable parameter' listed next to parameters that are repotable under the HACCP system | Refer to TRIM D15/31238 which highlights the changes | TF | 2015-03-01 | Y
57 | PLN-00091 | Beaudesert WTP | HACCP Plan | UV Disinfection System overview and Validation | 2.1.3.10 updated to reflect description of UVT value Validation updated in accordance with UVT change. | Refer to TRIM D15/31240 which highlights the changes | TF | 2015-03-01 | Y
58 | REG-00343 | Capalaba WTP | HACCP Plan Wall Chart | HACCP Limits | HACCP limits updated following Critical Limit Review workshop | Refer to TRIM D15/1238 which highlights the changes | TF | 2014-10-01 | Y
59 | PRO-01187 | Boonah-Kalbar WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in othe HACCP Operational Monitoring Plan, Verification Sample Point Guide and Wall Chart | Procedure archived in Qpulse | TF | 2015-10-28 | Y
60 | PRO-01127 | Boonah-Kalbar WTP | Iron and Manganese Removal QCP Procedure | All | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-10-28 | Y
61 | PRO-01127 | Boonah-Kalbar WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-10-28 | Y
62 | PRO-01124 | Boonah-Kalbar WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-10-28 | Y
63 | PRO-01123 | Boonah-Kalbar WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-10-28 | Y
64 | PRO-01122 | Boonah-Kalbar WTP | Raw water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-10-28 | Y
65 | PRO-01074 | Boonah-Kalbar WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2015-10-28 | Y
66 | PLN000119 | Boonah-Kalbar WTP | Operational Monitoring Plan | Monitoring Table | Addition of 'Purpose' column Updated to reflect current online and grab sample monitoring requirements Removal of items that appear on operator checklists | Refer to TRIM D15/165190 which highlights the changes | TF | 2015-10-28 | Y
67 | REG-00341 (now PRO-02003) | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | All | HACCP Limits updated following HACCP Limit review including addition of limits for new UV system 'Hazards' and 'Preventative measures' columns removed as information already appears in the Risk Register. List of moniotring replaced with Monitoring Plan reference and Operator Checklist reference Corrective Actions seperated into 'Action Limit Corrective Actions' and 'Critical Limit Corrective Actions' | Refer to TRIM D15/165223 which highlights the changes | TF | 2015-10-28 | Y
68 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | All | Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meetings are recorded in the HACCP Risk Register or in the minutes of the meetings. Flow Diagram updated now includes addition of UV dosing Schematic Diagram updated as per HACCP process flow diagram. System Overview details of each Process Step now includes any relevant information from 'Section 3 Background' of the CCP/QCP procedures and new section for UV. NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. | Refer to TRIM D15/165229 which highlights the changes Refer to TRIM D14/140896 which illustrates HACCP procedure streamlining process | TF | 2015-10-28 | Y
69 | REG-00342 | Boonah-Kalbar WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency UV process step added to Mitigated Risk Register Refer to Summary page for changes in significant risks | Refer to TRIM D15/31184 which highlights the changes | TF | 2015-10-28 | Y
70 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Monitoring Table | Addition of 'Purpose' column Updated to reflect current online and grab sample monitoring requirements Removal of items that appear on operator checklists Addition of 'HACCP Reportable parameter' against monitoring parameters which are HACCP reportable | Refer to TRIM D15/44425 which highlights the changes | TF | 2015-09-01 | Y
71 | REG-00425 | Molendinar WTP | HACCP Plan Wall Chart | Limits | Alkalinity adjusted to align with BWSA Fluoide limits adjusted to reflect the Code Manganese limits updated to reflect Process Validation Standard | Refer to TRIM D15/122615 which highlights the changes | TF | 2015-09-01 | Y
72 | PRO-004160 | Molendinar WTP | Manganese Removal QCP Procedure | Limits | Mangnese limits updated to reflect Process Validaiton Standard | Refer to TRIM D15/122621 which highlights the changes Note: this procedure will be archived following HACCP Critical Limit review workshop | TF | 2015-09-01 | Y
73 | PRO-00390 | Molendinar WTP | Pre-treatment CCP Procedure | 4. Monitoring 5. Limits | Section updates to align with updated Monitoring Plan and Wall Chart | Refer to TRIM D15/122623 which highlights the changes Note: this procedure will be archived following HACCP Critical Limit review workshop | TF | 2015-09-01 | Y
74 | PRO-00133 | Molendinar WTP | Fluoridation CCP Procedure | 5. Limits | Updates to align with Monitoring Plan and Wall Chart | Refer to TRIM D15/122625 which highlights the changes Note: this procedure will be archived following HACCP Critical Limit review workshop | TF | 2015-09-01 | Y
75 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Monitoring Table | Minor updates as dose rate checks are listed on Operator Checklists not in the Monitoring Plan | Refer to TRIM D15/122631 which highlights the changes | TF | 2015-09-01 | Y
76 | GDE-00056 | Moogerah Dam WTP | Verification Sample Point Guide | All. Sample taps unchanged | Updated format Included table with related procedures Updated SAWCS/online induction requirements Included document history table | Refer to TRIM D15/116035 | TF | 2015-09-01 | Y
77 | GDE-00057 | Kooralbyn WTP | Verification Sample Point Guide | All. Sample taps unchanged | Updated format Included table with related procedures Updated SAWCS/online induction requirements Included document history table | Refer to TRIM D15/116034 | TF | 2015-09-01 | Y
78 | GDE-00058 | Rathdowney WTP | Verification Sample Point Guide | All. Sample taps unchanged | Updated format Included table with related procedures Updated SAWCS/online induction requirements Included document history table | Refer to TRIM D15/114111 | TF | 2015-12-01 | Y
79 | GDE-00059 | Beaudesert WTP | Verification Sample Point Guide | All. Sample taps unchanged | Updated format Included table with related procedures Updated SAWCS/online induction requirements Included document history table Updated timing restrictions for Beaudesert WTP | Refer to TRIM D15/96697 | TF | 2015-09-01 | Y
80 | GDE-00068 | Mudgeeraba WTP | Verification Sample Point Guide | New treated water sample tap | Treated water sample tap details and photo updated | Refer to TRIM D15/53985 | TF | 2015-10-22 | Y
81 | REG-00353 | Beaudesert WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks | Refer to TRIM document D15/174038 which illustrates the changes | TF | 2015-10-27 | Y
82 | REG-00378 | Rathdowney WTP | HACCP Plan Wall Chart Procedure | Limits | Pre Res upper chlorine limits updated due to increased storage | Refer to TRIM document D15/184726 which illustrates the changes | TF | 2015-08-19 | Y
83 | PRO-01467 | Rathdowney WTP | Iron and Manganese Removal QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse. Refer TRIM D15/113484 | TF | 2015-08-19 | Y
84 | PRO-00968 | Rathdowney WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse Refer TRIM D15/113489 | TF | 2015-08-19 | Y
85 | PRO-00969 | Rathdowney WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse Refer TRIM D15/113486 | TF | 2015-08-19 | Y
86 | PRO-00967 | Rathdowney WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse Refer TRIM D15/113481 | TF | 2015-08-19 | Y
87 | PRO-00970 | Rathdowney WTP | Raw water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse Refer TRIM D15/113478 | TF | 2015-08-19 | Y
88 | PLN-00093 | Rathdowney WTP | Operational Monitoring Plan | Monitoring Table | Addition of 'Purpose' column Updated to reflect current online and grab sample monitoring requirements Removal of items that appear on operator checklists | Refer to TRIM D15/109136 which highlights the changes | TF | 2015-08-19 | Y
89 | REG-00378 (now PRO-01768) | Rathdowney WTP | HACCP Plan Wall Chart Procedure | All | HACCP Limits updated following HACCP Limit review (refer D15/80326) including addition of limits for Supernatant Return CCP. 'Hazards' and 'Preventative measures' columns removed as information already appears in the Risk Register. List of moniotring replaced with Monitoring Plan reference and Operator Checklist reference Corrective Actions seperated into 'Action Limit Corrective Actions' and 'Critical Limit Corrective Actions' | Refer to TRIM D15/109139 which highlights the changes | TF | 2015-08-19 | Y
90 | PLN-00094 | Rathdowney WTP | HACCP Plan | All | Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meetings are recorded in the HACCP Risk Register or in the minutes of the meetings. Flow Diagram updated now includes addition of UV dosing Schematic Diagram updated as per HACCP process flow diagram. System Overview details of each Process Step now includes any relevant information from 'Section 3 Background' of the CCP/QCP procedures and new section for UV. NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. | Refer to TRIM D15/165229 which highlights the changes Refer to TRIM D14/140896 which illustrates HACCP procedure streamlining process | TF | 2015-08-19 | Y
91 | PRO-01768 | Rathdowney WTP | HACCP Plan Wall Chart Procedure | Disinfection limits | Pre treated water tank free chlorine upper HACCP critical limit to be increased from 4.0 mg/L to 4.5 mg/L to overcome the filter water flow fluctuations and lack of flow paced chlorine dosing (Kith has a project underway to address this issue) and the chlorine decay being experienced with warmer temperatures and increased storage volumes. | Refer to TRIM D15/184726 which highlights the changes | TF | 2015-10-27 | Y
92 | REG-00166 | Maroon Dam WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks Addition of Raw Water and Treated Water summary tabs | Refer to TRIM D15/205263 which highlights changes | TF | 2015-12-30 | Y
93 | REG-00171 | Moogerah Dam WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks Addition of Raw Water and Treated Water summary tabs | Refer to TRIM D15/208589 which highlights changes | TF | 2015-12-30 | Y
94 | REG-00368 | Canungra WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks Addition of Raw Water and Treated Water summary tabs | Refer to TRIM D15/208778 which highlights changes | TF | 2015-12-30 | Y
95 | REG-00375 | Kooralbyn WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks Addition of Raw Water and Treated Water summary tabs Change over from magnasol 589 dosing to alum dosing considered as part of review. Note alum dosing had not commenced at time of risk assessment review | Refer to TRIM D15/80325 which highlights changes | TF | 2015-12-30 | Y
96 | REG-00441 | Hinze Dam WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks Addition of Raw Water and Treated Water summary tabs | Refer to TRIM D15/208778 which highlights changes | TF | 2015-12-30 | Y
97 | REG-00449 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Umitigated and Mitigated Risk reviewed in accordance with review frequency Refer to Summary page for changes in significant risks Addition of Raw Water and Treated Water summary tabs | Refer to TRIM D15/208608 which highlights changes | TF | 2015-12-30 | Y
98 | PRO-02028 | Mudgeeraba WTP | HACCP Plan Wall Chart Procedure | All | HACCP Limits updated following HACCP Limit review. Refer D15/196958. 'Hazards' and 'Preventative measures' columns removed as information already appears in the Risk Register as part of HACCP procedure streamlining initiative. List of moniotring replaced with Monitoring Plan reference and Operator Checklist reference Corrective Actions seperated into 'Action Limit Corrective Actions' and 'Critical Limit Corrective Actions' | Refer to TRIM D15/196970 which highlights the changes | TF | 2016-02-16 | Y
99 | REG-00426 | Mudgeeraba WTP | HACCP Risk Register | Various minor | All Unmitigated and Mitigated risks were reviewed and updated in previous revision however there were a couple of Improvement Items that needed to be clarified along with some other minor changes to wording. No changes to Risk Ratings or number of Improvement Items. | Refer to TRIM D16/75728 which highlights the changes | TF | 2016-02-16 | Y
100 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | Various minor | Minor updates to descriptions and notes as to which parameters are now ‘HACCP Reportable’ following the HACCP Limit Review. No changes to frequency/location/parameters. | Nil | TF | 2016-02-16 | Y
101 | PLN-00071 | Mudgeeraba WTP | HACCP Plan | All | Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meetings are recorded in the HACCP Risk Register or in the minutes of the meetings. Flow Diagram updated Schematic Diagram updated as per HACCP process flow diagram. System Overview details of each Process Step now includes any relevant information from 'Section 3 Background' of the CCP/QCP procedures updated with information transferred from CCP/QCP procedures NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. | Refer to TRIM D15/196988 which highlights the changes Refer to TRIM D14/140896 which illustrates HACCP procedure streamlining process | TF | 2016-02-16 | Y
102 | PRO-00467 | Mudgeeraba WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
103 | PRO-00471 | Mudgeeraba WTP | Powdered Activated Carbon Dosing QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
104 | PRO-00472 | Mudgeeraba WTP | Pre-treatment CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
105 | PRO-00476 | Mudgeeraba WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
106 | PRO-00483 | Mudgeeraba WTP | Manganese Removal QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
107 | PRO-00485 | Mudgeeraba WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
108 | PRO-00486 | Mudgeeraba WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
109 | PRO-00260 | Mudgeeraba WTP | Fluoridation CCP procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
110 | PRO-00488 | Mudgeeraba WTP | Supernatant Return QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
111 | PRO-01184 | Mudgeeraba WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-02-16 | Y
112 | PLN-00100 | Maroon Dam WTP | HACCP Plan | All | Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meetings are recorded in the HACCP Risk Register or in the minutes of the meetings. Flow Diagram updated Schematic Diagram updated as per HACCP process flow diagram. System Overview details of each Process Step now includes any relevant information from 'Section 3 Background' of the CCP/QCP procedures updated with information transferred from CCP/QCP procedures NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. | Refer to TRIM D15/205270 which highlights the changes Refer to TRIM D14/140896 which illustrates HACCP procedure streamlining process | TF | 2016-04-05 | Y
113 | PLN-00101 | Maroon Dam WTP | Operational Monitoring Plan | All | Various online monitoring had been installed at WTP and not incorporated into Operational Monitoring Plan. Plan now includes all online water quality monitoring for each CCP and daily crosschecks of online monitoring. | Refer to TRIM D16/75747 which highlights the changes | TF | 2016-04-05 | Y
114 | REG-00165 (now PRO-02054) | Maroon Dam WTP | HACCP Plan Wall Chart Procedure | All | Updated as per Critical Limit Review (D15/205274) . Chlorine CL low limit now reflects operation of tanks run in series. | Refer to TRIM D15/205274 which highlights the changes | TF | 2016-04-05 | Y
115 | PRO-01032 | Maroon Dam WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-05 | Y
116 | PRO-01033 | Maroon Dam WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-05 | Y
117 | PRO-01034 | Maroon Dam WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-05 | Y
118 | PRO-01035 | Maroon Dam WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-05 | Y
119 | PRO-01036 | Maroon Dam WTP | Distribution CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-05 | Y
120 | PRO-01192 | Maroon Dam WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-05 | Y
121 | PRO-02057 | Capalaba WTP | HACCP Plan Wall Chart Procedure | Various | All CCPs and QCP limits updated following HACCP Team Meeting Critical Limit Review 12/02/16. Refer TRIM D16/52427 | Refer to TRIM D16/52427 which highlights the changes to HACCP limits | TF | 2016-04-15 | Y
122 | PLN-00120 | Capalaba WTP | Operational Monitoring Plan | Various minor | Suggested changes are highlighted in yellow. Reflects outcomes of audit and the outcomes of Instrumentation Working Group. Now noted which parameters are now ‘HACCP Reportable’ following the HACCP Limit Review. | Refer to TRIM D16/35638 which highlights the changes | TF | 2016-04-15 | Y
123 | PLN-00037 | Capalaba WTP | HACCP Plan | All | Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meetings are recorded in the HACCP Risk Register or in the minutes of the meetings. Flow Diagram updated now includes addition of UV dosing Schematic Diagram updated as per HACCP process flow diagram. System Overview details of each Process Step now includes any relevant information from 'Section 3 Background' of the CCP/QCP procedures and new section for UV. NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. | Refer to TRIM D16/35637 which highlights the changes Refer to TRIM D14/140896 which illustrates HACCP procedure streamlining process | TF | 2016-04-15 | Y
124 | PRO-00800 | Capalaba WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-15 | Y
125 | PRO-00795 | Capalaba WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-15 | Y
126 | PRO-00789 | Capalaba WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-15 | Y
127 | PRO-00799 | Capalaba WTP | Manganese Removal QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-15 | Y
128 | PRO-00796 | Capalaba WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-15 | Y
129 | PRO-01080 | Capalaba WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-15 | Y
130 | PRO-01178 | Capalaba WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-15 | Y
131 | PRO-02058 (now PRO-02058) | North Stradbroke Island WTP | HACCP Plan Wall Chart Procedure | Disinfection limits | Disinfection C.t has been recalculated based on a minimum Treated Water Res level of 50% (applies when running through Res 1 or Res 2) and the HACCP Limit for min free chlorine has been increased from 0.5 mg/L up to 0.6 mg/L. Action limit has subsequently been increased by 0.1 mg/L. Target remains unchanged. The free chlorine limits and minimum reservoir level of 50% apply up to a maximum flow rate of 250 L/s when operating through Treated Water Res 2. If there is a need in future to increase flow above this level when operating through Res 2 only then the limits would need to be adjusted. | Refer to TRIM D16/50493 which highlights the changes | TF | 2016-04-18 | Y
132 | PLN-00076 | North Stradbroke Island WTP | Operational Monitoring Plan | Various minor | Process step alignment with Risk Register and HACCP flow diagram. No changes to parameters or frequencies. | Refer to TRIM D16/50489 which highlights the changes | TF | 2016-04-15 | Y
133 | PLN-00040 | North Stradbroke Island WTP | HACCP Plan | Data summary Validation Flow diagram Op Challenges | Removal of duplicated information which appears in risk register (data summary) or overarching Drinking Water Quality Management Plan which is not site specific. Validation section updated based on updated HACCP Limits. Conditions of Operation updated to include maximum flow rate when operating through Treated Water Res 2. HACCP Flow diagram updated. Service Water pump issue added to Operational Challenges section. | Refer to TRIM D15/65733 | TF | 2016-04-15 | Y
134 | REG-00085 | North Stradbroke Island WTP | HACCP Risk Register | Coagulation and DAF CCPs | Coagulation and DAF process steps separated. No changes to risk scores. Two Improvement Items added. Treated water and raw water data summaries added. | Refer to TRIM D15/50482 | TF | 2016-04-15 | Y
135 | PRO-01984 | Molendinar WTP | HACCP Plan Wall Chart Procedure | All | HACCP Limits updated following HACCP Limit review. Refer D16/76990. 'Hazards' and 'Preventative measures' columns removed as information already appears in the Risk Register as part of HACCP procedure streamlining initiative. List of monitoring replaced with Monitoring Plan reference and Operator Checklist reference Corrective Actions seperated into 'Action Limit Corrective Actions' and 'Critical Limit Corrective Actions' | Refer to TRIM D16/61556 | TF | 2016-04-29 | Y
136 | PLN-00069 | Molendinar WTP | HACCP Plan | All | Updates to regulatoray and governance terminology. Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation doucmentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact as the names of individuals who attend HACCP Risk Assessments and HACCP Team meeting attendees are recorded in the HACCP Risk Register or in the minutes of the meetings. Flow Diagram updated Schematic Diagram updated as per HACCP process flow diagram. System Overview details of each Process Step now includes any relevant information from 'Section 3 Background' of the CCP/QCP procedures updated with information transferred from CCP/QCP procedures NEW sections 'HACCP Limits and HACCP Limit Validation' and 'Review' transfered from CCP procedures into HACCP Plan. Removal of references to CCP procedures and information from these procedures is duplicated in the HACCP Plan, Risk Register, Wall Chart or Monitoring Plan. | Refer to TRIM D16/61557 | TF | 2016-04-29 | Y
137 | REG-00424 | Molendinar WTP | HACCP Risk Register | Various minor | All Unmitigated and Mitigated risks were reviewed and updated in previous revision however there were a couple of Improvement Items that needed to be clarified along with some other minor changes to wording. No changes to Risk Ratings or number of Improvement Items. | Refer to TRIM D16/61558 which highlights markups | TF | 2016-04-29 | Y
138 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Various minor | Minor updates to descriptions and notes as to which parameters are now ‘HACCP Reportable’ following the HACCP Limit Review. No changes to frequency/location/parameters. | Refer to TRIM D16/61559 which highlights markups | TF | 2016-04-29 | Y
139 | PRO-00381 | Molendinar WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
140 | PRO-00387 | Molendinar WTP | PAC Dosing QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
141 | PRO-00390 | Molendinar WTP | Pre-treatment CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
142 | PRO-00411 | Molendinar WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
143 | PRO-00436 | Molendinar WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
144 | PRO-00435 | Molendinar WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
145 | PRO-00133 | Molendinar WTP | Fluoridation CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
146 | PRO-00416 | Molendinar WTP | Manganese Removal QCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
147 | PRO-00465 | Molendinar WTP | Supernatant Return CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
148 | PRO-01183 | Molendinar WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-04-29 | Y
149 | REG-00344 | Capalaba WTP | HACCP Risk Register | Update to UV | UV CCP reviewed for go UV go live. Other items updated following audit. | Refer to TRIM D16/60648 | TF | 2016-05-03 | Y
150 | GDE-0063 | North Stradbroke Island WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
151 | GDE-00054 | Boonah-Kalbar WTP | Verification Sample Point Guide | Section 1 New format WTP name update | Notification required prior to sampling amended to include PASS application and PASS site access requirements. The word “Boonah” was removed from the document as the plant is now called just Kalbar WTP | NA | TF | 2016-05-06 | Y
152 | GDE-00055 | Maroon Dam WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
153 | GDE-00056 | Moogerah Dam WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
154 | GDE-00057 | Kooralbyn WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
155 | GDE-00058 | Rathdowney WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
156 | GDE-00059 | Beaudesert WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
157 | GDE-00062 | Capalaba WTP | Verification Sample Point Guide | Section 1 New format | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-03 | Y
158 | GDE-00064 | Dunwich WTP | Verification Sample Point Guide | Section 1 New format | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
159 | GDE-00065 | Amity Point WTP | Verification Sample Point Guide | Section 1 New format | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
160 | GDE-00061 | Canungra WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
161 | GDE-00067 | Molendinar WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
162 | GDE-00068 | Mudgeeraba WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
163 | GDE-00069 | Hinze Dam WTP | Verification Sample Point Guide | Section 1 | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
164 | GDE-00066 | Point Lookout WTP | Verification Sample Point Guide | Section 1 New format | Notification required prior to sampling amended to include PASS application and PASS site access requirements. | NA | TF | 2016-05-06 | Y
165 | PRO-02003 | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | Disinfection CCP limits | ‘Raw water inlet’ Process Step name changes to ‘Raw water abstraction’ as per WTP Process Validation Standard. Dosed filtered water tank inlet free chlorine HACCP Action Limit increased from 3.5 mg/L to 4.0 mg/L as per Operator suggestion to allow for chlorine dose into tank can be increased on start up from shut down to raise the outlet free chlorine levels as chlorine can decay with time in summer months. Dosed filtered water tank inlet free chlorine HACCP Critical Limit increased from 4.0 mg/L to 4.5 mg/L as above. ‘Treated water tank’ references changed to ‘Dosed Filtered Water Tank’ as tank is prior to UV disinfection and cannot be labelled ‘Treated Water’. | Refer to TRIM D16/74095 which highlights the changes | TF | 2016-05-17 | Y
166 | REG-00171 | Moogerah Dam WTP | HACCP Risk Register | Various minor | Minor updates to wording. Addition of Improvement Opportunity relating to distribution system turbidity. No change to risk ratings or process steps. Raw Water Intake nomenclature changed to Raw Water Abstraction as per SPE-00320 WTP Process Validation Standard. Risk Improvements changed to Improvement Opportunities. | Refer to TRIM D16/81848 which highlights markups | TF | 2016-06-01 | Y
167 | PLN-00107 | Moogerah Dam WTP | HACCP Plan | All | Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. | Refer to TRIM D16/81860 which highlights markups | TF | 2016-06-01 | Y
168 | PLN-00108 | Moogerah Dam WTP | Operational Monitoring Plan | All | Updates to monitoring to reflect current requirements and practices. Addition of ‘purpose’ column and notation against parameters that are reportable. Alignment of process steps with process steps in risk register. | Refer to TRIM D16/818656 which highlights markups | TF | 2016-06-01 | Y
169 | REG-00170 (now PRO) | Moogerah Dam WTP | HACCP Plan Wall Chart Procedure | All | Updates to HACCP limits as per HACCP limit review meeting D16/23909. | Refer to TRIM D16/188473 which highlights markups | TF | 2016-06-01 | Y
170 | PRO-01037 | Moogerah Dam WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-01 | Y
171 | PRO-01038 | Moogerah Dam WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-01 | Y
172 | PRO-01039 | Moogerah Dam WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-01 | Y
173 | PRO-01040 | Moogerah Dam WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-01 | Y
174 | PRO-01041 | Moogerah Dam WTP | Distribution CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-01 | Y
175 | PRO-01191 | Moogerah Dam WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-01 | Y
176 | PLN-00107 | Moogerah Dam WTP | HACCP Plan | Disinfection CCP | Section 2.1.3.6 Disinfection C.t calculation updated based on reduced treated water reservoir level. Section 3.2 HACCP limit validation Disinfection CCP updated to reflect changes. | Refer to TRIM D16/82532 for markups | TF | 2016-06-02 | Y
177 | REG-00170 (now PRO) | Moogerah Dam WTP | HACCP Plan Wall Chart Procedure | Disinfection CCP | Dosed filtered water and treated water free chlorine limits increased based on a request from Operators to reduce the minimum treated water level from 80% to 60% due to periods of high demand experienced during holiday periods in the system. | Refer to TRIM D16/82526 for markups | TF | 2016-06-02 | Y
178 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | New doc | Documented has always existed in Veolia's document management system and has now been uploaded into Seqwater's document management system for ease of access and reference. This documents is managed (reviewed, updated, audited) through Veolia’s management systems. The document review process involves a review step by the Water Quality Group of which representatives within our DWQ team are a part of (process documented in HACCP Plan). DWQ Coord will be aware of any updates and will forward these through to QPulse accordingly. | Doc is pdf | TF | 2016-06-10 | Y
179 | REF-00307 | Gold Coast Desalination Plant | HACCP Treated Water Quality Specification | New doc | Documented has always existed in Veolia's document management system and has now been uploaded into Seqwater's document management system for ease of access and reference. This documents is managed (reviewed, updated, audited) through Veolia’s management systems. The document review process involves a review step by the Water Quality Group of which representatives within our DWQ team are a part of (process documented in HACCP Plan). DWQ Coord will be aware of any updates and will forward these through to QPulse accordingly. | Doc is pdf | TF | 2016-06-10 | Y
180 | REF-00308 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated) | New doc | Documented has always existed in Veolia's document management system and has now been uploaded into Seqwater's document management system for ease of access and reference. This documents is managed (reviewed, updated, audited) through Veolia’s management systems. The document review process involves a review step by the Water Quality Group of which representatives within our DWQ team are a part of (process documented in HACCP Plan). DWQ Coord will be aware of any updates and will forward these through to QPulse accordingly. | Doc is pdf | TF | 2016-06-10 | Y
181 | REF-00310 | Gold Coast Desalination Plant | HACCP Risk Register (mitigated) | New doc | Documented has always existed in Veolia's document management system and has now been uploaded into Seqwater's document management system for ease of access and reference. This documents is managed (reviewed, updated, audited) through Veolia’s management systems. The document review process involves a review step by the Water Quality Group of which representatives within our DWQ team are a part of (process documented in HACCP Plan). DWQ Coord will be aware of any updates and will forward these through to QPulse accordingly. | Doc is pdf | TF | 2016-06-10 | Y
182 | REF-00309 | Gold Coast Desalination Plant | HACCP Validation Plan | New doc | Documented has always existed in Veolia's document management system and has now been uploaded into Seqwater's document management system for ease of access and reference. This documents is managed (reviewed, updated, audited) through Veolia’s management systems. The document review process involves a review step by the Water Quality Group of which representatives within our DWQ team are a part of (process documented in HACCP Plan). DWQ Coord will be aware of any updates and will forward these through to QPulse accordingly. | Doc is pdf | TF | 2016-06-10 | Y
183 | REG-00449 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Risk Register | Various minor | Minor updates to wording. Addition of Risk Treatment to assess condition of and remove Point Lookout Reservoir Bypass. This has been identified as a significant risk (medium 8). Raw Water Intake nomenclature changed to Raw Water Abstraction as per SPE-00320 WTP Process Validation Standard. Risk Improvements changed to Improvement Opportunities. | Refer to TRIM D16/87493 which highlights markups | TF | 2016-06-27 | Y
184 | PLN-00075 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. | Refer to TRIM D16/87492 which highlights markups | TF | 2016-06-27 | Y
185 | PLN-00144 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | Operational Monitoring Plan | All | Updates to monitoring to reflect current requirements and practice including addition of pre treated water reserovir analysers. Addition of ‘purpose’ column and notation against parameters that are reportable. Alignment of process steps with process steps in risk register. | Refer to TRIM D16/87490 which highlights markups | TF | 2016-06-27 | Y
186 | REG-00448 (now PRO-02099) | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan Wall Chart Procedure | All | Updates to HACCP limits as per HACCP limit review meeting D16/23910 | Refer to TRIM D16/87486 which highlights markups | TF | 2016-06-27 | Y
187 | PRO-00560 | Amity Point WTP | Fluoridation CCP procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
188 | PRO-00579 | Dunwich WTP | Fluoridation CCP procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
189 | PRO-00583 | Point Lookout WTP | Fluoridation CCP procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
190 | PRO-00602 | Dunwich WTP | Iron Removal and Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
191 | PRO-00603 | Amity Point WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
192 | PRO-00606 | Point Lookout WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
193 | PRO-01180 | Amity Point WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
194 | PRO-01181 | Dunwich WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
195 | PRO-01182 | Point Lookout WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-06-27 | Y
196 | PLN-00073 | Hinze Dam WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. | Refer to TRIM D16/93744 which highlights markups | TF | 2016-07-19 | Y
197 | PLN-00074 | Hinze Dam WTP | Operational Monitoring Plan | Various minor | No changes to frequency or location of monitoring currently occurring. Now noted which parameters are HACCP reportable. | Refer to TRIM D16/93729 which highlights markups | TF | 2016-07-14 | Y
198 | REG-00053 (now PRO) | Hinze Dam WTP | HACCP Plan Wall Chart Procedure | All | Updated as per CL review workshop and HTM last week | Refer to TRIM D16/93734 which highlights markups | TF | 2016-07-14 | Y
199 | REG-00441 | Hinze Dam WTP | HACCP Risk Register | PAC Process step Coag and Settling Process steps | PAC removed as a process step from R.A. Hazardous event of PAC dosing impacting raw water quality included in Raw Water CCP. Coagulation separated out from settling. Addition of requirement to confirm/assess/remove treated water reservoir bypass. Some minor updates including terminology of improvements. | Refer to TRIM D16/93763which highlights markups | TF | 2016-07-14 | Y
200 | PRO-01007 | Hinze Dam WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-14 | Y
201 | PRO-01008 | Hinze Dam WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-14 | Y
202 | PRO-01009 | Hinze Dam WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-14 | Y
203 | PRO-01010 | Hinze Dam WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-14 | Y
204 | PRO-01011 | Hinze Dam WTP | Distribution CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-14 | Y
205 | PRO-01217 | Hinze Dam WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-14 | Y
206 | PRO-00839 | Canungra WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
207 | PRO-00840 | Canungra WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
208 | PRO-00841 | Canungra WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
209 | PRO-00842 | Canungra WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
210 | PRO-01065 | Canungra WTP | Fluoridation CCP procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
211 | PRO-01188 | Canungra WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
212 | PLN-00102 | Canungra WTP | HACCP Plan | All | Streamlined: Increase in Scope of HACCP Plan document to include 'site specific details of each HACCP CCP' and Validation documentation' as part of the removal of duplication from the CCP procedures and integration of remaining information from the CCP procedures into the HACCP plan where appropriate. Updates to HACCP Team member position titles used and expectations rather than name/position/expertise/contact. Flow Diagrams updated. | Refer to TRIM D16/103878 which highlights markups | TF | 2016-07-25 | Y
213 | PLN-00007 | Canungra WTP | Operational Monitoring Plan | Various minor | No changes to frequency or location of monitoring currently occurring. Now noted which parameters are HACCP reportable. | Refer to TRIM D16/103873 which highlights markups | TF | 2016-07-25 | Y
214 | PLN-00369 (now PRO) | Canungra WTP | HACCP Plan Wall Chart Procedure | All | Updated as per CL review workshop | Refer to TRIM D16/103869 which highlights markups | TF | 2016-07-25 | Y
215 | REG-00368 | Canungra WTP | HACCP Risk Register | Minor | Some minor updates to terminology. Refer mark ups. | Refer to TRIM D16/103881 which highlights markups | TF | 2016-07-25 | Y
216 | PRO-00974 | Kooralbyn WTP | Raw Water CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
217 | PRO-00971 | Kooralbyn WTP | Clarification CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
218 | PRO-00973 | Kooralbyn WTP | Filtration CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
219 | PRO-00972 | Kooralbyn WTP | Disinfection CCP Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
220 | PRO-01100 | Kooralbyn WTP | Fluoridation CCP procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
221 | PRO-01189 | Kooralbyn WTP | Bulk Supply Monitoring Point Procedure | N/A | Procedure to become OBSELETE based on duplication and move to streamlining procedures. Relevant information from this procedure was transferred to the HACCP plan or is already duplicated in the HACCP Operational Monitoring Plan and Wall Chart | Procedure archived in Qpulse | TF | 2016-07-25 | Y
222 | PLN-00095 | Kooralbyn WTP | HACCP Plan | All | As per other HACCP Plans the plan now contains info that was in CCP procedures (to be archived). System overview updated to reflect upgrades. HACCP diagrams updated to reflect upgrades. HACCP limit validation reflects new HACCP limits. | HACCP limits, monitoring and associated corrective actions will become applicable on commencement of SAT (Chemicals) which is scheduled to start the week beginning 15/8. Refer markups TRIM D16/106664 | TF | 2016-07-25 | Y
223 | PLN-00096 | Kooralbyn WTP | Operational Monitoring Plan | All | Monitoring requirements reflects upgrades. | HACCP limits, monitoring and associated corrective actions will become applicable on commencement of SAT (Chemicals) which is scheduled to start the week beginning 15/8. Refer markups TRIM D16/106662 | TF | 2016-07-25 | Y
224 | REG-00376 (now PRO) | Kooralbyn WTP | HACCP Plan Wall Chart Procedure | All | HACCP limits updated based on numerous workshops and discussions to reflect upgrades. Will become a PRO. | HACCP limits, monitoring and associated corrective actions will become applicable on commencement of SAT (Chemicals) which is scheduled to start the week beginning 15/8. Refer HACCP CL review meeting D15/80326 | TF | 2016-07-25 | Y
225 | REG-00375 | Kooralbyn WTP | HACCP Risk Register | Various minor | Risk Register was updated in workshop in May last year with upgrades in mind. I have made some minor updates to terminology. No changes to hazardous events or risk ratings. | HACCP limits, monitoring and associated corrective actions will become applicable on commencement of SAT (Chemicals) which is scheduled to start the week beginning 15/8. Refer markups TRIM D16/106661 | TF | 2016-07-25 | Y
226 | REG-00377 | Rathdowney WTP | HACCP Risk Register | Various minor | ID numbers have been assigned to ‘Improvement Opportunities’ and these are now listed on the Summary tab. Treated water and raw water data summaries used in the R.A workshop have been added Current Risk column was dated 2013. Should state 2015. No updates to details/content. This will occur next year when we review the register in full. Updates to progress against Risk Treatments and Improvement Opportunities occurs at the quarterly HACCP team meetings. | Refer markups TRIM D16/107388 | TF | 2016-07-26 | Y
227 | REG-00353 | Beaudesert WTP | HACCP Risk Register | Various minor | ID numbers have been assigned to Improvement Opportunities. Removal of ‘count of ADWG exceedances’ from RW summary tab as not applicable. Current Risk column was dated 2013. Should state 2015. No updates to details/content. This will occur next year when we review the register in full. Updates to progress against Risk Treatments and Improvement Opportunities occurs at the quarterly HACCP team meetings. This site was audited in last month so the HACCP documents will be updated based on these findings in the next couple of months. | Refer markups TRIM D16/107394 | TF | 2016-07-26 | Y
228 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | Various minor | Updates to process schematic diagram – verification point is now before supernatant return point, new ID, bypass between raw water main and inlet to dosed filtered water reservoir added (not yet removed but planned to be), treated water tank now labelled as dosed filtered water reservoir. Minor changes to formatting and headings throughout doc. HACCP limits added to Section 3.2 HACCP Validation table. Previously only explanation of why the limits are what they are. | Refer markups TRIM D16/107397 | TF | 2016-07-27 | Y
229 | REG-02003 | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | Various minor | updates to naming. No changes to limits. Refer markups. | Refer markups TRIM D16/107400 | TF | 2016-07-27 | Y
230 | REG-00342 | Boonah-Kalbar WTP | HACCP Risk Register | Various minor | ID numbers have been assigned to Improvement Opportunities and added to Summary page. Addition of hazardous event for ‘Mercury contaminating treated water’ from UV lamp breakage added as per other sites with UV disinfection. Improvement item raised for development of procedure regarding this event. | Refer markups TRIM D16/107405 | TF | 2016-07-27 | Y
231 | REG-00354 (now PRO) | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Document number | change the document ID of [REG-00354 Beaudesert WTP – HACCP Plan Wall Chart Register] to [PRO-xxxxx Beaudesert WTP – HACCP Plan Wall Chart Procedure]. Document was 'streamlined' in 2015 however doc ID was not changed over as per other Wall Charts. Update the header of the document from ‘Register’ to ‘Procedure’ | No change to limits or content. Review to occur following finalisation of IMS audit report | TF | 2016-07-19 | Y
232 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | Flow diagrams Operational challenges | HACCP flow diagram process schematic updated to included ‘normally closed’. Raw water to QUU network bypass/cross connection also removed under recent project so has been removed from diagrams. Raw water to dosed filtered water tank currently still in placed but due for removal within weeks. Clarifier bypass will remain. Delete filter bypass (is already removed) Operational challenges updated to include lack of onsite storage due to UV being after storage tank. Operational challenge also added for supernatant return lagoons receiving storm flow runoff and return pump being fixed speed and oversized. | Refer markups TRIM D16/134296 | TF | 2016-09-16 | Y
233 | PLN-00119 | Boonah-Kalbar WTP | Operational Monitoring Plan | Coagulation CCP | Addition of dosed water pH grab/ validation of online instrument result Accidental omission from MP. Operators were performing daily grab sample despite it not being documented in the plan. Plan has been updated. | Refer markups TRIM D16/134299 | TF | 2016-09-16 | Y
234 | GDE-00063 | Boonah-Kalbar WTP | Verification Sample Point Guide | Raw water sample point | Raw water sample point relocated. New photo, ID and coordinates. | Refer markups TRIM D16/134300 | TF | 2016-09-16 | Y
235 | REG-00342 | Boonah-Kalbar WTP | HACCP Risk Register | Whole of system | IMS audit July 2016 findings: 1. According to the RA the UV must be operating if WTP is operating. There is a UV bypass in place that should be removed and this should be documented in the RA. – Now documented in Whole of System. Also documented in Improvement Plan. 2. There is a large swallow colony (nests) below the clarifier. Consider any hazard that may cause hazards to the process and in particular to the clear water storage nearby (not vermin proof). – Swallow colony does not pose risk to water quality in clarifier. Risk exists with insufficient vermin proofing on dosed filtered water reservoir. Refer NC/1 in audit report. As a result REG-00342 Kalbar WTP HACCP Risk Register hazardous event ‘Animals contaminating chlorinated water storage’ has been updated and increased from Medium 5 (Rare-major) to Medium 8 (Unlikely-Major) making this a significant risk. An improvement item ALL24 already existed for this hazardous event and this has been updated based on the audit findings. The Improvement Plan (D15/200) has been updated accordingly for ALL24 for Kalbar WTP. 3. Add mode when clarifier bypass is opened and address hazards - As this is not considered normal operation this would be considered a change of operating conditions and an increase in risk which would also trigger regulator notification. If short term direct filtration mode was being considered to allow for maintenance or project works a risk assessment would need to be undertaken at the time to assess the current risk taking into consideration the log reduction requirements of the WTP and the monitoring and performance criteria that would need to be achieved by other process steps in order to claim log reduction credits. REG-00342 Kalbar WTP HACCP Risk Register hazardous event ‘Failure or incorrect operation of a bypass valve’ has been updated to include the requirement to perform a risk assessment at the time rather than risk assessing this mode of operation pre-emptively. | Refer markups TRIM D16/134301 | TF | 2016-09-16 | Y
236 | PLN-00040 | North Stradbroke Island WTP | HACCP Plan | Flow diagrams Section 2.1.3 overview for Supernatant return | Flow diagram updated documenting Supernatant return process step as a PRP not a CCP. Explanation provided in Section 2.1.3.3. | Refer markups TRIM D16/135199 | TF | 2016-09-19 | Y
237 | PLN-00076 | North Stradbroke Island WTP | Operational Monitoring Plan | Raw water abstraction | Change nomenclature ‘Raw Water Intake’ to ‘Raw Water Abstraction’ to align with standardised naming of process steps | Refer markups TRIM D16/135200 | TF | 2016-09-19 | Y
238 | PRO-02058 | North Stradbroke Island WTP | HACCP Plan Wall Chart Procedure | Dosed water DAF | Dose water pH critical limit incorrectly stated as ‘>5.3’ when should be ‘<5.3’ A critical limit is in place for the DAF for outlet colour however there was ‘N/A’ in the Critical Limit Corrective Actions guidance column. Column has been updated and guidance is as per critical limit exceedance for the Coagulation CCP. | Refer markups TRIM D16/135203 | TF | 2016-09-19 | Y
239 | REG-00085 | North Stradbroke Island WTP | HACCP Risk Register | Supernatant Return Raw water Abstraction | Change nomenclature ‘Raw Water Intake’ to ‘Raw Water Abstraction’ to align with consistent naming of process steps Supernatant return CCP assessment outcome changed from ‘QCP’ to ‘PRP’ and commentary added to CCP comment column. | Refer markups TRIM D16/135205 | TF | 2016-09-19 | Y
240 | GDE-00055 | Maroon Dam WTP | Verification Sample Point Guide | Treated water sample tap and distributions system sample tap | Treated water sample tap relocated to after treated water sample pumps. Previously located on 1 of 3 treated water tanks which can be operated in various arrangements. Distribution system sample tap relocated due to vacation of houses on supply line to tap resulting in unrepresentative sample of system | Refer markups TRIM D16/142492 | TF | 2016-09-30 | Y
241 | GDE-00057 | Kooralbyn WTP | Verification Sample Point Guide | Raw water sample point | Raw water sample tap relocated following project works | Refer markups TRIM D16/142671 | TF | 2016-09-30 | Y
242 | PLN-00071 | Mudgeeraba WTP | HACCP Plan | 1.2 Conditions of Operation 2.1.2 Flow diagram 2.1.3 Process description 2.1.4 Opreational challenge 3.2 HACCP limit validation | • 1.2 Conditions of Operation updated to describe the improvements to WTP interlock functionality • 2.1.2 Updates to HACCP flow diagram and schematic diagram to include clarifier bypass, poly type, stormwater and chem bund flows as intermittent input to supernatant return tank, reversal of order of hypo (now first) then caustic (now second) at Disinfection CCP, delineation of key interface point between CoGC and Supply System, optional lime dosing into inlet channel, • 2.1.3 Oder of process steps to be re-ordered to align with Risk Assessment and HACCP Process Flow diagram. Description of lime venture dosing arrangement in Coagulation section. Inclusion of detail of which polymers are used where. Description around existence of clarifier bypass. Updates to description of summer v. winter free chlorine targets now remaining at summer target, supernatant return system description updated to describe upgrades. • 2.1.4 Operational challenge regarding high levels in supernatant return tank and washwater recovery tank preventing filters being able to backwash following rainfall due to stormwater runoff. • 3.2 HACCP Limit validation - further detail added on HACCP limits and supporting validation. | Refer markups TRIM D17/54447 | TF | 2017-04-21 | Y
243 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | order of process steps | • Order of process steps to be re-ordered to align with Risk Assessment and HACCP Process Flow diagram. No changes to frequencies or parameters | Refer markups TRIM D17/54449 | TF | 2017-04-21 | Y
244 | PRO-02028 | Mudgeeraba WTP | HACCP Plan Wall Chart Procedure | Raw water Supernatant Return Coagulation Disinfection Fluoride | • Raw water Abstraction raw water turbidity HACCP limit changed from >10 NTU to change ±10 NTU, timeframe reduced from 2 hours to 30 mins as per standard, Critical limit for turbidity removed, • Supernatant return CCP Action Limit increased from >10 NTU to >15 NTU, Critical Limit new % return >10% of raw water flow for 15mins, Critical Limit for pH timeframe reduced from 15 mins to 5 mins to prevent unnecessary additional alum being returned to inlet channel, critical limit corrective action guidance updated to include bottleneck scenario • Coagulation CCP dosed water pH lower critical limit increased from 5.7 to 5.8 to align with Validation Standard, new dosed water pH critical limit when dosing pot perm to align with Validation Standard, Critical Limit correction action guidance updated with regard to recovering from loss of alum dose • Disinfection CCP targets now consistently at ‘summer’ levels rather than ‘summer’ or ‘winter’, reservoir level new target and critical limit based on C.t inputs, critical limit corrective action guidance updated to include option to recover low chlorine • Fluoride CCP pre reservoir critical limit timeframe reduced from 15mins to 2mins • Removal of Treated Water as a process step • Nomenclature for ‘clear water’ and ‘Res 2’ changed to ‘treated water’ • All CCPs where a WTP shutdowns is the consequence of CL exceedance - corrective action guidance updated to include notification to Seqwater Control room within 30 mins of shutdown | Refer markups TRIM D17/54448 | TF | 2017-04-21 | Y
245 | PRO-02057 | Capalaba WTP | HACCP Plan Wall Chart Procedure | Manganese UV Disinfection Free Chlorine Disinfection Fluoridation | • Manganese Removal QCP – new raw water manganese soluble Action Limit of >0.1 mg/L. Refer data attached. A raw water soluble result of 0.1 mg/L would indicate higher than typically seen levels of manganese in the raw water. • UV Disinfection CCP – UVT target reduced from >85% to >80% which is consistent with WTP targets and the UV validation (i.e not <80%) • Free Chlorine Disinfection CCP – C.t volumes reviewed resulting in change to treated water critical limit from <1.0 mg/L to <0.8 mg/L and the treated water action limit from 1.2 mg/L to 1.0 mg/L. • Treated water pH target now the same as dosed water pH target. C.t action limit and critical limit removed for now. • Fluoridation CCP – volumes reviewed resulting in timeframe for pre reservoir fluoride critical limit reducing from 15 mins to 12 mins. | Refer markups TRIM D17/56855 | TF | 2017-04-28 | Y
246 | PLN-00120 | Capalaba WTP | Operational Monitoring Plan | Various minor | • No change to frequency or parameters • Updates to some terminology • Removal of total iron • Removal of references to CO2 due to delays in delivery | Refer markups TRIM D17/56853 | TF | 2017-04-28 | Y
247 | PLN-00037 | Capalaba WTP | HACCP Plan | Flow diagram Section 2.1.3 Section 3.2 | • HACCP Flow Diagram and Process schematic updated to show CO2 and caustic (into sludge equalisation tank) as dashed lines (future provision) instead of solid lines. HACCP flow diagram needs to be signed and JJ is away so can you please sign scan and email it back to me. • Various minor updates to wording throughout. • Section 2.1.3 Updates to UV system description and Updates to the values in the disinfection C.t calculation. • Section 3.2 HACCP limit validation updated to include more detail on HACCP limits and updates to limits as per wall chart. | Refer markups TRIM D17/56851 | TF | 2017-04-28 | Y
248 | PRO-01986 | Westbank WTP | HACCP Plan Wall Chart Procedure | Raw Water, Coagulation, Manganese Removal | • Raw turbidity action limit slightly decreased. • Raw water conductivity removed limit and extended into a Summer and Winter limit • Alum deviation alarm time extended from 2 mins to 5 mins for action and critical limit. • Manganese removal free chlorine action limit increased slightly. • Grab samples identified in chart. | Changes made to assist with enhanced coagulation. | KM | 2017-06-30 | Y
249 | PRO-01985 | Eastbank WTP | HACCP Plan Wall Chart Procedure | Kholo Early Warning Station Raw Water, Coagulation, Manganese Removal, Primary Disinfection, Secondary Disinfection, Treated Water. | • Kholo Early Warning Station - Raw turbidity action limit slightly decreased. • Kholo Early Warning Station - Raw water conductivity removed limit and extended into a Summer and Winter limit • Eastbank raw turbidity action limit slightly decreased. • Eastbank raw water conductivity removed limit and extended into a Summer and Winter limit. • Alum deviation alarm time extended from 2 mins to 5 mins for action and critical limit. • Manganese removal free chlorine action limit increased slightly. • New primary disinfection turbidity limit added (inlet to Camerons Hill 1 & 2). • Time frame added to secondary disinfection pH limit. • Treated water turbidity action limit added for Camerons Hill 1 & 2. | Changes made to assist with enhanced coagulation. | KM | 2017-06-30 | Y
250 | GDE-00054 | Boonah-Kalbar WTP | Verification Sample Point Guide | Process | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated |  | AS | 2017-12-04 | Y
251 | GDE-00055 | Maroon Dam WTP | Verification Sample Point Guide | Process | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated |  | AS | 2017-12-04 | Y
252 | GDE-00056 | Moogerah Dam WTP | Verification Sample Point Guide | Process | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated |  | AS | 2017-12-04 | Y
253 | GDE-00057 | Kooralbyn WTP | Verification Sample Point Guide | Process | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated |  | AS | 2017-12-04 | Y
254 | GDE-00058 | Rathdowney WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The picture for sample point RAT-SP120 was edited to make the sample tap more visable |  | AS | 2017-12-04 | Y
255 | GDE-00059 | Beaudesert WTP | Verification Sample Point Guide | Process | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated |  | AS | 2017-12-04 | Y
256 | GDE-00061 | Canungra WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The picture for sample point CAN-SP120 was edited to make the sample tap more visable • The picture for sample point CAN-SP910 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
257 | GDE-00062 | Capalaba WTp | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The picture for sample point CAP-SP920 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
258 | GDE-00063 | North Stradbroke island WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The GPS location for raw sample point NSI-SP121 was updated • The GPS location for raw sample point NSI-SP122 was updated • The picture for sample point NSI-SP122 was edited to make the sample tap more visable • The picture for sample point NSI-SP913 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
259 | GDE-00064 | Dunwich WTP | Verification Sample Point Guide | Process | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated |  | AS | 2017-12-05 | Y
260 | GDE-00065 | Amity Point WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The picture for sample point AMI-SP910 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
261 | GDE-00066 | Point Lookout WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The picture for sample point PLO-SP910 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
262 | GDE-00067 | Molendinar WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The picture for sample point MOL-SP933 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
263 | GDE-00068 | Mudgeeraba WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The GPS location for treated sample point MUD-SP923 was updated • The picture for sample point MUD-SP121 was edited to make the sample tap more visable • The picture for sample point MUD-SP122 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
264 | GDE-00069 | Hinze Dam WTP | Verification Sample Point Guide | Process, Sample Point Details | • Document was reviewed and updated • All ALS contract protocols were removed and sampling procedure references were updated • The GPS location for treated sample point HIN-SP920 was updated • The picture for sample point HIN-SP12 was edited to make the sample tap more visable • The picture for sample point HIN-SP980 was edited to make the sample tap more visable |  | AS | 2017-12-05 | Y
265 | PLN-00069 | Molendinar WTP | HACCP Plan | 1.2 Conditions of Operation 2.1.2 HACCP Process Flow Diagram and Schematic 2.1.3 System overview 3.2 HACCP Limit validation Section 6 Materials and Chemicals | 2.1.2 HACCP Process Flow Diagram and Schematic: Renaming of Clear Water Pond to Chlorine Contact Tank; Removal of plant bypass. Bypass was removed PID02077 TMO: Install Blank Plate on Bypass Penstock at Inlet Works complete Aug 2016; Fluoride dosing point changed to inlet of CCT. Monitoring changed to inlet of CCT. - PAC, pot perm and backwash recovery alum dosing lines changed from solid line to dashed line on HACCP diagram as they are dosed ‘as needed’. - Future: improve schematic detail on reservoir flow direction and arrangement - gravity main added 2.1.3 System overview – Alignment of numbering of all process steps in accordance with HACCP process steps. - Catchment raw water sources - Updates to wording on source water category. Various minor updates to all Process Steps. 2.1.3.8 Updates to the C.t calculation based on meeting C.t 8 mg.min/L under various pumping scenarios. 2.1.4 Updates to operational challenges to reflect WTP interlocks with treated water interlocks yet to be enabled. 3.2 HACCP Limit validation and PRO-01984 Molendinar WTP HACCP Plan Wall Chart Procedure: - Raw Water Abstraction: Change of target from ‘<5 NTU’ to ‘Turbidity at last coagulant dose change’. - Taste and Odour Control: Change in name of Process step from ‘PAC dosing’ to ‘Taste and Odour control’ as per R.A. Critical Limit values are now Action Limit Values. Presence of T&O in treated water does not make water unsafe rather it is aesthetically displeasing. T&O is managed - Manganese and Iron Removal: Timeframe of critical limit extended to > Action limit timeframe to allow Operator to be aware of an issue and intervene before the Critical Limit is reached as the oxidative state of the filter is not immediately at risk. - Changes to various process steps to update Process names CCP/QCP/oPRP terminology as per outcome of 2017 R.A. - Disinfection (primary): a pH target of >7.1 has been set which will allow the WTP to reliably meet the BWSA of pH 7.0 or greater. The WTP does not typically dose more sodium hydroxide than required hence there is little risk that pH will be dosed much above pH 7.1 therefore no upper target range has been set. The Action Limit has been aligned to reflect the BWSA of pH <7.0. - CCT target and minimum level have been adjusted from 55% to 62% based on recalculation to achieve minimum C.t 8 mg.min/L. CL Corrective action guidance added to instruct Ops to contact DWQ Coord if CCT level or treated water chlorine limits are triggered to prompt a check against actual C.t. - Addition of a treated water turbidity target of <0.2 NTU and an Action Limit of >0.5 NTU for 30 mins following Petrie Incident and to increase awareness and corrective action relating to impact of turbidity on primary disinfection. - Fluoridation: Pre fluoride HACCP limits added. - Removal of ‘Treated Water’ Process Step from Wall Chart. This is not a HACCP process step. ADWG exceedences are reported by the DWQ Coord using Form 27 which the assistance of Operations. - Section 6 Materials and Chemicals: Addition of hydrochloric Acid used in the process and reference to REG-00250 Commercial Services – Register Chemical Panel List which lists the contract status of each chemical and chemical supplier. | Refer markups D17/163000 | TF | 2017-12-05 | Y
266 | PRO-01984 | Molendinar WTP | HACCP Plan Wall Chart Procedure | Raw water abstraction Taste and Odour control Manganese and Iron Removal Disinfection (primary) Removal of Treated Water Process Step | Refer HACCP Plan 3.2 HACCP Limit validation notes above. | Refer markups D17/162997 | TF | 2017-12-05 | Y
267 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Terminology Fluoride monitoring Disinfection | - Changes in terminology of Process Steps to align with 2017 R.A review - Removal of Treated water and Sludge monitoring. Turbidity monitoring moved to Disinfection Primary Process Step. Sludge monitoring is part of Envir system, not DWQ. - Changes to Fluoride monitoring as per changes at WTP. | Refer markups D17/162999 | TF | 2017-12-05 | Y
268 | PRO-02105 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | All process steps except Fluoridation | Raw Water Abstraction - change of terminology, change from CCP to oPRP as per Validation guideline. Removal of CL for turbidity as per Validation guideline. Ammonia HACCP limits adjusted as per Ammonia treatment design capacity. Coagulation: Alum loss of dose changed from 'no flow' to <50% to detect flow deviations which may not be detected by low flow of 0 L/s. New coagulated water pH limits as per validation standard for organics removal but slightly lower to allow for dirty water events where high alum dose required for increased raw water turbidity/colour without the need for caustic dosing. Settled water colour as per validation standard for alum sites. Floc and Settling separated from Coag. Settled water turbidity as per validation standard for alum sites. Media Filtration - New dosed water pH limits following introduction of settled water caustic dosign to maintain biological properties in filter. UV disinfection - Dose rate as per validation standard and UV system validation. Removal of system unhealthy/unavailable as this relates to asset failure and loss of redundancy and not water quality. Disinfection (primary) broken up into NORMAL MODE and AMMONIA MODE follwoing delivery of breakpoint ammonia treatment. Disinfection (primary) NORMAL MODE - Change in terminology to 'dosed irradiated water' slight reduction in dosed irradiated water limits as improved chlorine decay expected with alum. New limits for dosed irradiated water as disinfection caustic dosing now in place. Treated water pH limits adjusted to reflect C.t 10 mg.min/L target down from C.t 15 mg.min/L target. New treated water turbidity limits introduced following Petrie incident to alert Operators to issue that requires investigation that could impact disinfection. Disinfection (primary) AMMONIA MODE - new limits to reflect operation of primary disinfection during ammonia mode. Refer HACCP plan validation. Further guidance added to Corrective Action guidance columns. |  | TF | 2018-02-26 | Y
269 | PLN-00092 | Beaudesert WTP | Operational Monitoring Plan | All process steps except Fluoridation | Introduction of new analysers following delivery of alum dosing and break point ammonia treatment |  | TF | 2018-02-26 | Y
270 | PLN-00091 | Beaudesert WTP | HACCP Plan | Glossary Intro Conditions of operation Flow diagrams System overview 2.1.3 Assessment of WQ data Validation Materials and Chemicals | Refer markups. Glossary, Intro, Assessment of WQ data updated as per other HACCP plans to reflect changes made to all HACCP Plans in streamlining process. Conditions of Operation, Flow Diagram, System overiew, Validation and Materials and Chemicals updated to reflect delivery of alum dosing and breakpoint ammonia treatment assets. | Refer markups D18/26201 Update: On awaiting final sign off of HACCP diagram on the day of commissioning the alum dosing it was found that the clarifier had poor settleablity. As such poly was introduced into the process on 1/03/18 as a settling aid. Refer incident. This was not reflected in the HACCP Plan. A risk assessment was undertaken to reflect this change D18/34774. The HACCP plan thus remained in draft until the success, or otherwise, of the changes led to a semi permanent solution which could include reverting back to magnasol 589. As such the HACCP Plan remains in final draft in REX. 26/04/18: LT-20 and LT-25 have now been incorporated into the HACCP Plan and Risk Register with an improvement item relating to delivery of permanent assets captured in the Risk Assessment. | TF | 2018-04-26 | Y
271 | PRO-02057 | Capalaba WTP | HACCP Plan Wall Chart Procedure | All process steps except Fluoridation | Refer summary of updates doc attached to email D18/68485. Numerous changes. | Refer markups D18/68433 | TF | 2018-04-27 | Y
272 | PLN-00037 | Capalaba WTP | HACCP Plan | 1.2 Cond of operation 2.1.3 system overview 3.2 HACCP Limit Validation 4.1 Operational procedures | • General updates to terminology throughout doc. • Section 1.2 Conditions of operation: Inclusion of alarm masking on start up in conditions of operation. Item captured in Risk Dashboard as alarm masking on start up requires an individual approach. • Flow diagrams: inclusion of CO2 as permanent. • Section 2.1.3 System Overview: Addition of use of hydrochloric acid in coagulation section for cleaning of lime hosed. Also added to Section 8 Materials and Chemicals. • Section 3.2 HACCP Limit Validation: Updated as per Wall Chart. • Section 4.1 Operational Procedures updated to include Ops Manual and FD. Addition of supporting docs. | Refer markups D18/68435 | TF | 2018-04-27 | Y
273 | PLN-00120 | Capalaba WTP | Operational Monitoring Plan | Coagulation CCP and terminology | Minor update to reflect UVT monitoring at Coagulation CCP but on the ground there are no changes to location and frequency of parameters. Just terminology updates | Refer markups D18/68432 | TF | 2018-04-27 | Y
274 | REG-00377 | Rathdowney WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 1/03/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
275 | REG-00353 | Beaudesert WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 7/06/17. This doc now obsolete. Risk Regiser document is now D17/73063 | Refer markups D18/26201 | TF/SR | 2018-05-08 | Y
276 | REG-00441 | Hinze Dam WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 22/06/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
277 | REG-00368 | Canungra WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 17/07/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
278 | REG-00375 | Kooralbyn WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 19/07/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
279 | REG-00342 | Boonah-Kalbar WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 23/08/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
280 | REG-00171 | Moogerah Dam WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 6/09/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
281 | REG-00166 | Maroon Dam WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 6/09/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
282 | REG-00344 | Capalaba WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 15/09/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
283 | REG-00426 | Mudgeeraba WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 27/10/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
284 | REG-00424 | Molendinar WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 3/11/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
285 | REG-00085 | North Stradbroke Island WTP | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 20/11/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
286 | REG-00449 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Risk Register | Unmitigated and Mitigated Risk Registers | Risk Assessment Review workshop 21/11/17. This doc now obsolete. Risk Regiser document is now D17/73063 |  | TF/SR | 2018-05-08 | Y
287 | PRO-02003 | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | All process steps except Fluoridation | - Raw water abstraction: raw water turbidity timeframe reduced f rom 1 hour to 30 mins as per SPE-00320.NEW Raw water colour target and action limits as per SPE-00320. NEW Raw water UV254 target and action limits- '- Supernatant Return: Supernatant return turbidity action limit value increased from 10 NTU to 15 NTU and timeframe reduced from 1 hour to 30 mins as per SPE-00320. NEW Sludge Thickener pH limits. Not previously determined. - Coagulation: Dosed water pH limits – adjusted downward to improve organics reduction. NEW Settled water organics target and action limit changed from true colour to UV254. Inclusion of lookup table and compass app for coag dose rate as per SPE-00320. Settled water colour target reduced from 5 HU to 2 HU as per SPE-00320 - Manganese and Iron Removal: Timeframes added for filtered water chlorine and filtered water pH following introduction of new analysers. NEW action limit for filtered water pH to detect overdose or under dose of settled water caustic for removal of Mn prior to critical limits being reached. New CL low limit for filtered water pH prevent shedding of Mn from filter. - Media Filtration: HACCP limits now based on individual filters following installation of new analysers - Disinfection (primary): NEW Upper operating target range added to free chlorine target to set an upper boundary for free chlorine target. NEW dosed filtered water pH limits added to detect potential impacts to Disinfection CCP on inlet to dosed filtered water reservoir. NEW treated water pH Action Limit to detect potential impacts to Disinfection CCP before Critical Limit is reached. Timeframe of CL reduced as per SPE-00320. NEW treated water turbidity Action Limit following Petrie incident to detect event in dosed filtered water reservoir that requires investigation. Reservoir level increased from 45% to 50% as per C.t calc. Timeframe of 5 mins added to reservoir level critical limit. Previously ‘any time’. NEW Max treated water flow rate for purposes of C.t and UV disinfection. - UV Disinfection: NEW UV Dose HACCP target and critical limit added as per SPE-00320. Removal of previous asset available/unavailable target and limit. These represent asset redundancy and water quantity risk rather than water quality. NEW UVT action limit of <80% introduced as a lead indicator of requirement to review processes to avoid impacts to UV Disinfection before Critical Limit is reached. UVT target also introduced. NEW UV reactor target and critical limits added as per SPE-00320. | Refer markups D18/76696 | TF | 2018-05-17 | Y
288 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | Flow diagrams, conditions of operation, terminology throughout, Operational challenges, Validation | • Flow diagram and flow schematic updated. Raw water to dosed filtered water tank inlet bypass removed. Caustic dose labelled ‘as required’ indicating intermittent use. Individual filter outlet turbidity monitoring added to each filter. Combined filtered water pH and chlorine online monitoring added. UV bypass removed. Descriptive detail added to sludge lagoons and removal of sludge. Addition of raw water screen • Conditions of operation flow rates updated based on recent audit. Refer RW 7671. • Disinfection C.t updated to reflect updates to treated water flow based on recent audit. Refer RW 7671. • Minor changes to process terminology. • 2.1.4 Operational challenges updated to reflect improvement filter monitoring and automation. Addition of challenges of treating fluctuating raw water organics and colour in Reynolds Creek and floc stir up on start up in clarifier. • 3.2 HACCP Limit Validation. Refer as per changes to PRO-02003 Kalbar WTP – HACCP Plan Wall Chart Procedure | Refer markups D18/76695 | TF | 2018-05-17 | Y
289 | PLN-00119 | Boonah-Kalbar WTP | Operational Monitoring Plan | Media Filtration, Manganese removal, terminologgy throughout | • Inclusion of new online combined filtered water chlorine and pH analysers • Alignment with PRO-02003 updates • Minor updates to terminology | Refer markups D18/76698 | TF | 2018-05-17 | Y
290 | PLN-00107 | Moogerah Dam WTP | HACCP Plan | flow diagrams 2.1.3 2.1.4 3.2 4.2 6 Appendix | • HACCP process step terminology updated to reflect risk assessment process steps. • HACCP flow diagram – ‘process step’ symbols added to flow diagram for Raw Water Abstraction and Distribution Pipeline process steps. • HACCP schematic diagram updated to show BW waste tank 1 and 2 running in series with outlet at BW tank 2. • Section 2.1.3 Disinfection C.t calculation updated based on update to treated water tank volume figure. • Section 2.1.4 distribution system dirty water events updated based on current knowledge of aged galvanized pipes. • Section 3.2 Validation update to reflect updated HACCP limits. Timeframe validation added where previously omitted. • Section 1.2 pre-requisite programs updated to reflect overarching PRP procedure and listed oPRPs. • Section 6 updated to reflect chemical supplier details captured in overarching REG-00250. • Appendix A updated with marked up drawing of distribution system. | Refer REX D18/117271 for markups | TF | 2018-08-07 | Y
291 | PRO-01929 | Moogerah Dam WTP | HACCP Plan Wall Chart Procedure | Raw water abstraction Coagulation Disinfection (primary) Distibution pipeline Treated water | • Raw water abstraction turbidity action limit changed from absolute values to change in turbidity as per approach to responding to change in raw water quality (decline or improvement) • Removal of raw water turbidity Critical limit. Decision to run WTP or shutdown and tanker to be made by Operations. Subsequent CCP CLs sufficient to ensure safety of drinking water. • Coagulation CCP upper pH limit timeframe reduced from 15 mins to 5 mins as this limit is proxy monitoring of loss of coag dose and timeframe is consistent with SPE-00320. • Disinfection (primary) CCP low chlorine values increased based on reduction in min reservoir level due to regular instances where CCT drops to <60% but not <50% and updated treated water reservoir volume figure. Treated water action limit timeframe reduced from 2 hours to 30 mins in line with SPE-00320. Low pH critical limits added to capture unforeseen events. • Distribution Pipeline chlorine target reduced from >0.5 mg/L to >0.2 mg/L in line with ADWG. Turbidity and pH targets and action limits added to detect water age issues or dirty water events that should initiate corrective actions. • Corrective Actions separated into responses based on specific HACCP limit exceedance. | Refer REX D18/117273 for markups | TF | 2018-08-07 | Y
292 | PLN-00108 | Moogerah Dam WTP | Operational Monitoring Plan | Terminology Distribution pipeline | • HACCP process step terminology updated to reflect risk assessment process steps. • Treated water colour monitoring changed from apparent to true • Weekly pH monitoring added to distribution pipeline process step | Refer REX D18/117272 for markups | TF | 2018-08-07 | Y
293 | PLN-00100 | Maroon Dam WTP | HACCP Plan | flow diagrams 2.1.3 2.1.4 3.2 4.2 6 Appendix | • HACCP process step terminology updated throughout to reflect risk assessment process steps. • HACCP flow diagram – ‘process step’ symbols (red circles) added to flow diagram for Raw Water Abstraction and Distribution Pipeline process steps. Terminology updated to reflect R.A. Coag and Clarifier bypass removed as pipework removed creating air gap and this bypass is not considered operationally available due to unacceptable water quality risk. • HACCP schematic diagram updated to show BW waste tank 1 and 2 running in series with outlet at BW tank 2. Change of location of treated water verification sample tap and update of sample tap IDs • Section 2.1.3 Disinfection C.t calculation updated based on update to treated water tank volume figures. As above bypass removed. • Paragraph added to floc and settling describing removal of bypass and describing it is not considered operationally available due to unacceptable water quality risk. • Section 2.1.4 distribution system dirty water events updated based on current knowledge of water age issues and aged galvanized pipes. Manual clarifier desludging added, turbidity monitoring after balance tank added with ref to late detection of clarifier issue.. Cross connection and lack of raw water turbidity analyser items removed. Distribution system issues updated. • Section 3.2 Validation update to reflect updated HACCP limits. Timeframe validation added where previously omitted. • Section 1.2 pre-requisite programs updated to reflect overarching PRP procedure and listed oPRPs. • Section 6 updated to reflect chemical supplier details captured in overarching REG-00250. • Appendix added to include drawing of distribution system diagram as per Maroon HACCP plan. | Refer REX D18/117321 for markups | TF | 2018-08-07 | Y
294 | PLN-00101 | Maroon Dam WTP | Operational Monitoring Plan | terminology treated water | • HACCP process step terminology updated to reflect risk assessment process steps. • Treated water colour monitoring changed from apparent to true and moved from ‘treated water’ to disinfection (primary). | Refer REX D18/117323 for markups | TF | 2018-08-07 | Y
295 | PRO-02054 | Maroon Dam WTP | HACCP Plan Wall Chart Procedure | Raw water abstraction Coagulation Disinfection (primary) Distribution Pipeline | • Raw water abstraction turbidity action limit changed from absolute values to change in turbidity as per approach to responding to change in raw water quality (decline or improvement) • Removal of raw water turbidity Critical limit. Decision to run WTP or shutdown and tanker to be made by Operations. Subsequent CCP CLs sufficient to ensure safety of drinking water. • Coagulation CCP upper pH limit timeframe reduced from 15 mins to 5 mins as this limit is proxy monitoring of loss of coag dose and timeframe is consistent with SPE-00320. • Disinfection (primary) CCP treated water low chlorine value decreased based on obtaining reservoir volumes from as con drawings. Dosed filtered water pH target range, critical limits and treated water lower pH critical limit added to capture unforeseen events. Treated water tanks min level target decreased from 50% to >30% in line with C.t calc. • Distribution Pipeline chlorine target reduced from >0.5 mg/L to >0.2 mg/L in line with ADWG. Turbidity and pH targets and action limits added to detect water age issues or dirty water events that should initiate corrective actions. • Corrective Actions separated into responses based on specific parameters rather than grouped together. | Refer REX D18/117324 for markups | TF | 2018-08-07 | Y
296 | PLN-00073 | Hinze Dam WTP | HACCP Plan | flow diagrams 2.1.3 3.2 4.2 6 Appendix | • HACCP process step terminology updated throughout to reflect risk assessment process steps. • Section 2.1.2 • HACCP schematic diagram updated to show raw water pumps in BoHT. RPZ added to rainwater into mains connection point. Sludge holding tank added. • HACCP Flow diagram and schematic diagram updated to show sludge holding tank and turbidity monitoring (not part of HACCP monitoring). Terminology updated to reflect risk assessment process steps. • Section 2.1.3 system overview Distribution Pipeline section updated to include description of rainwater system and Cedar lakes raw water pipeline. • Section 3.2 HACCP limit validation minor updates as per wall chart changes. • Section 4.2 pre-requisite programs updated to reflect overarching PRP procedure and listed oPRPs. • Section 6 updated to reflect chemical supplier details captured in overarching REG-00250. • Appendix added to include drawing of distribution system diagram as per Maroon HACCP plan. | Refer REX D18/117407 markups | TF | 2018-08-07 | Y
297 | PLN-00074 | Hinze Dam WTP | Operational Monitoring Plan | Terminology Distribution pipeline | • HACCP process step terminology updated to reflect risk assessment process steps. • Weekly turbidity added to hinze visitor centre park tap. | Refer REX D18/117409 markups | TF | 2018-08-07 | Y
298 | PRO-02103 | Hinze Dam WTP | HACCP Plan Wall Chart Procedure | terminology Raw water abstraction Disinfection (primary) Distribution pipeline | • HACCP process step terminology updated throughout to reflect risk assessment process steps. • Raw water abstraction - removal of raw water turbidity Critical limit. Decision to run WTP or shutdown and tanker to be made by Operations. Subsequent CCP CLs sufficient to ensure safety of drinking water. • Removal of T&O target and actions. Management of T&O control is driven by Molendinar HACCP Plan. Note in Critical Limit Corrective Actions guidance that tankering is an option. • ‘Treated water’ process step removed. • Disinfection (primary) low pH CL considered but removed based on likelihood of low pH in WTP process not occurring. • Distribution Pipeline Hinze visitor Centre tap turbidity added. Should be <1 NTU. Operator to assist in performing basic checks of system integrity if turbidity high. | Refer REX D18/117410 markups | TF | 2018-08-07 | Y
299 | PLN-00075 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan | flow diagrams 2.1.3 2.1.4 3.2 4.2 6 | • HACCP process step terminology and updated throughout to reflect risk assessment process steps and GDE-00235 WTP Equipment Field Labeling Guideline. Process step symbol (red circle) added to flow diagrams where previously omitted for Process Steps. • Section 2.1.2 HACCP Flow diagram process step terminology updated to reflect risk assessment process steps. Addition of Raw Water Abstraction grab sample monitoring requirement. • All: Redland reservoir assets that control treated water pump start/stop remain. All other Redland network assets removed. • Dunwich flow diagram and schematic – online filtered water turbidity added. • Section 2.1.3 1. Point Lookout WTP: bore 1 casing damage and operating philosophy added. • Section 2.1.3 3 Dunwich WTP: description of online turbidity added. • Fluoridation and Disinfection (primary) order of appearance switched. • Section 2.1.4 operational challenges updated to remove reference to raw water iron for Amity Point as this is captured in unmitigated R.A process. Point Lookout in summer 17-22 hours supply challenges during peak demand period added. • Section 3.2 HACCP limit validation minor updates as per wall chart changes. • Section 4.2 pre-requisite programs updated to reflect overarching PRP procedure and listed oPRPs. • Section 6 updated to reflect chemical supplier details captured in overarching REG-00250. | Refer REX D18/117478 markups | TF | 2018-08-08 | Y
300 | PLN-00144 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | Operational Monitoring Plan | terminology Raw water abstraction Media filtration | • HACCP process step terminology updated to reflect risk assessment process steps. • All Raw and treated water – colour – removed. Risk doesn't warrant operational monitoring and treatment for colour does not exist at WTP. • Dunwich WTP NEW – Media Filtration – online filtered water turbidity added and grab sample (crosscheck) daily from weekly. | Refer REX D18/117478 markups | TF | 2018-08-08 | Y
301 | PRO-02099 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan Wall Chart Procedure | Corrective actions Raw Water Abstraction Media Filtration Disinfection (primary) | • All HACCP process step terminology and process water updated throughout to reflect risk assessment process steps and standard naming conventions (GDE-00235 WTP – Equipment Field Labelling). • All removal of ‘treated water’ process step line item from • All shutdown/interlocks requirements separated for Stablised water (pre) and treated water (post) in Critical Limits corrective actions column. To be reviewed/actioned by SCADA change request form. • All NEW - Raw water abstraction – raw water turbidity target and action limit from daily grab sample to detect change or disturbance in bore water quality. • Dunwich WTP: NEW – Media Filtration – filtered water target and action limit to integrate online filtered water turbidity meter • Amity Point WTP: reduction of treated water free chlorine action limit timeframe from 2 hours to 30 mins in line with SPE-00320 and other WTP Disinfection (primary) CCP timeframes. • All treated water turbidity action limit timeframe reduced from 4 hours to 30 mins and critical limit increased from 0.8 NTU to 1.0 NTU and timeframe reduced from 1 hour to 15 mins. | Refer REX D18/117484 markups | TF | 2018-08-08 | Y
302 | PLN-00094 | Rathdowney WTP | HACCP Plan | terminology flow diagrams 2.1.3 2.1.4 3.2 4.2 6 | • HACCP process step terminology and updated throughout to reflect risk assessment process steps and GDE-00235 WTP Equipment Field Labeling Guideline. Process step symbol (red circle) added to flow diagrams where previously omitted for Process Steps. • Section 2.1.2 HACCP Flow diagram process step terminology updated to reflect risk assessment process steps. Removal of Manganese removal process step. • Section 2.1.3: Coagulation section updated to describe 589 dosing as neat and max 589 dose rate as 80 mg/L. Manganese and Iron removal section removed and description of historical process captured under media filtration. Distribution system updated to reflect QUU new reservoir. • Section 2.1.4 operational challenges updated describe stormwater flows into solids handling system. • Section 3.2 HACCP limit validation minor updates as per wall chart changes. • Section 4.2 pre-requisite programs updated to reflect overarching PRP procedure and listed oPRPs. • Section 6 updated to reflect chemical supplier details captured in overarching REG-00250. | Refer D18/117800 markups | TF | 2018-08-07 | Y
303 | PRO-01768 | Rathdowney WTP | HACCP Plan Wall Chart Procedure | terminology manganese and iron control supernatant return coagulation Disinfection (primary) | • All HACCP process step terminology and process water updated throughout to reflect risk assessment process steps and standard naming conventions (GDE-00235 WTP – Equipment Field Labelling). • Manganes and Iron removal removed. As per R.A 2017: pre filter chlorine assets still in place. If pre-filter chlorine were to be re-initiated refer to previous HACCP Risk Assessment and review and update for this process. Not assessed in 2017. • Removal of ‘treated water’ process step line item. • Raw Water Abstraction HACCP limits changed from absolute values to change over specified timeframe which is representative of this WTP and in line with SPE-00320. • Supernatant return Action limit value increased and timeframe decreased in line with SPE-00320. • Coagulation: action limit colour decreased from 15 HU to 10 HU which should be readily achievable at this site. • Disinfection: dosed filtered water upper free chlorine action limit increased from 3.5 mg/L to 3.8 mg/L based on feedback from Ops regarding chlorine decay in summer months • Disinfection: treated water turbidity action limit added following Petrie incident. • All shutdown/interlocks requirements separated for individual parameters. | Refer D18/117801 markups | TF | 2018-08-07 | Y
304 | PLN-00093 | Rathdowney WTP | Operational Monitoring Plan | terminology | • HACCP process step terminology updated to reflect risk assessment process steps and HACCP reportable parameters. | Refer D18/117798 markups | TF | 2018-08-07 | Y
305 | PLN-00095 | Kooralbyn WTP | HACCP Plan | flow diagrams 2.1.3 2.1.4 3.2 4.2 6 | • HACCP process step terminology and updated throughout to reflect risk assessment process steps and GDE-00235 WTP Equipment Field Labeling Guideline. Process step symbol (red circle) added to flow diagrams where previously omitted for Process Steps. • Section 2.1.2 HACCP Flow diagram process step terminology updated to reflect risk assessment process steps. Addition of Raw Water Abstraction grab sample monitoring requirement. Caustic dosing changed to ‘as required’ (dashed line) to reflect requirements. Bigfoot Lagoon clearly identified as optional source. • Section 2.1.3 description of Bigfoot lagoon as alternate source added. • Section 2.1.3 C.t changed from 15 to 10 and updated as per C.t calculator. Min level reduced to 20%. • Section 2.1.4 operational challenges updated to include insufficient alum storage, high pH during dry periods, regular Operator intervention to optimize coagulation during raw water changes in Logan River. • Section 3.2 HACCP limit validation updates as per wall chart changes. • Section 4.2 pre-requisite programs updated to reflect overarching PRP procedure and listed oPRPs. • Section 6 updated to reflect chemical supplier details captured in overarching REG-00250. | Refer D18/117965 markups | TF | 2018-08-07 | Y
306 | PLN-00096 | Kooralbyn WTP | Operational Monitoring Plan | terminology | • HACCP process step terminology updated to reflect risk assessment process steps and alignment of ‘HACCP reportable parameters’ with Wall Chart. • ‘Treated Water’ process step monitoring for treated water turbidity and colour moved into Disinfection (primary) process step. | Refer D18/117966 markups | TF | 2018-08-07 | Y
307 | PRO-02110 | Kooralbyn WTP | HACCP Plan Wall Chart Procedure | Raw water abstraction Coagulation Disinfection (primary) | • All HACCP process step terminology and process water updated throughout to reflect risk assessment process steps and standard naming conventions (GDE-00235 WTP – Equipment Field Labelling). • Raw Water Abstraction: removal of turbidity critical limit. • Raw Water Abstraction: addition of raw water colour target and action limit similar to Kalbar WTP. • Raw Water Abstraction: note added regarding impact of PAC dosing when using Bigfoot Lagoon on raw water turbidity. • Coagulation: settled water UV 254 Action limit added as more sensitive measure of organics removal performance through the coagulation process similar to Kalbar WTP. • Disinfection (primary): Dosed Filtered Water Action limit pH reduced from pH 8.0 to 7.6 as WTP targets C.t 10 mg.min/L which requires pH to be ≤8.0. Therefore critical pH limit reduced from 8.5 to 8.0. • Disinfection (primary): Treated water pH Action limits and critical limits as per Dosed filtered water to prevent out of spec water leaving CCT. • Disinfection (primary): Reservoir level target and critical limit reduced from 45% to 20%. No impact to min chlorine for C.t 10 mg.min/L. Previous error/oversight • Disinfection (primary): treated water turbidity action limit added following Petrie incident. • Removal of ‘treated water’ process step line item. | Refer D18/117967 markups | TF | 2018-08-07 | Y
308 | REF-00306 (PL-GDC-20-1680) | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2018-01-09 | Y
309 | REF-00308 (obsolete) REF - new (CRA-GCD-13-9635) | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated) | reveiwed and updated | REF-00308 and REF-00310 merged together become (CRA-GCD-13-9635) single doc. REF-NEW | Refer Veolia doc management system | Veolia | 2018-01-10 | Y
310 | REF-00310 (obsolete) REF - new (CRA-GCD-13-9635) | Gold Coast Desalination Plant | HACCP Risk Register (mitigated) | reveiwed and updated | REF-00308 and REF-00310 merged together become (CRA-GCD-13-9635) single doc. REF-NEW | Refer Veolia doc management system | Veolia | 2018-01-10 | Y
311 | REF-00309 (PL-GCD-20-1682 | Gold Coast Desalination Plant | HACCP Validation Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2017-11-16 | Y
312 | REF (REF-DCG-4-1664) | Gold Coast Desalination Plant | Operational Monitoring Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2018-07-05 | Y
Submission to Regulator - Amendment Application August 2018
313 | PLN-00357 | Canungra WTP | HACCP Plan | All | New Canungra MF WTP | New procedure | TF | 2018-09-07 | Y
314 | PLN-00358 | Canungra WTP | Operational Monitoring Plan | All | New Canungra MF WTP | New procedure | TF | 2018-09-07 | Y
315 | PRO-02267 | Canungra WTP | HACCP Plan Wall Chart Procedure | All | New Canungra MF WTP | New procedure | TF | 2018-09-07 | Y
316 | GDE-00255 | Canungra WTP | Verification Sample Point Guide | All | New Canungra MF WTP | New procedure | TF | 2018-09-12 | Y
317 | PLN-00357 | Canungra WTP | HACCP Plan | Validation | • Section 1.1 scope: updated to include date of commissioning of new Canungra WTP. • Schematic diagram – removal of KIP reference as this only relates to Supply System sites. • Sample point codes update from CAN to CNG, Membrane Pressure Decay changed to Protozoa LRV • Risk Register / Risk Dashboard terminology made consistent throughout doc • Section 2.1.3 Distribution System: removal of inaccurate daily system demand figure • Section 3.2 HACCP limit validation: Disinfection CCP: Update of validation to reflect removal of dosed filtered water and treated water pH action limits of >8.0 for >30 mins based on the control system automatically shifting the minimum C.t alarm/interlock between 10 mg.min/L and 15 mg.min/L based on online pH. The raw water can be approx. pH 8.0 and there is no pH correction (reduction) through the process hence there can only be an increase through the process. The upper pH Operating Protocol Notification trigger is pH 8.0 therefore a Notification to QUU would occur if/when the weekly treated water verification sample is pH >8.0. | Refer mark ups D18/138336 | TF | 2018-09-18 | Y
318 | PRO-02267 | Canungra WTP | HACCP Plan Wall Chart Procedure | All | • Disinfection CCP Dosed Filtered Water and Treated Water upper pH Action Limits >8.0 for >30 mins removed. • Corrective actions for high pH moved from ‘Action Limit Corrective Action Guidance’ to ‘Critical Limit Corrective Action Guidance’. | Refer mark ups D18/138337 | TF | 2018-09-18 | Y
319 | PLN-00040 | North Stradbroke Island WTP | HACCP Plan | Flow diagrams Section 2.1.3 overview for Supernatant return | Updates to flow diagrams and Section 2.1.3.3 to include return of TISAB to filter backwash tank and supernatant return process. | Refer markups D18/142223 | TF | 2018-09-25 | Y
320 | PLN-00357 | Canungra WTP | HACCP Plan | Validation | Increase in Membrane Filtration CCP limit from 230 µS/cm to 300 µS/cm based on current (normal) raw water conductivity levels. | Refer markups D18/148247 | TF | 2018-09-26 | Y
321 | PRO-02267 | Canungra WTP | HACCP Plan Wall Chart Procedure | Membrane Filtration CCP | Increase in Membrane Filtration CCP limit from 230 µS/cm to 300 µS/cm based on current (normal) raw water conductivity levels. | Refer markups D18/148245 | TF | 2018-09-26 | Y
322 | PLN-00069 | Molendinar WTP | HACCP Plan | Section 2.1 2.1.3 System overview 3.2 validation 4.2 PRPs 6 Materials & Chemicals | • 2.1.1 CWQ Coord added to HACCP team. Previous omission. • 2.1.2 Verification sample point ID’s added to HACCP Schematic diagram • 2.1.2 Dashed lines added to HACCP Process Flow Diagram and HACCP Schematic Diagram showing clear delineation between Molendinar WTP HACCP Plan and Supply System HACCP Plan and CRE. • Aerial photograph updated to more recent photo • Site layout of reservoirs removed as this is supply system asset. • 2.1.3 Catchment & storage description updated by CWQ Coord to reflect Sanitary survey • Process step nomenclature updated as per Risk Assessment • C.t calc details updated • Section 3.2 Validation: updates to validation section to align with updates to changes to HACCP limits and more detail added in line with SPE-00320. • 4.2 pre-requisite programs updates to align with REG-00775. • 6 Material & chemicals updated to align with REG-00250 process. | Refer markups D18/158124 | TF | 2018-10-29 | Y
323 | PRO-01984 | Molendinar WTP | HACCP Plan Wall Chart Procedure | Supernatant Return Coagulation Floc & Settling Disinfection (primary) | • Supernatant return turbidity AL increased from 10NTU to 15NTU in line with SPE-00320 • Coagulated water pH target values, action limit values and critical limit values aligned with SPE-00320 for site where organics removal is not the primary driver. • Settled water colour target value aligned with SPE-00320. Was ≤2 HU now <2 HU. • Settled water turbidity limit aligned with SPE-00320 from >3 NTU for 2 hours to > 5 NTU for 60 mins to accommodate clarifier boil up events which occur regularly (nightly) but does not impact filter. • Disinfection (primary) C.t and free chlorine target, lower action limit value and lower critical limit value increased based on worst case scenario running 5 treated water pumps. Previously action to contact DWQ Coord to recalc C.t if >3 TW pumps running however no engineering controls in place to stop >3 TW pumps running so HACCP limit adjusted to accommodate this scenario. • Various wording updates to Corrective action guidance. Refer markups. | Refer markups D18/158122 | TF | 2018-10-29 | Y
324 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Manganese & Iron removal | • Removal of daily manganese testing on supernatant return and settled water. Not required as per validation standard. PRO HACCP Plan Wall Chart Procedure includes corrective action to Check raw, settled and supernatant return soluble manganese if high treated water Mn detected > action limit. | Refer markups D18/158123 | TF | 2018-10-29 | Y
325 | PLN-00095 | Kooralbyn WTP | HACCP Plan | 2.1.2 2.1.3 2.1.4 3.2 | • 2.1.2 aerial photograph text updated indicating temporary tanks in use and the treated water reservoir offline. • 2.1.3.2 – coagulation – alum storage volume increased from 1700L to 10000L. Legacy info relating to magnasol 589 removed. • 2.1.3.5 disinfection – treated water tank description added. C.t calculation updated. • 2.1.4: Operations challenge: Alum storage upgraded mid-2018. Operational challenge relating to undersized alum storage removed. • 3.2 Validation: values updated to reflect changes to C.t when operating with four temporary tanks. | Refer D18/186076 markups | TF | 2018-11-07 | Y
326 | PRO-02110 | Kooralbyn WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) | • Disinfection (primary) HACCP limits adjusted • Treated water free chlorine Action Limit increased from 1.0 mg/L to 1.5 mg/L • Treated water free chlorine Critical Limit increased from 0.8 mg/L to 1.2 mg/L • Treated water reservoir minimum level increased from 20% to 32 % | Refer D18/186072 markups | TF | 2018-11-07 | Y
327 | PLN-00357 | Canungra WTP | HACCP Plan | Validation | Validation to support changes to individual filter turbidity HACCP limits. | Refer markups D18/166986 | TF | 2018-11-20 | Y
328 | PRO-02267 | Canungra WTP | HACCP Plan Wall Chart Procedure | Membrane Filtration CCP | Increase HACCP Operational Target from <0.05 NTU to <0.10 NTU Removal of HACCP Action limit value >0.05 NTU for >15 mins Adjustment of HACCP Critical limit value from >0.5 NTU for 1 min / >0.1 NTU for 5mins TO >0.15 NTU for 5 mins Following continuos spikes in online turbidity reading following start up from shutdown on backwash which has been found to be related to air or possibly manganese build up in sample lines and not membrane integrity based on direct integrity testing. Limits adjusted to account for process issues that are not representative of membrane integrity issues AND turbidity verificaiton not possible to <0.1 NTU. Refer notes to validation section 3.2. | Refer markups D18/166984 | TF | 2018-11-20 | Y
329 | PLN-00357 | Canungra WTP | HACCP Plan | Flow diagram Section 2.1.3 Section 3.2 | Updates relating to introduction of potassium permanganate: • 2.1.2 Flow Diagram & schematic diagram updated: potassium permanganate added under Mn and Fe Control QCP. Treated water caustic dosing line changed to ‘dashed’ as is only dosed as required on HACCP Flow diagram. • 2.1.3 Manganese and Iron Control QCP updated to include potassium permanganate system description. • 3.2 Validation Manganese and Iron control updated to include potassium permanganate dosing as specific dosing to reduce Mn control. Previously stated specific Mn control not available. | Refer markups D18/168614 | TF | 2018-11-26 | Y
330 | PRO-02267 | Canungra WTP | HACCP Plan Wall Chart Procedure | Mn and Fe Control | Updates relating to introduction of potassium permanganate: • No changes to HACCP limits. • Manganese and Iron control QCP updated to include corrective action for high manganese to check and adjust potassium permanganate dose rate. Corrective action if treated water Mn high updated to include verifying that a potassium permanganate overdose has/hasn’t occurred. | Refer markups D18/168612 | TF | 2018-11-26 | Y
331 | PLN-00358 | Canungra WTP | Operational Monitoring Plan | Mn and Fe Control | Updates relating to introduction of potassium permanganate: • Manganese and Iron control QCP: Daily visual inspection and recording of potassium permanganate batching tank level (usage). | Refer markups D18/168613 | TF | 2018-11-26 | Y
332 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Disinfection (primary) | Removal of WTP Operator 3 x weekly sampling from Reservoirs 3, 4, 5, 6 outlets. This sampling will be performed under the Supply System verification monitoring program as of Monday 3rd Dec in line with these Reservoirs being part of the Supply System HACCP system and not the Molendinar WTP HACCP system. | Refer markups D18/170645 | TF | 2018-11-29 | Y
333 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | Mn and Fe Control | Removal of daily manganese testing on supernatant return and settled water. Not required as per validation standard. PRO HACCP Plan Wall Chart Procedure includes corrective action to Check raw, settled and supernatant return soluble manganese if high treated water Mn detected > action limit. | Refer markups D18/173376 | TF | 2018-12-05 | Y
334 | PRO-01768 | Rathdowney WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) | • Disinfection primary target and action limits expanded to include winter (May-Oct) and summer (Nov-Apr) free chlorine dosed filtered water targets and action limits based on chlorine decay experienced in warmer months and chlorine required to reliably achieve treated water free chlorine target. • Note added that it is the responsibility of the Operations Supervisor to make changes to the free chlorine HACCP Action Limits in SCADA in summer/winter as per the HACCP Plan. | Refer D18/181982 markups | TF | 2018-12-17 | Y
335 | PLN-00094 | Rathdowney WTP | HACCP Plan | 2.1.1 2.1.2 2.1.3 3.2 | • 2.1.1 HACCP team: Addition of CWQ Coord to HACCP team table • 2.1.2 aerial photo updated • 2.1.3.6 Disinfection primary description updated to include impact of warmer and cooler months on chlorine residual. Updated C.t calc. • 3.2 Validation section updated as per updates to Wall Chart HACCP limits for Disinfection (primary) free chlorine. | Refer D18/181983 markups | TF | 2018-12-17 | Y
336 | PLN-00095 | Kooralbyn WTP | HACCP Plan | 2.1.1 2.1.3 2.1.4 3.2 | • 2.1.1 CWQ Coord added to HACCP team. Previous omission. • 2.1.3 aerial photograph notes updated indication 1.5 ML res in use • 2.1.3.5 Disinfection primary section updated to reflect 1.5 ML res. C.t calc updated based on changes back to 1.5 ML reservoir. • Distribution system section updated to reflect 1.5 ML res. • 2.1.4 updated to remove reference to use of Bigfoot and need for baffle. • Section 3.2 Validation: updates to validation section to align with updates to changes to HACCP limits back to 1.5 ML reservoir • 4.1 operational procedures. Removal of remaining references to magnasol procedures. | Refer D18/181979 markups | TF | 2018-12-17 | Y
337 | PRO-02110 | Kooralbyn WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) | • Treated water free chlorine Action Limit decreased from 1.5 mg/L back to 1.0 mg/L • Treated water free chlorine Critical Limit decreased from 1.2 mg/L to 0.8 mg/L • Treated water reservoir minimum level decreased from 32% to 20% | Refer D18/181979 markups | TF | 2018-12-17 | Y
338 | PRO-02105 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Raw Water Abstraction Coagulation PAC (new) Media Filtration Disinfection (primary) | Raw water abstraction – raw water turbidity action limit reduced from ±20 NTU to ±10 NTU as interim limits 25/06/18 have become permanent. Raw water turbidity colour action limit >30 HU changed to >± 20 HU to capture dynamic approach to responding to raw water change to trigger review of coag dose rate change. Target changed to colour at last coag dose rate change Coagulation – coagulated water upper pH action limit increased from pH 7.0 to pH 7.3 and timeframe reduced from 30 mins to 15 mins. Refer section 3.2 validation. PAC – new process step Media Filtration – new target and action limit for settled water chlorine dosing. Disinfection(primary) (normal mode) – free chlorine critical limit timeframe reduced to 2 mins for consistency with timeframe when running through buffer tank. Typo of res tank level > symbol corrected. Disinfection (primary) (ammonia mode) – breakpoint chlorine target and action limit reduced based on only needing to achieve primary disinfection and not extra chlorine for network as it all gets consumed in GAC. Discrepancy action limit and critical limit values and timeframes increased based on operational experience. Disinfection (primary) (ammonia mode) - Nomenclature updated. | Refer markups D18/184929 | TF | 2018-12-18 | Y
339 | PLN-00092 | Beaudesert WTP | Operational Monitoring Plan | PAC dosing Floc and Settling Media Filtration | PAC dosing – daily dose rate check added (when in use) Flocculation and Settling – daily dose rate check added Media filtration – daily filtered water free chlorine grab sample added | Refer markups D18/184930 | TF | 2018-12-18 | Y
340 | PLN-00091 | Beaudesert WTP | HACCP Plan | 1.2 2.1.1 2.1.2 2.1.3 2.1.4 3.2 4.2 6 | 1.2 Notes added to Conditions of Application table based on Seqwater Asset Capability Statement – Treatment and Transport – 2015 (D14/38264) 2.1.1 CWQ Coord added to HACCP team 2.1.2 HACCP flow diagram and schematic updated to include PAC, settled water chlorine. Both as required. Changed settled water caustic to ‘as required’. Aerial photographs updated. 2.1.3.3 PAC new section 2.1.3.5 Media Filtration description of change of filter from biological to non-biological and description of settled water chlorine dosing added. 2.1.3.7 Disinfection (primary) reformatted with headings ‘normal mode’ and ‘ammonia mode’. C.t calc updated. 2.1.4 challenges regarding temporary nature of poly and settled water chlorine dosing systems, high raw water pH and clarifier performance added. 3.2 Validation updated to reflect updates to Wall Chart. Detail added where limits previously not specifically detailed. 6 Material and chemical updated to reflect new REG-00250 commercial services process. 4.2 Pre-requisite programs updated to reflect new REG-00775 corporate HACCP RPRs process. | Refer markups D18/184931 | TF | 2018-12-18 | Y
341 | PLN-00102 | Canungra WTP | HACCP Plan | obsolete | Old WTP demolished 14/12/18 | Refer email Paul F 14/12/18 | TF | 2018-12-20 | Y
342 | PLN-00007 | Canungra WTP | Operational Monitoring Plan | obsolete | Old WTP demolished 14/12/18 | Refer email Paul F 14/12/18 | TF | 2018-12-20 | Y
343 | PRO-02109 | Canungra WTP | HACCP Plan Wall Chart Procedure | obsolete | Old WTP demolished 14/12/18 | Refer email Paul F 14/12/18 | TF | 2018-12-20 | Y
344 | PLN-00357 | Canungra WTP | HACCP Plan | 2.1.3 3.2 | • 2.1.3.2 Mn and Fe Control: description added to include scales for monitoring chemical usage. • 3.2 HACCP Limit Validation: updated to reflect changes to Wall Chart | Refer markups D19/1112 | TF | 2019-01-04 | Y
345 | PRO-02267 | Canungra WTP | HACCP Plan Wall Chart Procedure | Membrane Filtration CCP Disinfection (primary) CCP Fluoridiation CCP | • Membrane Filtration CCP Filtered water conductivity target and critical limits changed from absolute <200 and >330 µS/cm values to calculated values of <20% (target) and >+20% (critical limit). • Disinfection (Primary) CCP Dosed filtered water free chlorine upper critical limit timeframe extended from >5 mins to >15 mins to allow for short term increases on start up with insignificant consequence to the treated water chlorine. • Fluoridation CCP Dosed filtered water fluoride timeframe reduces from >15 mins to >5 mins to allow for earlier detection of an overdose and interlocking of the fluoride plant. | Refer markups D19/1113 | TF | 2019-01-04 | Y
346 | PLN-00073 | Hinze Dam WTP | HACCP Plan | 1.1 2.1.2 2.1.3 | DWQMP Amendment Application 2018 - Additional Information Request: • Section 1.1 Scope updated to include brief description of Cedar Lakes raw water supply assets and management of Cedar Lakes supply is not covered under the Hinze Dam WTP HACCP Plan. • Section 2.1.2 Hinze Dam WTP Plan HACCP flow diagram and schematic diagram updated to show Cedar Lakes raw water supply off raw water main and separation from Hinze Dam WTP HACCP system assets. Refer HACCP Plan Appendix 1 drawing ‘Cedar Lakes Line’ • Aerial photograph updated to show location of cedar lakes supply from below dam wall off raw water main. • Section 2.1.3.6 further updated to state that the Cedar Lakes raw water supply system assets are physically separate from the potable water assets and management of the Cedar Lakes raw water supply system is not covered under PLN-00073 Hinze Dam WTP HACCP Plan. | Refer REX D19/10720 | TF | 2019-01-31 | Y
347 | PLN-00071 | Mudgeeraba WTP | HACCP Plan | 1.2 2.1.1. 2.1.2 2.1.3 3.2 4.2 6.0 | All process step terminology and CCP/QCP/oPRP alignment with WQ Risk Dashboard Associated docs list updated 1.2 Conditions of operation table – further detail added. Values unchanged. 2.1.1 HACCP team – CWQ Coord added. Previous omission. 2.1.2 HACCP flow diagram updated to include interconnecting Res1/Res2 pipeline which is C.t and fluoride bypass. HACCP schematic diagram minor updates for location of raw water flow meters and include interconnecting Res1/Res2 pipeline 2.1.3 aerial photograph updated Catchment and Storages description updated by CWQ Coord Disinfection primary description updated to include more detail on virus and bacteria log inactivation. C.t calc also updated. Min chlorine value unchanged. 3.2 Validation table updated based on changed to PRO-02028 – Mudgeeraba WTP – HACCP Plan Wall Chart Procedure and further detail added for some limits. 4.2 oPRP section now PRP section. Section paragraph updated and table updated. 6 Materials and chemical Section paragraph updated and table updated based on REG-00250 now overarching panel list register. | Refer markups D19/36056 | TF | 2019-03-26 | Y
348 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | Disinfection (primary) | All process step terminology and CCP/QCP/oPRP alignment with WQ Risk Dashboard Disinfection (primary) – treated water turbidity listed as HACCP reportable parameter in line with new HACCP limit. | Refer markups D19/36062 | TF | 2019-03-26 | Y
349 | PRO-02028 | Mudgeeraba WTP | HACCP Plan Wall Chart Procedure | Raw Water Abstraction Taste and Odour control Floc and Settling Mn and Fe removal Disinfection (primary) | All process step terminology and CCP/QCP/oPRP alignment with WQ Risk Dashboard Raw water abstraction target turbidity changed from <5 NTU to turbidity at last coag dose change as per SPE-00320. Action limits separated for HUI and LND supplies. Note added re shutdown based on operations team assessment. Taste and odour control critical limit for T&O results/complaints now action limit. Flocculation and Settling – settled water turbidity target changed ‘≤2’ to ‘<’ in line with SPE-00320. Action limit increased from >3 NTU to >5 NTU as per SPE-00320 and WTP expected performance. Manganese and Iron control – upper free chlorine action limit reduced from 0.8 mg/L to 0.7 mg/L in line with SPE-00320. Critical limit for upper free chlorine timeframe reduced to 15 mins and lower limit timeframe reduced to 2 hours. Refer HACCP plan section 3.2 validation. Disinfection (primary) pH targets and limits updated and aligned for dosed filtered water pH and treated water pH to better align with CRE protocols/supply agreement. Refer HACCP plan section 3.2 validation. Disinfection (primary) new target and action limit added for treated water turbidity to detect any disturbance or other issue that has the potential to impact free chlorine disinfection. | Refer markups D19/36058 | TF | 2019-03-26 | Y
350 | GDE-00061 | Canungra WTP | Verification Sample Point Guide | obsolete | Old WTP demolished 14/12/18 | Refer email Paul F 14/12/18 Inadvertently omitted from list of docs sent through to be obsolete 20/12/18 | TF | 2019-03-29 | Y
351 | PLN-00040 | North Stradbroke Island WTP | HACCP Plan | 1.2 2.1.1 2.1.2 2.1.3 2.1.4 3.2 4.2 6 | List of Associated docs updated 1.2 conditions of application updated based on figures from other authoritative docs 2.1.1 CWQ Coord added to HACCP team – previous omission 2.1.2 Flow diagram updated to include new geotube installation and poly dosing into sludge collection pit (supernatant return CCP) and new CCT outlet Cl, pH monitoring (Disinfection (primary) CCP. WTP aerial photograph updated to more recent image. 2.1.3 Catchment & Storage description updated based on feedback from CWQ Coord. Supernatant Return CCP description updated based on upgrades. Coagulation CCP updated to describe change in poly from AN905 to LT-20 and change in poly dosing pump configuration. Media Filtration CCP updated to describe backwash limitation based on BWRT level. Disinfection (primary) CCP to describe interlock process and further detail of HBT, C.t calc updated to reflect lower reservoir level value. 2.1.4 operational challenges updated 3.2 Validation: all sections updated to include values and validation details. New Supernatant return and Disinfection (primary) CCP limits added in line with upgrades and new analysers. 4.2 Operational Pre-requisite Programs (oPRPs) entire section updated to reference overarching Register and site based oPRPs. 6 Materials and chemicals updated to reflect overarching panel register and changes to poly on site. Documents references and terminology updated throughout doc. | Refer markups D19/46529 | TF | 2019-04-15 | Y
352 | PRO-02058 | North Stradbroke Island WTP | HACCP Plan Wall Chart Procedure | All | Raw Water Abstraction QCP raw water colour target changed from absolute values to moving values. Removal of Critical Limit. Refer HACCP plan validation and wall chart. Supernatant Return CCP new HACCP limits following upgrades and new online analysers Coagulation CCP limits aligned with SPE-00320. DAF CCP action limit aligned with SPE-00320 Disinfection (primary) CCP new CCT outlet pH and free chlorine targets and limits following installation of new analysers. Treated water reservoir level limits adjusted to reflect current operation. Fluoridation CCP lower fluoride action limits (pre and post) timeframes extended from 60 mins to 4 hours. No increase in WQ risk. Treated water CCP removed as per R.A. Not a process step. | Refer markups D19/46532 | TF | 2019-04-15 | Y
353 | PLN-00076 | North Stradbroke Island WTP | Operational Monitoring Plan | Supernatant return Disinfection (primary) | NEW Supernatant return CCP monitoring added NEW CCT outlet pH and Cl online/verification monitoring added Removal of note at end of table for combined filtered water sample monitoring. Individual filtered water analyser verification well embedded. Combined filtered water sampling redundant. Updates to Process step to align with R.A. Updates to terminology of Process Steps and monitoring location throughout. | Refer markups D19/46530 | TF | 2019-04-15 | Y
354 | PLN-00040 | North Stradbroke Island WTP | HACCP Plan | 1.2 2.1.4 3.2 | 1.2 Conditions of operation & 2.1.3.2 Supernatant Return: updates to supernatant return flow rate figures. 2.1.4 Operation challenges: issue relation to location of CCT analysers causing delay time and CCT process fluctuations 3.2 Validation: Disinfection (primary) validation for HACCP limit timeframes amended as per wall chart. | Refer markups D19/54343 | TF | 2019-05-08 | Y
355 | PRO-02058 | North Stradbroke Island WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) | CCT upper and lower free chlorine & upper pH action limit timeframes extended from 30 mins to 75 mins CCT upper and lower free chlorine & upper pH critical limit timeframes extended from 15 mins to 60 mins Changes due to: 1. The location of the analysers in relation to the sample point causing a delay in measuring a process change 2. Current process fluctuations in CCT for pH and chlorine | Refer markups D19/54342 | TF | 2019-05-08 | Y
Submission to Regulator - DWQMp Annual Report 2019
356 | PLN-00069 | Molendinar WTP | HACCP Plan | 1.2 2.1.2 2.1.3 2.1.4 | •1.2 Conditions of Application: clarification on transfer of product from Molendinar WTP to Seqwater Supply System. Updates to describe no alarm masking on start up and removal of reference to treated water pump interlocks not in place – now in place. •2.1.2 Flow diagrams: addition of Cedar lakes raw water supply of raw water main as per QWSR RFI, improved illustration of raw water supply arrangement, supply to dosed water pH analysers updated, inclusion of backwash pumps from CCT and option to transfer to inlet channel (new recirc), improved illustration of WTP handover to supply system, inclusion of CCT partial bypass from backwash channel to treated water main (pre existing but previously not captured/illustrated). •2.1.3 Conditions of Operation: Media Filtration: updated to remove description of old high velocity backwash pumps in inlet channel and describe new backwash pumps and ability to pump water from CCT back to inlet channel. •2.1.4 Operational Challenges: updated to include limitations in backwash area associated with high velocity backwash sequence and removal of reference to treated water pump interlocks not in place. | Refer markups D19/93466 D17/6063 Water Quality Risk Dashboard for Molendinar WTP also updated to include the following new hazardous events: •Disinfection (primary) CCP: Contamination due to backflow – backflow from inlet channel into filter outlet pipework – not possible due to air gap but needs to be captured that design provides risk mitigation (new) •Disinfection (primary) CCP: Failure or incorrect operation of bypass valve – failure or operation (opening) of CCT gravity main valve (pre-existing but not previously documented) – not acceptable for use due to absence of interlock functionality •Disinfection (primary) CCP: Failure or incorrect operation of bypass valve – incorrect valve configuration between treated/backwash water pump 5 and treated water pipework resulting in bypass of main CCT tank channel and bypass of treated water analysers (pre-existing but not previously documented) – valve configuration must be correct to prevent contact time bypass and bypass of analysers •Risk reductions will occur at R.A review later this year following introduction of treated water pump interlocks last year and improvements to ingress points into CCT thanks to Sam’s team. | TF | 2019-07-10 | Y
357 | PLN-00075 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan | 1.2 2.1.1 2.1.2 2.1.3 2.1.4 Appendix A | 1.2 Conditions of Application: updates to Dunwich to include Bore 4. Inclusion that this revision of the HACCP plan does not cover operating in filter bypass mode. 2.1.1 HACCP Team: inclusion of CWQ Coord 2.1.2 Dunwich HACCP and schematic diagrams updated to include filter bypass (labelled as closed) and filter backwash storage tanks 2.1.3.1 Raw water abstraction: updates to Dunwich to include bore 4 2.1.3.3 Media Filtration: updates to iron treatment criteria, updates to backwash capturing, updates to describe bypass 2.1.3.4 Disinfection (primary): updates to C.t calcs and HBT assessment description 2.1.4 Operational challenges: removal of item relating to absence of filtered water turbidity meter. Inclusion of insufficient C.t for Dunwich and WQ bore characteristic challenges. Appendix A: removal of maps as outdated and not required. Refer aerial photographs section 2.1.2. | Refer markups D19/99759 | TF | 2019-07-22 | Y
358 | PRO-02099 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan Wall Chart Procedure | Raw Water Abstraction | Raw Water Abstraction: Bore 4 max turbidity included for reference | Refer markups D19/99758 | TF | 2019-07-22 | Y
359 | PLN-00357 | Canungra WTP | HACCP Plan | 2.1.1 3.2 6 | • Section 2.1.1 HACCP Team: addition of CWQ Coord to HACCP team table. • Section 3.2 HACCP Limit Validation: updated to reflect changes to Wall Chart. • Section 6 Materials and Chemical: update to include pot perm, fluoride and caustic. | Refer markups D19/127254 | TF | 2019-09-06 | Y
360 | PRO-02109 | Canungra WTP | HACCP Plan Wall Chart Procedure | Floc & Settling QCP Membrane Filtration CCP | • Flocculation & Settling QCP Membrane Balance Tank free chlorine target and action limit moved from Mn and Fe Control QCP to Membrane Filtration CCP as the intent is to provide some pre-oxidation of settled water to improve performance of the membrane filters and not specifically treat for Mn. No change to limits. • Membrane Filtration CCP Protozoa-LRV target reduced from >4.5 to >4.2 and action limit reduced from <4.5 to <4.2. Change is based on being sufficiently above the minimum P-LRV specification of 4.0 P-LRV (critical limit) and allowing for operational flexibility with regard to triggers for backwash and CIP. This in turn provides more flexibility with flow rate and run time (within design specification). | No change to OMP required. Refer markups D19/127255 | TF | 2019-09-06 | Y
361 | GDE-00063 | North Stradbroke Island WTP | Verification Sample Point Guide | Bore raw water tap Treated water tap | • Update to new format • New Bore Raw Water No 2 sample tap and code due to changes made to laboratory taps on site. • New Treated Water sample tap and code due to changes made to laboratory taps on site. | ION raised for further future changes to location of treatd water sample tap | TF | 2020-03-30 | Y
362 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2018-01-09 | Y
363 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-08-29 | Y
364 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-10-14 | Y
365 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-01-24 | Y
366 | REF-00460 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated & mitigated) | Refer Veolia doc management system | RA review updates - Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-02-06 | Y
367 | REF-00460 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated & mitigated) | Refer Veolia doc management system | Cyber risk inclusion into RA - Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-08-20 | Y
368 | REF-00461 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated & mitigated) | Refer Veolia doc management system | RA review updates - Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-10-15 | Y
369 | REF-00462 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated & mitigated) | Refer Veolia doc management system | Pretreatment polymer and sulphuric acid RA review updates - Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-12-18 | Y
370 | REF-00309 | Gold Coast Desalination Plant | HACCP Validation Plan | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-03-14 | Y
371 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-10-02 | Y
372 | REF-00307 | Gold Coast Desalination Plant | HACCP Treated Water Quality Specification | Refer Veolia doc management system | Refer Veolia doc management system | Refer Veolia doc management system | Veolia | 2019-08-09 | Y
373 | REF-00490 | Gold Coast Desalination Plant | HACCP Corrective Actions | New doc | Document has always existed in Veolia's document management system and has now been uploaded into Seqwater's document management system for ease of access and reference. This documents is managed (reviewed, updated, audited) through Veolia’s management systems. The document review process involves a review step by representatives of the Water Quality Team (process documented in HACCP Plan). Lead Water Quality - Manufactured Water will be aware of any updates and will forward these through to QPulse accordingly. | Refer Veolia doc management system | Veolia | 2019-12-04 | Y
374 | PLN-00094 | Rathdowney WTP | HACCP Plan | 1.2 2.1.1 2.1.2 2.1.3 3.2 4.1 4.2 6 | • 1.2 Conditions of Application: documentation of coag low flow alarm masking of 5 mins on start up. • 2.1.1 HACCP team: updates to position descriptions and separation of process labs from data services • 2.1.2 Flow diagrams: change from magnasol 589 to ACH. Removal of optional settled water chlorine dose. Note: pre filter chlorine assets still in place. If pre-filter chlorine were to be re-initiated refer to previous HACCP Risk Assessment and review and MoC process. Not covered under current HACCP plan. Would need to go Moc. Not captured in wall chart, monitoring plan or risk assessment. Justification for not reinstating – destruction of biofilter. • 2.1.3 System overview: change of description of coagulation system from 589 to ACH. Removal of option to dose settled water chlorine • 3.2 Validation: updated to reflect changes to HACCP Wall Chart • 4.1 Operational Procedures: updated to reflect changes to Operator Checklists, changes to 589 drop test and jar test work instructions • 4.2 PRPs: updated to reflect more recent Risk Assessment – no oPRPs identified during R.A 2020 • 6 Material and Chemicals: updated to reflect change from magnasol 589 to ACH. Delivery and transport notes added. • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer D20/117099 markups | TF | 2020-07-06 | Y
375 | PRO-01768 | Rathdowney WTP | HACCP Plan Wall Chart Procedure | Supernatant Return Coagulation Floc & Settling Disinfection (primary) | • Supernatant Return CCP: rate of return critical limit symbol changed from ‘>’ to ‘≥’ • Coagulation CCP: removal of max 589 dose rate critical limit; coagulant dose rate flow critical limit changed from no flow for > 5 mins to <3mL for 5 seconds based on outcome of Jan incident; settled water colour action limit changed from >10 HU to >5 HU in line with SPE-00320 standard • Flocc & Settling QCP: settled water turbidity target changed from <3NTU to <2NTU; action limit changed from >10 NTU for 2 hours to >5 NTU for 1 hour in line with SPE-00320 standard • Disinfection CCP: min reservoir level timeframe changed from ‘any time’ to ‘5 mins’ to allow for consistency between SCADA and wall chart • Updates to reporting from Form 27 to Risk Wizard in reporting tables • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer D20/117098 markups | TF | 2020-07-06 | Y
376 | PLN-00093 | Rathdowney WTP | Operational Monitoring Plan | Minor | • Changes to Process Steps from oPRPs to QCPs are per Risk Assessment 2020; changes from 589 to ACH; removal of reference to RAT-SP920 for free chlorine monitoring. • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer D20/117100 markups | TF | 2020-07-06 | Y
377 | PLN-00075 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan | 1.2 2.1.1 2.1.2 2.1.3 3.2 4.1 4.2 | • 1.2 Conditions of Application: updates to WTP flow rates based on Functional Descriptions. TPL Bore 1 flow rate TBC. • 2.1.1 HACCP team: updates to position descriptions and separation of process labs from data services • 2.1.2 Flow diagrams: no change. Bore 1 was existing in diagrams. • 2.1.3 System overview: updates to bore flow rates and status. Updates to HBT assessment for TDU. • 3.2 Validation: updated to reflect changes to HACCP Wall Chart. Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 • 4.1 Operational Procedures: updated to reflect changes to Operator Daily site inspection checklists, addition of Operations Manuals. • 4.2 PRPs: updated to reflect more recent Risk Assessment – oPRP 1 Bore cleaning | Refer markups D20/117113 | TF | 2020-07-06 | Y
378 | PRO-02099 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan Wall Chart Procedure | TDU: Media Filtration TPL: Raw Water Abstraction | • TDU: Media Filtration: NEW HACCP critical limit filtered water turbidity >1.0 NTU for 15 minutes • TPL: Raw Water Abstraction: reduction of combined Raw Water turbidity action limit from 1.0 NTU to 0.5 NTU and NEW HACCP critical limit for individual bores >1.0 NTU. Purpose is to have triggers and corrective actions in place to if/when bore turbidity high. We had a Bore 1 turbidity result >1 NTU which indicates that there is still potential for fluctuation and uncertainty as to whether this will reduce with time. Predominately <1 NTU. • Updates to reporting from Form 27 to Risk Wizard in reporting tables • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer markups D20/117111 | TF | 2020-07-06 | Y
379 | PLN-00144 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | Operational Monitoring Plan | Raw water abstraction | • Raw water Abstraction: individual Bore sample as required i.e when daily combined raw water sample >Action Limit. • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer markups D20/117112 | TF | 2020-07-06 | Y
380 | PLN-00091 | Beaudesert WTP | HACCP Plan | 1.2 2.1.1 2.1.2 2.1.3 2.1.4 3.2 4.1 4.2 6 | • 1.2 Conditions of Application: description of use of diesel pumps in high flow events • 2.1.1 HACCP team: updates to position descriptions and separation of process labs from data services • 2.1.2 Flow diagrams: online raw water ammonia removed and grab sample added, new storages added, breakpoint free/total chlorine after GAC pumps not before, removal of alum dose before aerator, new alum dosing point in aerator bell mouth, updated aerial photo, note to include Bromelton storage currently offline • 2.1.3 System overview: updates to all process steps following review and inclusion of new storages. • 2.1.4 Operational Challenges: updated to reflect current challenges • 3.2 Validation: updated to reflect changes to HACCP Wall Chart • 4.1 Operational Procedures: updated to reflect changes to Operator Checklists, changes to 589 drop test and jar test work instructions • 4.2 PRPs: updated to reflect 2020 Risk Assessment – oPRP1 included • 6 Material and Chemicals: sodium hydroxide % strength added. • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer markups D20/139976 | TF | 2020-08-03 | Y
381 | PRO-02105 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Raw Water Abstraction Coagulation Manganese and Iron Control Fluoridation Disinfection (primary) GAC Disinfection (secondary) | • Raw Water Abstraction QCP: Addition of <100 NTU to current raw water turbidity action limit ±10 NTU; new raw water turbidity action limit if >100 NTU ±50 NTU which factors in higher coag dose rates at higher turbidity’s. Replacement of online raw water ammonia HACCP limit timeframe to ‘grab sample’ due to inoperability of raw water ammonia analysers and risk mitigation provided by existing filtered water analyser. • Coagulation CCP: low alum dose rate critical limit changed from <50% of setpoint to <6.0 L/Hr for 2 mins due to currently control system functionality supporting absolute value rather than % value; alignment of coagulated water pH limits with SPE-00320 for sites targeting organics removal. • Manganese and Iron Control CCP: new process step. Limits previously in media filtration step. Dosed settled water pH limits aligned with SPE-00320 with exception of lower pH action limit which is 6.9 rather than 7.0 due to proximity of action limit 7.0 to target 7.1 in light of acceptable instrument tolerance range; filtered water free chlorine lower action limit reduced from 0.2 to 0.1 due to management of risk of THMs at this site balanced against low level Mn risk, timeframes based on grab samples, absence of filtered water chlorine monitoring and insufficient dosing system design. • Fluoridation CCP: critical limit timeframe reduced to 2 mins to reduce impact of fluoride overdose on volume in new storages which wouldn’t be picked up until treated water pumps. • Disinfection (primary) CCP: filtered water ammonia limits reduced and critical limit introduced to account for removal of online raw water ammonia monitoring; dosed irradiated water pH action limit increased to align with UU comms trigger; new breakpoint water free chlorine targets and limits based on using this analyser under all operating modes going forward; min level of CCT reduced based on re-calc of C.t • GAC CCP: Max GAC flow rate introduced for purposes of C.t • Disinfection (secondary) CCP: New reservoir feed targets and limits based on new analysers; reduction of treated water chlorine based on new storages as per UU comms trigger; turbidity critical limit added to detect turbidity >UU comms trigger. • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer markups D20/139973 | TF | 2020-07-31 | Y
382 | PLN-00092 | Beaudesert WTP | Operational Monitoring Plan | Raw Water Abstraction Coagulation Disinfection (secondary) | • Removal of online ammonia, addition stabilised water pH, addition reservoir feed chlorine, pH, turbidity • Alignment of Process Steps QCPs/CCPs with Risk Assessment 2020 | Refer markups D20/139974 | TF | 2020-07-31 | Y
Submission to Regulator - Amendment Application August 2020
383 | PRO-02105 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) Disinfection (secondary) | • Disinfection (primary) CCP: breakpoint water (after CCT) target range increased from 2.5-3.0 mg/L to 2.5-3.5 mg/L. Upper action and critical limits increased from 3.0 mg/L to 3.5 mg/L and 3.5 mg/L to 4.0 mg/L respectively to allow for increased chlorine dose to reliably meet treated water free chlorine targets. • Disinfection (secondary) CCP: reservoir feed free chlorine target range increased from 2.5-3.0 mg/L to 2.5-3.5 mg/L. Upper action and critical limits increased from 3.0 mg/L to 3.5 mg/L and 3.5 mg/L to 4.0 mg/L respectively to allow for increased chlorine dose to reliably meet treated water free chlorine targets. | Refer markups D20/148650 | TF | 2020-08-13 | Y
384 | PLN-00091 | Beaudesert WTP | HACCP Plan | 2.1.3 3.2 6 | • 2.1.3 System overview: updates to various process step descriptions to include Health Based Target pathogen log reduction information. • 3.2 Validation: updated to reflect changes to HACCP Wall Chart • 6 Materials and Chemicals: addition of PAC and sodium chloride (water softener) previous omission | Refer markups D20/148652 | TF | 2020-08-13 | Y
385 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | 8.43 6.6 2.1 2.3 3.1 5.2.1 6.6 | update section 8.4.3 (Reporting) of HACCP Plan. Include Pest Control procedures in PRP's list for HACCP Plan. (section 6.6) Updated with requirements for HACCP Barrier risk assessments when maintenance / process intervention is required. (PRP's, Section 6.6) Updated Section 2.1 - Organisational Chart Updated Section 2.3 - Food Safety / HACCP Team Updated Figure 3.1 - Supply System Schematic Updated Section 5.2.1. to include "or a suitably qualified Process Engineer" for flow diagram review / verification. Update to HACCP Team table. Updated Section 6.6 PRP description (1st paragraph). Updated Section 6.6 to include the PRP Table (Table 6.4) | Markups recorded in Veolia document management system | Veolia/EH | 2020-08-21 | Y
386 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | Assocaited docs 1.2 Conditions of Operation 2.1.1 HACCP Team 2.1.3 System overview 2.1.4 Operational challenges 3.2 Validation 4.2 PRPs 6 Materials and Chemicals | • Associated documents updated to include additional references • 1.2 Conditions of Application: Max flow rate increased as per MAN-00328A Operations Manual. Further validations regarding max treated water flow rate. • 2.1.1 HACCP Team: position names updated. CWQ added. Previous omission • Flow Diagram and Schematic Diagram updated to include PAC dosing • 2.1.3 System overview: addition of T&O process step. Various other descriptive updates. • 2.1.4 Operational challenges: updated now that filtered water pH in place. • 3.2 HACCP Limit Validation: updated to reflect changes to Wall Chart • 4.2 Prerequisite programs: updated to reflect 2019 R.A. Nil determined. • 6 Materials and chemicals: updated to include PAC, sodium hydroxide, sodium chloride | Refer markups D20/172485 | TF | 2020-09-28 | Y
387 | PRO-02003 | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | Supernatant Return CCP T&O control QCP Coagulation CCP Fluoridation CCP UV Disinfection CCP | • Supernatant Return CCP Addition of ‘high turbidity’ text corrective actions to align with other corrective action guidance headings • NEW Taste & Odour Control QCP New HACCP limits based on PAC dosing for purpose of T&O control. • Coagulation CCP Change of critical limit from ‘No coagulant dose’ to ‘Alum dose rate <6 L/hr’ to remove ambiguity with regard to SCADA v. Wall Chart alignment. Note: SCADA value of zero not appropriate to detect loss of alum dose as SCADA trend will always have small fluctuations above zero when alum dosing lost preventing interlock being triggered. • Fluoridation CCP Dosed filtered water (pre) fluoride critical limit timeframe reduced from 15 mins to 2 mins to allow for earlier interlocking of fluoride dosing system (corrective action) to reduce impacts to treated water (post) fluoride levels further reducing any impacts to supply as agreed by DWQ and Ops Supervisor. • UV Disinfection CCP Change of target from ‘UV Dose’ to UV system 1 and 2 ‘Healthy’ and Change of critical limit from ‘UV Dose’ to UV system 1 and 2 ‘Alarm’ based on outputs from UV system at this WTP indicative of validated dose rate <40 mJ/cm2. • General items Alignment of CCP/QCP with Risk Assessment General updates to Critical Limit corrective action guidance wording and update of references from Form 27 to Risk Wizard. Changes from ‘QUU’ to ‘UU’. Ops protocol THM value reduced from 175 µg/L to 130 µg/L as per current Ops protocol revision | Refer markups D20/172484 | TF | 2020-09-28 | Y
388 | PLN-00119 | Boonah-Kalbar WTP | Operational Monitoring Plan | General | • Alignment of Process step names with Risk Assessment | Refer markups D20/172494 | TF | 2020-09-28 | Y
389 | PLN-00091 | Beaudesert WTP | HACCP Plan | 3.2 Validation | • Section 3.2 Validation – updated to describe validation relating to changes. The lower pH Action Limit for dosed irradiated water and reservoir feed water pH <6.9 has been set at the time of this revision which is slightly below the Operating Protocol limit trigger of pH 7.0. This is due to an increase of approx. 0.3-0.4 pH units occurring through the new onsite storage reservoirs. It’s expected that the impact of these new assets on the treated water pH will reduce with time (approx. 6 months) and the action limit can once again be increased back in line with Operating Protocol limit trigger. | Refer markups D20/173997 | TF | 2020-09-30 | Y
390 | PRO-02105 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) Disinfection (secondary) | • Disinfection (primary) CCP: Dosed Irradiated Water pH action limit reduced from pH<7.0 to pH<6.9 • Disinfection (secondary) CCP: Reservoir Feed Water pH action limit reduced from pH<7.0 to pH<6.9 • Table of Definitions wording updated. | Refer markups D20/173996 | TF | 2020-09-30 | Y
391 | PLN-00075 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan | Associated docs 2.1.2 Flow diagrams 2.13 system overview 3.2 validation | o Associated docs: addition of Supernatant UV system documents o 2.1.2 Flow Diagrams: Dunwich WTP schematic and HACCP flow diagrams updated to included supernatant return CCP. Aerial photo updated to show location of supernatant return CCP system assets. o 2.1.3 System overview: New section for Supernatant return CCP describing backwash handling system, cartridge filter and UV disinfection system. o 3.2 Validation: updated to reflect new supernatant return CCP and updated to reflect other changes to HACCP limits. | Refer markups D20/176220 | TF | 2020-10-07 | Y
392 | PRO-02099 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | HACCP Plan Wall Chart Procedure | TDU: New supernatant return Disinfection (primary) TPL: Raw water Abstration TAP: Disinection (primary) | o TDU new supernatant return targets and limits for rate of return, supernatant turbidity, UV dose o TPL raw water turbidity HACCP limit in line with other WTPs o TAP reduced timeframe for dosed water chlorine from 15 mins to 5 mins (trial) based on detecting low chlorine before it impacts treated water chlorine (refer incident Nov 2018) o TDU Disinfection CCP HACCP limits updated to achieve a minimum C.t of 8 mg.min/L | Refer markups D20/176221 | TF | 2020-10-07 | Y
393 | PLN-00144 | North Stradbroke Island Town WTPs (Amity, Dunwich & Point Lookout) | Operational Monitoring Plan | TDU: New supernatant return | o TDU new Supernatant return CCP monitoring | Refer markups D20/176221 | TF | 2020-10-07 | Y
394 | GDE-00069 | Hinze Dam WTP | Verification Sample Point Guide | Treated water sample tap pic and GPS | Updated photo of Hinze Dam WTP treated water verification sample point HIN-SP920 and GPS location information. Updated due to upgrade of above ground pipework supplying sample tap as part of reticulation system leak repair job. Refer OCA 1143722 / Risk Wizard Incident 22395. Location of sample point in the process. Still on treated water main on outlet of treated water reservoir / CCT. | Refer markups D20/173668 | TF | 2020-10-08 | Y
395 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Whole of document | Updated historic grid manager and DEWS references to Seqwater and DNRME. | Markups recorded in Veolia document management system | Veolia/EH | 2020-11-24 | Y
396 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Section 1.1 | Table added near the front of the HACCP plan to cross reference the Seqwater doc numbers and titles with the Veolia document reference numbers and titles | Markups recorded in Veolia document management system | Veolia/EH | 2020-11-24 | Y
397 | GDE-00064 | Dunwich WTP | Verification Sample Point Guide | Bore sample point taps Doc Ref list | Added the production bores to the Verification sample point guides for Dunwich, Amity Point & Point Lookout. Edited the ref document list on each file & updated the version # etc. | Updates by Field Science team | TF/SPH | 2020-11-03 | Y
398 | GDE-00066 | Point Lookout WTP | Verification Sample Point Guide | Bore sample point taps Doc Ref list | Added the production bores to the Verification sample point guides for Dunwich, Amity Point & Point Lookout. Edited the ref document list on each file & updated the version # etc. | Updates by Field Science team | TF/SPH | 2020-11-03 | Y
399 | GDE-00065 | Amity Point WTP | Verification Sample Point Guide | Bore sample point taps Doc Ref list | Added the production bores to the Verification sample point guides for Dunwich, Amity Point & Point Lookout. Edited the ref document list on each file & updated the version # etc. | Updates by Field Science team | TF/SPH | 2020-11-03 | Y
400 | PLN-00073 | Hinze Dam WTP | HACCP Plan | 2.1.3 System overview 6 Material and chemicals | updated to address DWQMP approval OFI raised by regulator for your review and approval. Section 2.1.3 System overview: description of material, age and conditions of pipes and reservoirs added. Section 6 Material and chemicals: note regarding process configuration scenario where PAC can be dosed into the raw water that supplies Hinze Dam WTP when dosing the raw water that supplies Molendinar WTP. | Refer markups D20/214514 | TF | 2020-12-03 | Y
401 | GDE-00054 | Boonah-Kalbar WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220811 | TF | 2020-12-16 | Y
402 | GDE-00055 | Maroon Dam WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 2 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Maroon Dam WTP – reticulation sample tap photo cropped following removed of ‘no naked flames’ signage • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220813 | TF | 2020-12-16 | Y
403 | GDE-00056 | Moogerah Dam WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Moogerah Dam WTP – section 1 updated to state that raw water can be sampled when WTP offline • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220819 | TF | 2020-12-16 | Y
404 | GDE-00057 | Kooralbyn WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220822 | TF | 2020-12-16 | Y
405 | GDE-00058 | Rathdowney WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220831 | TF | 2020-12-16 | Y
406 | GDE-00059 | Beaudesert WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 2 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Beaudesert WTP – new sample tap before new reservoirs added HEL-SP911 • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220832 | TF | 2020-12-16 | Y
407 | GDE-00067 | Molendinar WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220839 | TF | 2020-12-16 | Y
408 | GDE-00068 | Mudgeeraba WTP | Verification Sample Point Guide | Doc Ref list Section 1 Section 3 | • Updated Document reference table to remove obsolete documents • Updated Notification requirements to reflect PASS system • Simplified sign on/off wording • Removed Section 3 document history table from some procedures as it’s not consistently in all docs | Refer markups REX D20/220842 | TF | 2020-12-16 | Y
409 | PLN-00037 | Capalaba WTP | HACCP Plan | Associated docs 1.2 Conditions of Application 2.1.1 HACCP Team Flow diagrams 2.1.3 system overview 3.2 HACCP limit validation 4.2 PRPs 6 Materials and Chemicals | • Associated documents updated to include additional references • 1.2 Conditions of Application: Max flow rate updated as per MAN-00328A Operations Manual along with further validations regarding max treated water flow rate. • 2.1.1 HACCP Team: position names updated. CWQ added. Previous omission • Flow Diagram and Schematic Diagram updated to include new lime sediment pipework to vac truck connection • 2.1.3 System overview: Various other descriptive updates to all sections including HBT assessment description • 3.2 HACCP Limit Validation: updated to reflect changes to Wall Chart • 4.2 Prerequisite programs: updated to reflect 2019 R.A. Nil determined. • 6 Materials and chemicals: updated to remove supplier details which are covered in REG-00250 and chemical names updated | Refer markups D20/207684 and D20/223490 | TF | 2020-12-18 | Y
410 | PLN-00037 | Capalaba WTP | Operational Monitoring Plan | Coagulation CCP Raw Water Abstraction General alignment | • Filtered water UVT moved from Coagulation CCP as it’s covered in UV Disinfection CCP • Removal of raw water (total) manganese monitoring. Only require raw Mn (sol) as a minimum in accordance with SPE-00320 however can continue to do this test if Ops wants to do it. • Alignment of Process step names with Risk Assessment | Refer markups D20/207682 | TF | 2020-12-18 | Y
411 | PLN-00037 | Capalaba WTP | HACCP Wall Chart | Supernatant Return CCP Coagulation CCP Manganese and Iron Control CCP UV Disinfection CP General items | • Supernatant Return CCP Reduction of turbidity action and critical limit in line with SPE-00320 standard. • Coagulation CCP Reduction of upper pH target value to bring in line with SPE-00320; UVT action limit moved to UV Disinfection CCP; addition of lookup table / WTC Coag App to operational target; change of critical limit from ‘No coagulant dose’ to ‘Alum dose rate <15 L/hr’ to remove ambiguity with regard to SCADA v. Wall Chart alignment. Note: SCADA value of zero not appropriate to detect loss of alum dose as SCADA trend will always have small fluctuations above zero when alum dosing lost preventing interlock being triggered. • Manganese and Iron control CCP Reduction of upper action limit from 1.0 mg/L to 0.8 mg/L and timeframe extended to two consecutive days; reduction of upper critical limit from 1.2 mg/L to 1.0 mg/L in line with SPE-00320 for management of DBP risk; inclusion of lower critical limit of <0.1 mg/L as per SPE-00320. • UV Disinfection CCP Filtered water UVT action limit moved to UV Disinfection step to reduce ambiguity. Change of wording of HACCP critical limits to include flow rate and UVT conditions. • Disinfection (primary) CCP Upper treated water action limit reduced from 3.0 mg/L to 2.5 mg/L to bring in line with Operating Protocol upper limit of 2.5 mg/L. Min free chlorine critical limit increased from 0.8 mg/L to 0.9 mg/L based on updated pipe dimensions. • General items Alignment of CCP/QCP with Risk Assessment General updates to Critical Limit corrective action guidance wording and update of references from Form 27 to Risk Wizard. Ops protocol upper free chlorine value 2.5 mg/L added as per current Ops protocol revision and Wall Chart critical limit corrective action relating to verification of analyser. Inclusion of process when HACCP critical limit instrument fails. | Refer markups D20/207680 | TF | 2020-12-18 | Y
412 | PLN-00095 | Kooralbyn WTP | HACCP Plan | 6 Materials and chemicals | sodium chloride (salt for water softener) added to table | Refer markups REX D20/224211 | TF | 2020-12-18 | Y
413 | PLN-00091 | Beaudesert WTP | HACCP Plan | 2.1.2 Flow diagrams 2.1.3 System overview 6 Materials and Chemicals | • 2.1.2 Flow diagrams: addition sulphuric acid dosing into raw water main. • 2.1.3 System overview: updates to Coagulation section to include sulphuric acid dosing system. • 6 Material and Chemicals: addition of sulphuric acid | Refer markups REX D20/224151 | TF | 2020-12-18 | Y
414 | PLN-00092 | Beaudesert WTP | Operational Monitoring Plan | Raw water abstraction | • Typo referring to Raw water abstraction as oPRP changed to QCP as per Risk Assessment. Stabilised Water pH daily verification was already in there from last update. | Refer markups REX D20/224152 | TF | 2020-12-18 | Y
415 | PRO-02105 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Coagulation | • Coagulation CCP: no change to HACCP limits. Updates to corrective action guidance for Coagulation CCP to include sulphuric acid dosing system checks and corrective action. • There is a new stabilised water pH analyser however we have not applied a HACCP limit to this as the Coag CCP pH meter will continue to be the CCP. | Refer markups REX D20/224153 | TF | 2020-12-18 | Y
416 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | 2.1.3 system overview 3.2 Validation | 2.1.3.8 Fluoridation system overview: removal of unnecessary detailed description of regulatory requirements. Duplicated in other procedures 2.1.3.9 Disinfection (primary) added detail on dosing modes 3.2 Validation: updated to reflect above changes to Wall Chart. Typo referring to filtered water UVT limit corrected to treated water UVT limit. | Refer markups REX D21/19709 | TF | 2021-02-05 | Y
417 | PRO-02003 | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) CCP | Increase in dosed filtered water target from 3.0-3.5 mg/L up to 4.3 mg/L Increase in dosed filtered water action limits from <2.0 or >4.0 mg/L up to <3.0 or >4.7 mg/L Increase in dosed filtered water critical limit from >4.5 to >4.9 mg/L Increase in treated water target from 2.0-2.5 mg/L to 3.3 mg/L (agreed with Urban) Increase in treated water action limits from <1.5 or >3.0 to <2.5 or >3.6 mg/L Increase in treated water critical limit from >3.5 mg/L to >3.8 mg/L | Refer markups REX D21/19707 | TF | 2021-02-05 | Y
418 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | 3.2 Validation | 3.2 Validation: updated to reflect above changes to Wall Chart. | Refer markups REX D21/35632 | TF | 2021-03-04 | Y
419 | PRO-02003 | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) CCP | Assisting UU in managing distribution system free chlorine residual: Dosed filtered water free chlorine targets for May-Oct 3.7 mg/L and Nov-Apr 4.0 mg/L changed from 4.3 mg/L Dosed filtered water free chlorine upper action limit for May-Oct >4.2 mg/L and Nov-Apr >4.5 mg/L changed from 4.7 mg/L. No change to lower action limit. Dosed filtered water free chlorine upper action limit reduced from >4.9 mg/L to >4.7 mg/L. No change to lower critical limit. Treated water free chlorine target decreased from 3.3 mg/L to 2.7 mg/L (agreed with Urban) Treated water free chlorine action limits decreased from <2.5 or >3.6 mg/L to <1.5 or >3.2 mg/L Treated water free chlorine upper critical limit decrease from >3.8 mg/L to >3.5 mg/L. No change to lower critical limit. | Refer markups REX D21/35630 | TF | 2021-03-04 | Y
420 | GDE-00054 | Boonah-Kalbar WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
421 | GDE-00055 | Maroon Dam WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
422 | GDE-00059 | Beaudesert WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
423 | GDE-00255 | Canungra WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
424 | GDE-00057 | Kooralbyn WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
425 | GDE-00067 | Molendinar WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
426 | GDE-00068 | Mudgeeraba WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
427 | GDE-00069 | Hinze Dam WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
428 | GDE-00056 | Moogerah Dam WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
429 | GDE-00058 | Rathdowney WTP | Verification Sample Point Guide | Sample point codes | Updated with new Sample Point codes | n/a | KL | 2021-06-29 | Y
Submission to Regulator - DWQMP Annual Report 2021
430 | PRO-02028 | Mudgeeraba WTP | HACCP Plan Wall Chart Procedure | Coagulation Mn & Fe Control Disinfection (primary) Fluoride | • Removal of minimum requirement for Supervisor to be notified immediately each time HACCP action limit is reached. This is now, at a minimum, to be reported in Action Limit register by end of next business day. WTP Operator can still notify Supervisor based on Operator assessment at the time as with all things operational issues. • Coagulation CCP: [no coag dose for >5mins] changed to [alum dose rate <20 L/hr for >5 mins] to remove ambiguity and allow for easy verification of Wall Chart against SCADA. SCADA already reflects this. • Manganese and Iron Control CCP: Removed the requirement to shutdown the WTP on high or low free chlorine. No changes to the requirement to notify, report, take corrective action etc as currently required. • Disinfection (primary) CCP: lower free chlorine dosed filtered water and treated water action limits and critical limits [increased by 0.1 mg/L] based on updated max WTP flow rate up to 95 ML/d and max treated water flow outlet Res 2 of 105 ML/d (max flow rate based on D21/51866 Mudgeeraba WTP High Flow Test Report & capacity stated in I&S daily sitrep) • Fluoride CCP: lower action limit timeframe increased from [60 mins] to [4 hours] based on 24/7 operation of WTP at request from Operation to reduce operational burden of dial out alarms out of hours. As per TMO. Dosed filtered water high fluoride critical limit timeframe reduced from [15 mins] to [2 mins] based on updated WTP flow rate up to 95 ML/d. • Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment, Addition of ‘alarm’ and ‘interlock’ terminology to applicable action and critical limits. | Refer markups REX D21/120519 | TF | 2021-07-23 | Y
431 | PLN-00071 | Mudgeeraba WTP | HACCP Plan | 1.2 2.1.1 2.1.2 2.1.3 2.1.4 3.2 4.2 6 8 | • 1.2 Conditions of Operation: max WTP flow rate up to 95 ML/d and max treated water flow outlet Res 2 of 105 ML/d. Updated alarm description. Removal of annunciator panel. • 2.1.1 HACCP team: updates to staff position titles as per DWQMP • 2.1.2 HACCP diagrams: Updates to flow diagram including oPRPs as per Risk Assessment, addition of raw water supply customers off raw water mains. Updates to schematic diagram as per markups from site walk through verification in Risk Assessment. Added additional aerial photograph showing BoHT and intakes. • 2.1.3 System overview: addition of HBT assessment, various updates to descriptions. Updates to C.t calc based on updated flow rate. • 2.1.4 Operational Challenges: updates based on recent improvements • 3.2 System validation: updates to HACCP values based on above. Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment. • 4.2 PRPs: alignment of oPRPs to reflect HACCP risk assessment. • 6 Materials and Chemicals: LT-22 removed (audit finding) • 8 Reporting: updates to team description and reporting timeframes | Refer markups REX D21/120518 | TF | 2021-07-23 | Y
432 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | Coagulation | • Coagulation CCP: alkalinity testing requirements changed from each raw water main to coagulated water as this is the point in the process where the alkalinity result triggers a change in lime dose rate, in addition to treated water alkalinity. Treated water colour test changed from true to apparent which is current practice and a more sensitive measurement (i.e unfiltered). • Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment. • Nomenclature updates | Refer markups REX D21/120520 | TF | 2021-07-23 | Y
433 | PLN-00073 | Hinze Dam WTP | HACCP Plan | 2.1.3 system overview | 2.1.3 System overview: updated to incorporate the information in Appendix 3 of D20/210002 that all plants don’t service more than 5000 people at any 1 point in time and therefore trigger additional microbial monitoring due to the network size. | Refer markups REX D21/131900 | TF | 2021-07-29 | Y
434 | PLN-00100 | Maroon Dam WTP | HACCP Plan | 2.1.3 system overview | 2.1.3 System overview: updated to incorporate the information in Appendix 3 of D20/210002 that all plants don’t service more than 5000 people at any 1 point in time and therefore trigger additional microbial monitoring due to the network size. | Refer markups REX D21/131905 | TF | 2021-07-29 | Y
435 | PLN-00107 | Moogerah Dam WTP | HACCP Plan | 2.1.3 system overview | 2.1.3 System overview: updated to incorporate the information in Appendix 3 of D20/210002 that all plants don’t service more than 5000 people at any 1 point in time and therefore trigger additional microbial monitoring due to the network size. | Refer markups REX D21/131912 | TF | 2021-07-29 | Y
436 | PLN-00094 | Rathdowney WTP | HACCP Plan | Materials and Chemicals | 6. Materials and Chemicals: changed from AN905 to LT20 as part of MoC 1520 | MoC 1520 | TF | 2021-07-29 | Y
437 | PLN-00069 | Molendinar WTP | HACCP Plan | 2.1.1 2.1.2 2.1.3 4.2 8 | • 2.1.1 HACCP team: updates to staff position titles as per DWQMP • 2.1.2 HACCP diagrams: Updates to flow diagram including oPRPs as per Risk Assessment, updates to schematic diagram as per markups from site walk through verification in Risk Assessment. Added additional aerial photograph showing BoHT and intake. • 2.1.3 System overview: addition of HBT assessment, various updates to descriptions. • 2.1.3 System validation: updates to HACCP values based on above. Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment. • 4.2 PRPs: alignment of oPRPs to reflect HACCP risk assessment. • 8 Reporting: updates to team description and reporting timeframes • Outdated references added as per feedback from Cam and yourself. | Refer markups REX D21/131858 | TF | 2021-08-04 | Y
438 | PRO-01984 | Molendinar WTP | HACCP Plan Wall Chart Procedure | Raw Water Abstraction Coaulgation Disinfection (primary) | • Removal of minimum requirement for Supervisor to be notified immediately each time HACCP action limit is reached. This is now, at a minimum, to be reported in Action Limit register by end of next business day. WTP Operator can still notify Supervisor based on Operator assessment at the time as with all things operational issues. • Raw Water Abstraction oPRP: raw water manganese (sol) action limit increased from 0.05 mg/L as per SPE-00320 up to 0.1 mg/L based on this WTP maintaining pre-filter chlorine dosing consistently year round maintaining the manganese dioxide layer. Raw water sol Mn 95th%ile based on 10 years of verification data was 0.1 mg/L and Mn shown to be easily removed based on past performance and data • Coagulation CCP: [no coag dose for >5mins] changed to [alum dose rate > ±25% of calculated setpoint for 2 minutes] to remove ambiguity, allow for exact verification of Wall Chart against current SCADA. • Disinfection (primary) CCP: upper free chlorine action limit decreased from 3.0 mg/L to 2.5 mg/L to align with current (and future) Bulk Water Supply Agreement. Note this is as per TMU. No change to target. Treated water pH target increased from >7.1 to 7.3 to ensure consistency of meeting current (and future) Bulk Water Supply Agreement. Can review this one again down the track based on how we are tracking against future BWSA reporting. Acknowledge WTP is currently targeting treated water pH 7.25. • Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment • removal of CCP/QCP/oPRP column as per HACCP wall chart as part of region wide ‘harmonisation’ • Addition of ‘alarm’ and ‘interlock’ terminology to applicable action and critical limits as per HACCP wall chart as part of all regions harmonisation approach | Refer markups REX D21/131859 | TF | 2021-08-04 | Y
439 | PLN-00070 | Molendinar WTP | Operational Monitoring Plan | Coagulation General | • Coagulation CCP: alkalinity testing requirements changed from each raw water main to coagulated water as this is the point in the process where alkalinity result triggers an operational change in lime dose rate, in addition to treated water alkalinity. Treated water colour test changed from true to apparent which is current practice and a more sensitive measurement (i.e unfiltered). • Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment. • Nomenclature updates | Refer markups REX D21/131863 | TF | 2021-08-04 | Y
440 | PRO-02003 | Boonah-Kalbar WTP | HACCP Plan Wall Chart Procedure | Mn and Fe Control UV Disinfection General | • Removal of minimum requirement for Supervisor to be notified immediately each time HACCP action limit is reached – updated table at end of doc to add minimum requirement to report in Action Limit Register in PDL by end next business day. WTP Operator can still notify Supervisor based on Operator assessment at the time as with all things operational issues (also communicated HACCP team meeting 21/07/2021) • Manganese and Iron Control CCP: removal of combined filtered water low critical limit for pH <6.0. Does not represent immediate water quality risk requiring process interlock as pre SPE-00320. Low pH indicating alum overdose (or caustic underdose) captured at Coagulation CCP. Combined filtered water low pH action limit with dial out alarm and associated corrective actions unchanged. Similarly combined filtered water high pH critical limit with process interlock pH >7.5 unchanged. • UV Disinfection CCP: UV Dose Low major alarm delay aligned with SPE-00320 and documented 5 mins. • Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment • removal of CCP/QCP/oPRP column as per HACCP wall chart as part of region wide ‘harmonisation’ • Addition of ‘alarm’ and ‘interlock’ terminology to applicable action and critical limits as per HACCP wall chart as part of all regions harmonisation approach | Refer markups REX D21/131821 | TF | 2021-08-09 | Y
441 | PLN-00138 | Boonah-Kalbar WTP | HACCP Plan | 2.1.1 2.1.2 2.1.3 3.2 4.2 | • 2.1.1 HACCP team: updates to staff position titles as per DWQMP • 2.1.2 HACCP diagrams: Updates to flow diagram including oPRPs as per Risk Assessment, updates to schematic diagram as per audit finding from site walk through. Added additional aerial photograph showing intake. • 2.1.3 System overview: addition of HBT assessment, various updates to descriptions. • 3.2 System validation: updates to HACCP values based on above. Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment. • 4.2 PRPs: alignment of oPRPs to reflect HACCP risk assessment. | Refer markups REX D21/131820 | TF | 2021-08-09 | Y
442 | PLN-00119 | Boonah-Kalbar WTP | Operational Monitoring Plan | General | • No changes to what/when/where • Alignment of CCPs/QCPs/oPRPs to reflect HACCP risk assessment. • Nomenclature updates | Refer markups REX D21/131818 | TF | 2021-08-09 | Y
443 | PRO-02028 | Mudgeeraba WTP | HACCP Plan Wall Chart Procedure | General | T&O control from QCP to oPRP and Mn removal from CCP to QCP as per risk assessment Media Filtration: note removed that 5 filters will dial out if offline as this has been changed to in control system such that single filter will dial out if offline Disinfection (primary): all tanks grouped under CCT preface Table: Definition of controls and reporting updated to reflect changes to action limit reporting | Refer markups REX D21/131754 | TF | 2021-08-12 | Y
444 | PLN-00071 | Mudgeeraba WTP | HACCP Plan | 2.1.2 2.1.3 3.1 3.2 4.2 6 | Associated documents: list updated to remove outdated references and addition of reporting procedures and PDL link 2.1.2 Flow Diagram: HACCP process flow diagram updated to change T&O control from QCP to oPRP and Mn removal from CCP to QCP as per risk assessment. Does not require re-verification by operations as no changes to inputs/outputs. 2.1.3: updated to include interlock functionality description as per Wall Chart 3.1, 3.2: updated to change T&O control from QCP to oPRP and Mn removal from CCP to QCP as per risk assessment. 4.2 PRPs: T&O control added to oPRP table 6 material and chemicals: aligned chemical names to REG-00250 | Refer markups REX D21/131747 | TF | 2021-08-12 | Y
445 | PLN-00072 | Mudgeeraba WTP | Operational Monitoring Plan | General | updated to change T&O control from QCP to oPRP and Mn removal from CCP to QCP as per risk assessment. | Refer markups REX D21/131752 | TF | 2021-08-12 | Y
446 | PLN-00100 | Maroon Dam WTP | HACCP Plan | 2.1.1 2.1.2 2.1.3 2.1.4 3.2 4.2 Appendix A | • 2.1.1 HACCP team: updates to staff position titles as per DWQMP • 2.1.2 HACCP diagrams: Updates to schematic diagram as per audit findings. Added additional aerial photograph showing intake. HACCP flow diagram requires re-verification and dating. • 2.1.3 System overview: addition of HBT assessment, various updates to descriptions. • 2.1.4 Operational challenges: updated to reflect upgrades to distribution system however noted that As-Constructed drawings of the entire distribution system were not able to be located at the time of this revision and not known to exist. • 3.2 System validation: updates to HACCP values based on above. • 4.2 PRPs: updated oPRP table. • Appendix A Maroon Dam WTP distribution system: updated with mark-ups from project 2019. Noted that As-Constructed drawings of entire distribution system were not able to be located at the time of this revision and not known to exist. | n/a | TF | 2021-09-13 | Y
447 | PLN-00101 | Maroon Dam WTP | Operational Monitoring Plan | General | • Removal of flow(s) and level(s) monitoring which do not have HACCP limits associated with them • Minor formatting updates | n/a | TF | 2021-09-13 | Y
448 | PRO-02054 | Maroon Dam WTP | HACCP Plan Wall Chart Procedure | Coagulation CCP Disinfectin (primary) CCP General | • Removal of minimum requirement for Supervisor to be notified immediately each time HACCP action limit is reached; updated reporting table at end of doc. • Coagulation CCP: removed ‘no alum dose for 5 mins’ as the high pH critical limit covers this scenario (audit finding). This will change again when the alum flow monitoring project is successfully commissioned and the low alum flow limit can be determined. • Disinfection (primary) CCP: reduced treated water turbidity target from ‘<1.0 NTU’ to ‘<0.5 NTU’ which is representative an increase above normal levels that should be investigated to prevent impacts to free chlorine disinfection efficacy; reduced treated water turbidity action limit and timeframe (alarm) from ‘<1.0 NTU for 4 hours’ to ‘>0.5 NTU for 30 mins’ based on reasonable timeframe that Operator should become aware of an increase/change in turbidity. Action limit aligns with TBK. • Addition of ‘alarm’ and ‘interlock’ terminology to assist in verification process of wall chart with scada page. • Removal of monitoring plan reference column | n/a | TF | 2021-09-13 | Y
449 | PLN-00095 | Kooralbyn WTP | HACCP Plan | 2.1.1 2.1.2 2.1.3 3.2 4.2 | • 2.1.1 HACCP team: updates to staff position titles as per DWQMP • 2.1.2 HACCP diagrams: Updates to schematic diagram as per audit findings. Updated aerial photographs. HACCP flow diagram requires re-verification and dating. • 2.1.3 System overview: addition of HBT assessment, various updates to descriptions. • 3.2 System validation: updates to HACCP values based on above. • 4.2 PRPs: updated oPRP table. | n/a | TF | 2021-09-15 | Y
450 | PLN-00096 | Kooralbyn WTP | Operational Monitoring Plan | Raw water abstraction T&O control | • Added in raw water ammonia monitoring to reflect current practice • Added in Taste & Odour control added as per TBE which has mobile PAC trailer • Minor formatting updates | n/a | TF | 2021-09-15 | Y
451 | PRO-02110 | Kooralbyn WTP | HACCP Plan Wall Chart Procedure | Raw Water Abstraction oPRP T&O control oPRP Coagulation CCP Disinfection (primary) CCP Fluoridation CCP | • Removal of minimum requirement for Supervisor to be notified immediately each time HACCP action limit is reached; updated reporting table at end of doc. • Raw Water Abstraction oPRP: added raw water ammonia target and action limit. Limit based on approx. 10 x 0.3 mg/L requiring 3.0 mg/L chlorine dose which is a point that will start to significantly impact disinfection (if not already picked up by the dosed filtered water free chlorine analyser). • Taste & Odour control oPRP: added as per TBE which has mobile PAC trailer • Coagulation CCP: amended ‘no alum dose for 5 mins’ to ‘alum dose rate >20% discrepancy from setpoint for 5 mins’ to remove ambiguity and allow for verification of wall chart with scada. • Disinfection (primary) CCP: change low CCT level timeframe from ‘anytime’ to ‘5 mins’ to remove ambiguity and allow for verification of wall chart with scada. • Fluoridation CCP: dosed filtered water fluoride timeframe reduced from ’15 mins’ to ‘2 mins’ based on current practice on site and request by Ops to have a conservative timeframe to minimise impacts to treated water. | n/a | TF | 2021-09-15 | Y
452 | PLN-00107 | Moogerah Dam WTP | HACCP Plan | 2.1.1 2.1.2 2.1.3 2.1.4 3.2 4.2 Appendix A | • 2.1.1 HACCP team: updates to staff position titles as per DWQMP • 2.1.2 HACCP diagrams: Updates to schematic diagram as per audit findings. Added additional aerial photograph showing intake. HACCP flow diagram requires re-verification and dating. • 2.1.3 System overview: addition of HBT assessment, various updates to descriptions. • 2.1.4 Operational challenges: updated to reflect upgrades to distribution system however noted that As-Constructed drawings of the entire distribution system were not able to be located at the time of this revision and not known to exist. • 3.2 System validation: updates to HACCP values based on above. • 4.2 PRPs: updated oPRP table. • Appendix A Moogerah Dam WTP distribution system: updated with mark-ups from project 2019. Noted that As-Constructed drawings of entire distribution system were not able to be located at the time of this revision and not known to exist. | n/a | TF | 2021-09-15 | Y
453 | PRO-01929 | Moogerah Dam WTP | HACCP Plan Wall Chart Procedure | Disinfection (primary) CCP Distribution pipeline oPRP General | • Removal of minimum requirement for Supervisor to be notified immediately each time HACCP action limit is reached; updated reporting table at end of doc. Coagulation CCP: removed ‘no alum dose for 5 mins’ as the high pH critical limit covers this scenario (audit finding). This will change again when the alum flow monitoring project is successfully commissioned. • Disinfection (primary) CCP: dosed filtered water target range increased from ‘2.0 mg/L’ to ‘2.5-3.5mg/L’ based on plant data; treated water free chlorine target increased from ‘>1.5 mg/L’ to ‘2.0 mg/L’ based on plant data; reduced dosed filtered water pH lower critical limit from ‘<6.5 to ‘<6.3’ based on alum dose requirements for this WTP and upper coag pH target and absence of pH correction to increase pH at Disinfection (primary) CCP; : reduced treated water turbidity target from ‘<1.0 NTU’ to ‘<0.5 NTU’ which is representative an increase above normal levels that should be investigated to prevent impacts to free chlorine disinfection efficacy; reduced treated water turbidity action limit and timeframe (alarm) from ‘<1.0 NTU for 4 hours’ to ‘>0.5 NTU for 30 mins’ based on reasonable timeframe that Operator should become aware of an increase/change in turbidity (action limit aligns with TBK); CCT low level critical limit timeframe increased from 5 mins to 15 mins based on time to overcome trend glitch following power interruption. • Distribution Pipeline oPRP: reticulated water turbidity target and action limit reduced from ‘5NTU’ down to ‘1NTU based of upgraded system and actual and expected turbidity in distribution system. • Addition of ‘alarm’ and ‘interlock’ terminology to assist in verification process of wall chart with scada page. | n/a | TF | 2021-09-15 | Y
454 | PLN-00108 | Moogerah Dam WTP | Operational Monitoring Plan | General | • Minor formatting updates | n/a | TF | 2021-09-15 | Y
455 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | n/a | Veolia/EH | 2019-10-02 | Y
456 | PRO-02115 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Disinfection (secondary) CCP | Changed AL to > 0.3 NTU for 15 minutes. Corrective actions to include check of the CCT |  | AC | 2021-10-28 | Y
457 | REF-00490 | Gold Coast Desalination Plant | HACCP Corrective Actions | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 4255 | Veolia/EH | 2019-12-18 | Y
458 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 7202 | Veolia/EH | 2020-03-19 | Y
459 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 7202 | Veolia/EH | 2020-05-13 | Y
460 | REF-00309 | Gold Coast Desalination Plant | HACCP Validation Plan | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: MAN 9394 | Veolia/EH | 2020-08-03 | Y
461 | REF-00462 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated & mitigated) | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: WIS 9395 | Veolia/EH | 2020-09-21 | Y
462 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 7202 | Veolia/EH | 2020-10-06 | Y
463 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 7202 | Veolia/EH | 2021-02-15 | Y
464 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: MAN 9393 | Veolia/EH | 2021-05-20 | Y
465 | REF-00309 | Gold Coast Desalination Plant | HACCP Validation Plan | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: MAN 9394 | Veolia/EH | 2021-05-20 | Y
466 | REF-00490 | Gold Coast Desalination Plant | HACCP Corrective Actions | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 4255 | Veolia/EH | 2021-06-09 | Y
467 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 7202 | Veolia/EH | 2021-08-12 | Y
468 | REF-00306 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: MAN 9393 | Veolia/EH | 2021-08-20 | Y
469 | REF-00459 | Gold Coast Desalination Plant | Operational Monitoring Plan and Relevant Criteria | Refer Veolia doc management system | Refer Veolia doc management system | Veolia BMS number: TEM 7202 | Veolia/EH | 2021-10-05 | Y
470 | PRO-02099 | North Stradbroke Island Town WTPs | HACCP Plan Wall Chart Procedure | Disinfection CCP | Updated pH stablisation limits for Amity Point and Point Lookout WTPs after adjustments to limestone bed to improve CCPP. Updated Supernatant Return Turbidity Limits to reflect system capability consistency with manufacturer's validation for UV system (on supernatant return line) |  | DH | 2022-02-21 | Y
471 | PRO-02115 | Beaudesert WTP | HACCP Plan Wall Chart Procedure | Disinfection CCP | The new limits: • Increase of target limits of dosed irradiated water (inlet to CCT) free chlorine target range from 3.0 - 3.2 mg/L to 3.3 - 3.8 mg/L • The lower free chlorine residual Action Limits for dosed irradiated water from <2.0 mg/L to <2.8 mg/L • The upper free chlorine Action Limits for dosed irradiated water and breakpoint water from 3.5 mg/L to 4.2 mg/L • Dosed irradiated water free chlorine residual from <1.5 mg/L to <2.5 mg/L • The upper critical limit from >4.0 mg/L to >4.5 mg/L • Action limits Reservoir Feed turbidity from >0.5 NTU for 30 minute to > 0.3 NTU > 5 minutes | ION 2057 | AC | 2022-02-24 | Y
472 | PLN-00091 | Beaudesert WTP | HACCP Plan | 3.2 HACCP Limit Validation | Review of 3.2 HACCP Limit Validation section Disinfection (primary) (CCP) NORMAL MODE to reflect changes made to the HACCP wallchart on 10/1/2022. The new limits have been applied and validated during operations. • Increase of target limits of dosed irradiated water (inlet to CCT) free chlorine target range from 3.0 - 3.2 mg/L to 3.3 - 3.8 mg/L • The lower free chlorine residual Action Limits for dosed irradiated water from <2.0 mg/L to <2.8 mg/L • The upper free chlorine Action Limits for dosed irradiated water and breakpoint water from 3.5 mg/L to 4.2 mg/L • Dosed irradiated water free chlorine residual from <1.5 mg/L to <2.5 mg/L • The upper critical limit from >4.0 mg/L to >4.5 mg/L • Action limits Reservoir Feed turbidity from >0.5 NTU for 30 minute to > 0.3 NTU > 5 minutes | ION 2057 | AC | 2022-02-24 | Y
473 | PRO-01768 | Rathdowney WTP | HACCP Plan Wall Chart Procedure | Raw water abstraction flocculation and settling | • Raw water abstraction is now oPRP • UV 254 is now included into AL corrective action in Raw water abstraction; settled water and treated water limits have been set • Flocculation and settling is oPRP • Reporting requirements have been updated | n/a | AC | 2022-04-22 | Y
474 | PLN-00093 | Rathdowney WTP | Operational Monitoring Plan | Raw water abstraction Review of parameter | • Raw water abstraction is now oPRP • UV 254 added to raw, settled and treated water • Delete Flow signal for flow paced 589 dosing and disinfection chlorine dosing (agreed with ops that it’s not part of the operational monitoring plan as it’s not in the PDL) • Filter Head Loss (Continuous Monitoring of Filter performance) • Added UVT in Filtration process • Disinfection: removal of valve position (Verify that unchlorinated filtered water sent to backwash water tank is not entering treated water tank) and Treated Water Pump Flow (Continuous monitoring of Contact Time for Disinfection CCP) | n/a | AC | 2022-04-22 | Y
475 | PRO-02110 | Kooralbyn WTP | HACCP Plan Wall Chart Procedure | Raw water abstraction flocculation and settling | • Raw water abstraction is now oPRP • Flocculation and settling is oPRP • Reporting requirements have been updated |  | AC | 2022-04-29 | Y
Submission to Regulator - July 2022

## DWQMP & Spt Programs
DWQMP and supporting programs change register
# | Document Ref | Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | WSR Amendment Required (by Principal PQ)
1 | D15/6241 | oPRP Table | N/A | A table documenting Seqwater's operational pre-requisite programs (oPRP) has been compiled and is used for updating HACCP plans and procedures, and risk registers. | The oPRPs listsed in this table are referenced as appropriate/ applicable in every HACCP plan and risk assessment register as they are updated. | D Healy | 2015-01-14 | N
2 | Seqwater Intranet | Seqwater Strategic Plan(2015-2020) | Appendix 1.2 | The strategic plan is subject to regular review/rewritten in line with changes in senior management |  | Seqwater Corporate | 2015
3 | Seqwater Intranet | Organisational Structure with Names | Appendix 1.4 | Seqwater's organisational structure is subject to regular change. These organisational charts are maintain on a fortnightly basis and reflects those in high duties. The organisational chart is available to all employees through Seqwater's intranet. |  | Seqwater Corporate | Updated fortnightly
4 | PRO-00656, FRM-00027, and Seqwater Intranet | Water Quality Notification Procedure (PRO-00656) and Water Quality Notification Form (FRM-00027) | Appendices 4.2 and 4.3 | Whilst the form remains extant, the form is now available to operators in an Adbobe PDf format with drop down boxes to assist operator completing the form. |  | D Healy | 2015-04-23
5 | D15/129027 | Certificate of Registration - Queensland~ety management System compliant... | Appendix 11.3 | The scope of Seqwater's ISO 22000 accrediation is currently being widened with new plants added to the current scope every six months until certification includes Seqwater's 12 largest operations and the supply system. Accordingly, the certificate is reissued every six months. |  | D Healy | 2015-06-15
6 | D15/198762 | Improvement Plan | Appendix 12.1 | An updated version of the DWQ (risk) improvement plan is an enclosure to this annual report. The improvement plan is subject to regular review and updates through risk assessment reviews and audits. |  | D Healy | Ongoing updates
7 | ERP-00001 | SE QLD Water Grid Emergency Response Plan | Appendix 6.1 | The ERP for the SE Queensland Water Grid is reviewed and updated every 2 years. This review involves all the water grid entities and the final document is subject to ministerial approval. | The next review will occur in 2017. | J Boldeman | 2015-10-31
8 | PLN-00004 | Drinking Water Quality Management Plan (DWQMP) | All sections and appendices | DWQMP revised following the DWQMP Review. Refer to D16/75162 DWQMP Review Report 30 June 2016 for detailed changes including a copy of the DWQMP with tracked changes shown. | The next review will occur in 2018. | D Healy | 2016-08-10
9 | PRO-00707 | Drinking Water Quality - Incident Reporting to WSR Procedure | N/A | Procedure revised to reflect changes at WSR and to reference Seqwater's approved DWQMP |  | D Healy | 2016-08-10
10 | PRO-01455 | Tankering of Drinking Water Supplies Procedure | N/A | Procedures revised in accordance with current operational practices for monitoring deliveries and to reflect the findings from an ICAM investigation (e.g. site access control and security) |  | D Healy | 2016-08-10
11 | PRO-01560 | Tools and Equipment Disinfection Procedure | N/A | New procedure |  | D Healy | 2016-08-10
12 | PRO-01869 | Disinfection of Pumps and Hoses Procedure | N/A | New procedure |  | D Healy | 2016-08-10
13 | PRO-01554 | Disinfection of Water Mains Procedure | N/A | New procedure |  | D Healy | 2016-08-10
14 | PRO-02019 | Disinfection of Small Reservoirs in Free Chlorine Systems Procedure (AWWA C652-11 Method 1) | N/A | New procedure |  | D Healy | 2016-08-10
15 | PRO-01559 | Disinfection of Bulk Water Supply Reservoirs Procedure (AWWA C652-11 Method 2) | N/A | New procedure |  | D Healy | 2016-08-10
16 | PRO-01870 | Underwater Inspections in Drinking Water Assets Procedure | N/A | New procedure |  | D Healy | 2016-08-10
Submission to Regulator - Ammendment Application August 2016
17 | PLN-00004 | Drinking Water Quality Management Plan (DWQMP) | N/A | Removal of Borumba WTP from scope of the DWQMP. | This WTP has been deregistered/decommissioned. | D Healy | 2017-09-13
18 | REG-00775 | Corporate HACCP - Register Prerequisite Programs (PRPs) | all sections | Description of PRPs and associated hazard analysis |  | A Clement | 2018-08-02
19 | PLN-00004 | Drinking Water Quality Management Plan (DWQMP) | N/A | Refer track changes submission to WSR |  | D Healy | 2018-08-08
Submission to Regulator - Ammendment Application August 2018
20 | PRO-02120 | Corporate HACCP - Procedure Management of WQ Online Instruments | all sections | improvement to describe the process flow and roles and responsibilities | Relates to PRP- 5 Management of water quality online instruments | A Clement | 2019-09-20 | N
21 | PRO-00656 | Operations- Procedure Water Quality Notification | all sections | improvement to describe the process flow and change of reporting requirements of limit exceedances using Risk Wizard instead of completing FRM 00027- internal stakeholders |  | A Clement | 2019-09-20
22 | PRO-01146 | WTP- Procedure Drinking Water Quality Notification and Reporting | all sections | improvement to describe the process flow and change of reporting requirements to internal and external stakeholders |  | A Clement | 2019-09-20
23 | PRO-02120 | PRP-5 Management of Water quality online instruments | Reporting and supernatant return limit | 6.1.2 Calibration Processs: Reporting requirements for instrument techs to use hard copies on site Added: Supernatant turbidity > 10 NTU/ Acceptable limits / Maximum Allowable Offset Values +/- 10% |  | A Clement | 2020-03-16
24 | PRO-02120 | PRP-5 Management of Water quality online instruments | Whole Document | 1.) 6. Procedure Addition of: The CIS Workorder Process is used to ensure timely compliance as detailed in Table 1 Planning schedules and frequencies. The stated frequencies are the minimum required. 2.) Table 1. Planning schedules and frequencies • Addition of time based/ scheduled calibration process to describe the Fluoride analyser calibration process better • Deleting supply system weekly verification process • Deleting supply system monthly calibration process (not practiced). The process is aligned to the verification process where calibration is performed on a required basis. 3.) Appendix 1 - Online Instrument Acceptable limits and Maximum Offset Values • Inclusion of Free ammonia, total ammonia and monochloramine limits in the disinfection/ distribution process step 4.) Appendix 4 - Record keeping Addition of: • F16/3981/001 Online Analyser Manuals • FRM-01111 Corporate HACCP - Online Instrument - Aspley WQMF - North… • FRM-01112 Corporate HACCP - Online Instrument - Aspley WQMF - South… 5.) Appendix 5 - List of approved online instruments • Hach 5500sc Ammonia/Monochloramine • Deleting the S:CAN reference 6.) Appendix 6 - List of approved bench-top laboratory instruments (for verification) • Addition of Hach TU5200 |  | A Clement | 2020-05-18
25 | PRO-02120 | PRP-5 Management of Water quality online instruments | 6 | including the maintenance of wet racks including calibration of fluoride online instruments conducted by trained operators |  | A Clement | 2020-06-23
26 | PRO-01146 | Drinking Water Quality Notification and Reporting Process | all sections | Minor chnages to terminology e.g. Change Distribution Retail Authority to Water Service Provider |  | C Veal | 2020-08-07
27 | PLN-00351 | Drinking Water Quality External Monitoring Program Methodology Justification | all sections | Update distribution list. Minor terminology changes. Update Introduction. Include Qld Health requirements as an input to parmeter identification step and update reference to PHR to PHR 2018 sections. Minor updates to passive sampler descriptions. Update Cyanobacteria Management Plan references. Add further description about Supply System assets. |  | C Veal | 2020-08-07
28 | PRO-00933 | Linkages between the DWQMP and the ERP | all sections | Minor updates to reflect organisational re-organisation. |  | C Veal | 2020-08-07
29 | PRO-00707 | Drinking Water Quality – Incident Reporting to WSR | all sections | Update refernce to PHR 2018. Update to relect organsiation re-organisation and current terminology e.g. water service provider. Clearly define what type of incident uses the two different WSR notification forms. Include new section 5.3 to provide guidance on type of informatoin Regulator is likely to ask for with initial notification. Update to reflect current approvals and responsibilities. Remove outdated flow diagrams for incident reporting to regulator. Updated contact details during incidents (Appendix A). Added appendix form to record inforamtion that is likely to be requested by regulator (Appendix B) |  | C Veal | 2020-08-07
30 | SPE-00320 | Validation Plan | all sections | New section: membrane filtration New section: secondary disinfection - rechlorination Water treatment plant process combination and broad catchment classification updated all other process steps reviewed and updated as per current requirements CCPs, QCPs and oPRPs defined |  | D Middleton/ B Hester/ E Harding/ C Veal | 2020-08-07
31 | PLN-00004 | Drinking Water Quality Management Plan (DWQMP) | all sections | Two yearly full review. Refer track changes REX D20/145531 |  | D Middleton/ C Veal | 2020-08-07 | Y
Submission to Regulator - Ammendment Application August 2020
32 | REG-00775 | Corporate HACCP - Register Prerequisite Programs (PRPs) | Reference | Define 2 new PRPs: PRP-8 Management of cybersecurity-Technology security PRP-9 Training for internal and external interested parties |  | A Clement | 2020-07-27
33 | PRO-00707 | Drinking Water Quality - Incident Reportin to WSR Procedure | Section 5.1 and Appendix 2 | Section 5.1 updated to include information from 8 December 2020 Regulator Symposium around "event's" and "detections with no ADWG value" only being notifiable if there is believed to be risk to public health. Updated contact details in Appendix 2 of Symbio on-call, Sunshince Coast PHU and Metro South PHU |  | D Middleton | 2021-01-28
34 | PRO-02120 | PRP-5 Management of Water quality online instruments | S 6 Appendix 4 Appendix 5 | Related changes are: • Inclusion of sample water return process • Orp analyser • Layout change of appendix 5 to include reference to FRM-00713 |  | A Clement | 2021-03-23
35 | PRO-02120 | PRP-5 Management of Water quality online instruments |  | Including references around the 'Isolation and Reinstatement of Sample Return Systems PRO-02516' and trainings requirements |  | A Clement | 2021-04-01
Submission to Regulator - DWQMP Annual Report 2021
36 | REG-00775 | Corporate HACCP - Register Prerequisite Programs (PRPs) | Reference | Review of: PRP 1 Source water Management- complete revamp PRP 2 Pest Management- addition of reference to Flick portal PRP- 3 Management of sanitary integrity- addition to reference to ROV innovations portal PRP- 4 Bulk chemicals supply control including product selection delivery and storage- revised monitoring procedures and documented information PRP-10 Food defence, biovigilance, and bio terrorism - inclusion/ definition of PRP into the program |  | A Clement | 2021-07-23 | Y
37 | PRO-01551 | Corporate - Inspection program for treated water reservoirs | All | Complete revision to reflect current practices including UAV and ROV inspections |  | A Clement | 2022-04-14 | Y
38 | PRO-01650 | Corporate - Tools & Equipment Disinfection Procedure | All (including Appendix) | Updated procedure to remove use of Milton Disinfection tablets and replace with Milton disinfection solution |  | D Healy | 2022-06-07 | Y
Submission to Regulator - July 2022

## Suggested changes register (hidden)
Operator Feedback - Register of feedback and suggested changes to HACCP plans, procedures or related documents
# | Document Reference Number (if known) | WTP/System Name | HACCP Plan/Procedure Title | Section/Para | Brief description and justification of change | Additional Comments | Your name / Point of Contact | Date | Your DWQ Coord's name | Response by DWQ Coordinator (by Principal DWQ)