## DWQIP
SITE | REGION | # | ISSUE | DESCRIPTION | ORIGIN OF IMPROVEMENT | SIGNIFICANT RISK | SIGNIFICANT RISK LEVEL | RESPONSIBLE | DUE FOR COMPLETION | STATUS | RISK TREATMENT COMMENTS | DATE RAISED | DATE CLOSED | LIMITING HAZARD
Supply System (All) | Central | 9461 | Supply System - Disinfection (secondary) - Incorrect chlorine dose Under dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water. Medium (8). | Redlands Supply Zone - Investigation of having duplicate single instruments for Heinemann Road Reservoirs 1, 2 3. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-02-15 09:00 | Completed | Refer to ION 01629 for further information on this improvement. | 2019-04-24 09:00 |  | Bacteria
Supply System (All) | Central | 9462 | Supply System - Disinfection (secondary) - Incorrect ammonia dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water Medium (5) - EPI Medium (8) - NPI Medium (5) - SRP | 1). Online ammonia instruments to be installed and commissioned at Chambers Flat and Caloundra Street WQMFs. 2). Install Chemscan analyser at Gramzow Road WQMF. 3). Conduct Process Assessment of chambers Flat WQMF dosing systems. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 09:00 | In progress | 1). Instruments have been installed at Caloundra Street WQMF and Chamber Flat WQMF. Still not operable as yet. 2). Refer to ION 01633 for information on Gramzow Road WQMF Chemscan | 2019-04-24 09:00 |  | Bacteria
Mt Crosby Eastbank WTP | Central | 9464 | Eastbank WTP - Raw Water Abstraction - Change in Raw Water Source Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. Medium (8). | 1). Undertake HBT Assessment for this site. Completed. Refer Rex D19/46266 Eastbank WTP - HBT Assessment 2017-18 - HBT Assessment Report July 2017 - June 2018. 2) Long term planning is underway for this WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2028-12-29 09:00 | In progress | 1). QMRA Mid Brisbane River study is currently underway. 2). Mid Brisbane River Water Supply Strategy Review is currently underway. Findings from this study will help inform long term planning requirements for Mt Crosby Eastbank and Westbank WTPs. Integrated Asset Management Plans - Mt Crosby to be completed by Oct 2022. | 2019-04-24 09:00 |  | Protozoa
Mt Crosby Eastbank WTP | Central | 9470 | Eastbank WTP - Coagulation - Flash mixer failure. Ineffective coagulation, flocculation and sedimentation, filter breakthrough and out of specification treated water. Medium (8). | 1). Installation of jet flash mixers for Sedimentation Basins No. 3 and 4. RTP ID 70 - Captured in the Facility Risk Review for Central - Sitting with ASP | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-12-29 09:00 | In progress | Refer to ION 01639 for further information. | 2019-04-24 09:00 |  | Protozoa
Mt Crosby Westbank WTP | Central | 9506 | Westbank WTP - Raw Water Abstraction - Change in raw water source Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. Medium (8). | 1). Undertake HBT Assessment for this site; 2). Long term planning is underway for this WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2028-12-29 09:00 | In progress | 1). QMRA Mid Brisbane River study is currently underway. 2). Mid Brisbane River Water Supply Strategy Review is currently underway. Findings from this study will help inform long term planning requirements for Mt Crosby Eastbank and Westbank WTPs. Integrated Asset Management Plans - Mt Crosby to be completed by Oct 2022. | 2019-04-24 09:00 |  | Protozoa
Mt Crosby Westbank WTP | Central | 9507 | Westbank WTP - Disinfection (primary) - Contamination of service water distribution system due to main break or backflow incident. Potential contamination of treated water. Medium (8). | Conduct audit of the the service water to ensure that there are adequate measures in place to stop backflow events. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-12-29 09:00 | In progress | Audit completed. Recommendations to be delivered. Refer to ION 01642 for further information. | 2019-04-24 09:00 |  | Bacteria
Mt Crosby Westbank WTP | Central | 9508 | Westbank WTP - Whole of System - Failure or incorrect operation of a bypass valve. Leading to out of specification treated water. Medium (8). | Consider reviewing lockout arrangements so that these bypass valves cannot be accidentally opened, prior to them being blanked off - Plates welded over spindles - | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-12-29 09:00 | Completed | Refer to ION 01643 for further information. After further investigation, it has been identified that there are no bypasses at West Bank WTP. Item closed. | 2019-04-24 09:00 | 2023-03-24 11:11 | All unmitigated hazards
Mt Crosby Westbank WTP | Central | 9509 | Westbank WTP - Whole of System - Contamination due to backflow Service water backflow prevention inadequate leading to out of specification treated water. Medium (8). | Full audit needs to be undertaken on backflow prevention at Westbank. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-12-29 09:00 | In progress | Audit has been completed. Findings yet to be delivered. Refer to ION 01642 for further information. | 2019-04-24 09:00 |  | Protozoa
Wivenhoe WTP | Central | 9512 | Wivenhoe dam WTP- Media Filtration - Filter breakthrough. Leading to out of specification treated water. Medium (8). | "Package plant to replace the existing plant between the raw water tanks and the clear water storage. Expected to be completed Dec 2018. Consideration should be given to ascertaining if it would be practical to install a first filtered water to waste system and undertake necessary works if this idea was deemed to be advantageous. Any upgrade of the control system associated with this WTP should retain interlocks that will automatically shut down the relevant parts of the WTP in the advent of a critical limit being triggered (i.e., filtered water turbidity)." | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-01-31 09:00 | In progress | Package plant to be commissioned January 2021. Update 27/1/2021: Delay in delivery: design agreement is at 30%. November 2021: Data logger for filtered water turbidity has been installed. | 2019-04-24 09:00 |  | Protozoa
North Stradbroke Island WTP | South | 9562 | TNS-RW-A-6562 Risk Treatment: Undertake upgrades to Coagulation CCP. | TNS - Coagulation - Incorrect lime dose/ Incorrect Coagulant dose. For Herring Lagoon (pre lime): Underdose of lime into raw water main leading to: - low alkalinity for coagulation - incorrect dosed water pH Overdose of lime into raw water main leading to: - incorrect dosed water pH Medium (8). (NSI-8 NSI-13) Risk Treatment (raised R.A review 2015 and DWQ Report to WTP Planning 2015 D14/149372): It is recommended that the coagulation process at NSI WTP is upgraded. This upgrade should consider: - paging of dosed water pH alarms to the Operator (Complete 2017) - interlock of WTP operation to dosed water pH alarms. This must include a full WTP HAZOP to ensure that all actions required to facilitate the interlock are identified and actioned, such that other unintentional adverse consequences are avoided (Complete Sep 2018) - feed forward control of coagulant dose - single set of alum dosing pumps (automatic changeover ‘duty’/’standby’ arrangement) that are capable of delivering the required dose across the range of flow and alum doses expected - flow meters on the alum dosing line, interlocked to WTP operation, such that the detection of no alum flow will shutdown the WTP - flow pacing of the alum dose to raw water flow meters on the inlet to each DAF train or installation of appropriate control such that the flow to the DAF basins is equal or known - relocation of the alum dosing points to immediately upstream of the inline rapid mixers | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | Update R.A 2017: 1) Operations South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included improvements to Lime System. Project cancelled Oct 2017. Project to be restarted. Update R.A 2018: 1) Interlocks programed Sep 2018 - Complete 2) APMP 2019 doc includes TNS: MCS Renewal: TNS: MCS Preliminary design for 20/21 and 21/22 3) APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Update 12/03/2020: timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 Update 12/03/2020: timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 | 2015-01-28 09:00 |  | Protozoa
North Stradbroke Island WTP | South | 9565 | TNS-RW-A-9565 Risk Treatment: Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF (oPRP). Under no circumstances would these bypasses be operated. | TNS - Dissolved Air Flotation (DAF) - Failure or incorrect operation of a bypass valve. Failure or incorrect operation of bypass from flash mixer to settled water main, or Failure or incorrect operation of bypass from supernatant return line to settled water main". Medium (8). (TNS-24) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | Update R.A 2018: Raised RR workshop 2018. Update 25/03/2020: ION raised (ION01324): Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF oPRP). Under no circumstances would these bypasses be operated. | 2017-11-20 09:00 |  | Protozoa
North Stradbroke Island WTP | South | 10182 | TNS-RW-A-10182 Risk Treatment: Improvements to dosing, monitoring and alarming relating to poly system. Current impact of failure is minimal under normal conditions however when required, if poly dosing fails, subsequent processes are likely to fail. Improvements required. | TNS - Coagulation - Incorrect coagulant aid dose. For Herring Lagoon: Overdose of AN905 into inlet flocculation tank leading to ineffective coagulation or acrylamide > ADWG OR Underdose of AN905 into inlet flocculation tank leading to ineffective coagulation Medium (8). (TNS-21) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | Update R.A 2018: APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Timelines under review. Update 11/03/2020: APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 | 2017-11-20 09:00 |  | Protozoa
Capalaba WTP | South | 10261 | TCP-RW-A-10261 Risk Treatment: Box gutter roof on Reservoir 1 roof subject to intrusion. | TCP - Disinfection (primary) - Contamination by animals - Contamination of chemical dosing chamber and/or treated water tanks Medium (8) (TCP-27) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-11-30 09:00 |  | Box gutter roof on Reservoir 1 roof subject to intrusion. Refer recommended improvements to Reservoir Condition Assessment Capalaba Reservoir 1 and Reservoir 2 2017 (GHD) Update R.A 2019: Southern Maintenance team in delivery of vermin proofing items Refer D21/83417 Capalaba WTP Facility Risk Register. Tracked in D22/48823 Southern Risk Forum: APMP 20200429 - Reservoir 1 Roof Renewal DG 28062023: due date extended as this work is associated with a res roof replacement that is scheduled to be delivered in September 2024. | 2017-08-15 09:00 |  | Viruses
Molendinar WTP | South | 10321 | TMO-RW-A-10321 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. | TMO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMO-17) Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatment capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update October 2019: Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81738 Molendinar WTP - HBT Assessment 2018/19 - Draft Report. Note this does not incorporate review of source water category. Rex Ref. D19/81738. Update 21/07/2020: Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled for August 2020 Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. | 2017-11-03 09:00 |  | Protozoa
Molendinar WTP | South | 10339 | TMO-RW-A-10339 Risk Treatment: WTP shutdown takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Under high flow conditions this is not insignificant. Review and optimise interlock sequencing. Develop recovery plans where required if impacts to CCPs during high flow conditions require recovery. | TMO - Whole of System - Loss of control system. Loss of SCADA system or loss of PLC leading to impacts to treated water quality Medium (8) Risk Treatment (raised R.A 2017): Raw water pump shut down takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Review and optimise interlock sequencing. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update R.A 2019: WTP shutdown takes 20 mins because raw water valve takes 20 mins to close due to functionality set. This improvement may not be possible until new valve installed. Update R.A 2021: Being actioned under Risk Wizard incident 26864 HACCP critical limit exceedance no coag flow. HACCP crash stop is 12 mins. | 2017-11-03 09:00 |  | Protozoa
Beaudesert WTP | South | 10351 | TBE-RW-A-10351 Risk Treatment: Tag out bypass to ensure clear identification of valve and prevent accidental use. | TBE - Flocculation and Settling - Failure or incorrect operation of a bypass valve Failure or incorrect operation of a clarifier bypass valve. Medium (5) (TBE-19) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | In progress | Update R.A 2020: increased to Risk Treatment due to relocation of alum dosing after the aerator this bypass is now a raw water to filtered water bypass which is an unacceptable risk. Remove bypass pipework to create air gap. Currently two closed valves in place. Check if maintenance can remove section of pipework between valves as interim until blanking plates can be installed via ION process. 29/9/2022 update: We have an alum dosing point into the aerator to allow for operational flexibility including direct filtration. Consideration of removing the bypass is given as soon as SW pipeline is completed. | 2017-06-07 09:00 |  | Protozoa
Hinze Dam WTP | South | 10397 | THZ-RW-A 10397 Risk Treatment: Although this is not known to have occurred at Hinze Dam WTP there is occurrences of coag dosing pipe breakages at other WTPs. There is currently a coagulant flow switch interlocked to WTP operation however coag flow monitoring interlocked to WTP operation is required. | THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water Medium (8) (HNZ-5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | Update R.A review 2017: Confirmed as viable WTP and will continue operating. Project will be pursued by Process Improvement Specialists based on current understanding that WTP will remain for the foreseeable future. To be included in Minor Works upgrade 17/18. Note Control System is very limited in terms of adding any further alarms or monitoring. Sludge upgrade project would trigger upgrade of PLC. Update R.A review 2019: Not delivered at time of R.A. Update 9/07/2021: Sen. DWQ Advisor Sth: wait for outcome of Moogerah and Maroon Dam coag flow meter projects. Similar flow rate and project currently in delivery. Issues with measuring such low flow rate may or may not be overcome. Update 21/09/2021: Senior DWQ Advisor Continuous Improvement to escalate ION184 or raise a new ION to install ACH coag flow meter. In the short term identify options to get existing signals available on the ACH dose pump into SCADA that can be used as the HACCP critical limit to interlock the WTP. Update Hinze Dam WTP HACCP Wall Chart and HACCP Plan Validation 3.2 to document signal in use for this HACCP critical limit. Update 29 NOV 21: Date extended 12 months as this work has not yet included in any program. Management of this risk to be reviewed on-site and then discussed at next HACCP team meeting (Mar 22). Due date extended 12 months to allow for changes in DWQ advisor staff (new and acting arrangements). Will be reassigned once DWQ advisor south position is stable. | 2015-03-23 09:00 |  | Protozoa
Hinze Dam WTP | South | 10398 | THZ-RW-A-10398 Improvement Opportunity: Static mixer post ACH dose point would improve coagulation and clarifier performance. | THZ - Coagulation - Inadequate mixing Lack of mixing resulting in poor floc formation resulting in filter breakthrough Medium (5) (HNZ4) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-12-31 09:00 | In progress | Update R.A review 2017: Confirmed as viable WTP and will continue operating. Project will be pursued by Process Improvement Specialists based on current understanding that WTP will remain for the foreseeable future. To be included in Minor Works upgrade 17/18. Process Engineers to perform assessment of ACH mixing at Hinze Dam WTP due to lack of static mixer or mechanical flocculator to ensure mixing of coagulant (batched with water) is sufficient. Note Control System is very limited in terms of adding any further alarms or monitoring. Sludge upgrade project would trigger upgrade of PLC. Update R.A review 2019: refer APMP 2020. | 2015-03-23 09:00 |  | Protozoa
Moogerah WTP | South | 10411 | TMG-RW-A 10411 Risk Treatment: HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP requires additional protozoa removal (i.e UV). | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Deterioration of Granular Activated Carbon (GAC) media resulting in inadequate removal of TO (primarily) and organics and manganese (secondary) due to: exceed GAC lifespan Medium (8) (TMG-15) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-28 09:00 | In progress | Update R.A 2020: Conservative assessment at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP will require additional protozoa treatment (i.e UV). Update 2020: ION01470 raised for the installation of UV | 2017-09-06 09:00 |  | Protozoa
Moogerah WTP | South | 10412 | TMG-RW-A 10412 Risk Treatment: install alum flow monitoring. | Lack of alum flow monitoring is an unacceptable risk due to periods of low RW pH. Alum flow monitoring required (and injection point flow switch or meter if carrier water used) with interlocks to shutdown the WTP. Raw water pH 5th%iles are <7.5 pH which is s the validated SPV upper critical limit for dosed water pH using alum. Therefore during a rain event when RW pH is low (5% of the time) if alum dosing was lost this would not trigger the upper critical limit of pH 7.5. In the short term a low coagulated water pH limit will be used which should detect alum dosing failure in most circumstances. Alum pump fault alarms and lowering dosed water pH limit are interim measures TMG - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - high pH Medium (8) (MOO5) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | Update R.A 2017: Investigate installation of flow switch to detect loss of alum dose. Update R.A 2020: Business Case in development Update 2021: In delivery however flow meter found to not yet be reliable. If unreliable, keep the upper coagulated water pH critical limit as it currently is and continue to use it as an indication of loss of alum dose. Alum flow monitoring SCADA interlock all working well. HACCP documents are being updated in due course. | 2015-11-04 09:00 | 2023-01-30 15:00 | Protozoa
Moogerah WTP | South | 10413 | TMG-RW-A 10413: Risk Treatment: Investigate opportunities to address clarifier sludge build up requiring manual draining and hose out on a regular basis. | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-16) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | In progress | Update R.A 2020: P.E to investigate replacement or modification of clarifier. Reference P.E action item | 2017-09-06 09:00 |  | Protozoa
Kooralbyn WTP | South | 10446 | TKO-RW-A 10446 Risk Treatment: Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146. Additional protozoa treatment required i.e UV Disinfection | TKO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TKO-15) TKO - Coagulation - Incorrect coagulant dose Underdose of alum resulting in contaminated treated water including incorrect dosed water pH Medium (8) (TKO-15) TKO - Coagulation - Incorrect CO2 dose Underdose (absence) of CO2 causing high dosed water pH resulting in contamination of treated water Medium (8) (TKO-15) TKO - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) (TKO-15) TKO - Flocculation and Settling - Failure or incorrect operation of a bypass valve Failure or incorrect operation of a clarifier bypass valve Medium (8) (TKO-15) TKO - Media Filtration - Filter breakthrough Filter breakthrough Medium (8) (TKO-15) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2025-04-30 09:00 | In progress | Raised Kooralbyn WTP - pathogen treatment assessment report June 2015 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19. Update R.A 2020: PID02914 TKO: UV Disinfection Upgrade in APMP for delivery 21/22. Additional need to confirm if filters have individual or combined filter monitoring as this can drop the LRV. There are four cells and two filtered water turbidity instruments. Refer TKO-RW-A 11740 Risk Treatment: determine filtered water turbidity assessment for HBT assessment. E.g four filters or two filters. | 2017-07-19 09:00 |  | Protozoa
Maroon Dam WTP | South | 10460 | TMD-RW-A-10460 Improvement Opportunity: Recommend conditionally formatting plant data spreadsheet to prevent excursions being missed. | TMD - Coagulation - Incorrect coagulant dose Underdose of alum including inadequate mixing TMD - Coagulation - Incorrect coagulant dose Overdose of alum leading to ineffective coagulation affecting treated water quality TMD - Distribution Pipeline - Elevated water age Presence of pathogenic bacteria resulting from loss of secondary disinfection barrier Medium (5) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | Update R.A 2020: Plant Operations Data Management Solution (PODMS) project underway. 29/8/2022: Conditional formatting of excel spreadsheet is completed. | 2015-11-04 09:00 | 2022-08-29 08:29 | Protozoa
Maroon Dam WTP | South | 10461 | TMD-RW-A 10461 Risk Treatment: Install alum flow monitoring (and injection point flow switch or meter if carrier water used) with interlocks to shutdown the WTP. | TMD - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - low pH in raw water Medium (8) Risk Treatment: Lack of alum flow monitoring is an unacceptable risk due to periods of low RW pH. Alum flow monitoring required (and injection point flow switch or meter if carrier water used) with interlocks to shutdown the WTP. Raw water pH 5th%iles are <7.5 pH which is the validated SPV upper critical limit for dosed water pH using alum. Therefore during a rain event when RW pH is low (5% of the time) if alum dosing was lost this would not trigger the upper crtical limit of pH 7.5. In the short term a low dosed water pH limit will be used which should detect alum dosing failure in most circumstances. | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | Update R.A 2017: Investigate installation of flow switch to detect loss of alum dose. Update R.A 2020: Business case in development Update 2021: in delivery however alum flow meters are proving to be problematic. Recommend leaving coagulated water pH upper critical limit unchanged for the purposes of detecting loss or underdose of alum. In use 2023. | 2015-11-04 09:00 | 2023-02-21 13:06 | Protozoa
Maroon Dam WTP | South | 10462 | TMD-RW-A 10463 Risk Treatment: HBT Assessment required for this WTP. Conservative assessment made at time of R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP requires additional protozoa removal (i.e UV). | TMD - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMD-18) TMD - Coagulation - Incorrect coagulant dose Underdose of alum including inadequate mixing Medium (8) (TMD-18) TMD - Coagulation - Incorrect coagulant dose Overdose of alum leading to ineffective coagulation affecting treated water quality Medium (8) (TMD-18) TMD - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMD-18) TMD - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (5) (TMD-18) TMD - Media Filtration - Filter breakthrough Deterioration of Granular Activated Carbon (GAC) media resulting in inadequate removal of TO (primarily) and organics and manganese (secondary) due to: - exceed GAC lifespan Medium (5) (TMD-18) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | In progress | Update R.A 2020: ION raised for UV installation (ION01469). | 2017-09-06 09:00 |  | Protozoa
Maroon Dam WTP | South | 10463 | TMD-RW-A 10463 Risk Treatment: Clarifier autodesludge on start up would be an operational improvement for this site. | TMD - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMD-19) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | In progress | Update R.A 2020: P.E to raise ION Update 02/03/2020: ION01262 raised for TMG- Auto de-sludge via pump or de-sludge valve. | 2017-09-06 09:00 |  | Protozoa
Mudgeeraba WTP | South | 10476 | TMU-RW-A-10476 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. | Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatement capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. TMU - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water (HUI LND) Medium (8) (TMU-29) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81746 Mudgeeraba WTP - HBT Assessment 2018 - Draft Report. Note this does not incorporate review of source water category. Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. | 2017-10-27 09:00 |  | Protozoa
Mudgeeraba WTP | South | 10485 | TMU-RW-A-10485 Risk Treatment: Undertake improvements to improve filter performance for filters which don't consistently achieve protozoa LRV log reduction credits due to filter ripening spikes. | Risk Treatment (Raised HACCP internal audit 2014): Review of filtration performance at Mudgeeraba WTP to identify inadequacies to Planning. Following the filter optimisation project the individual filtered data will need to be assessed. If operational changes do not improve filter performance then capital improvements such as addressing the filter to waste restriction or an additional process step (eg UV) should be considered as log removal credits under the Health Based Targets standard cannot be applied based on the current HACCP limits. TMU - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) when required Medium (5) (MUD-22) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update R.A 2017: Further quantitative assessment in Pathogen Treatment Assessment for Mudgeeraba WTP performed June 2015 (D15/116852) confirmed filters don't meet performance expectations on ripening and overall don't meet the HBT filter performance targets for 3.0 log protozoa reduction. Process Engineering team are preparing to trial an extended terminal sub-fluidisation wash (ETSFW) sequence in the filters to determine whether this improves the ripening issues. D17/120476 Mudgeeraba (TMU) Long Term Planning Report has also captured that for individual filters, ripening times are a significant performance issue. Update R.A 2019: HBT assessment done for filter performance from Jan to Dec 2018 at 1 min interval as part of process improvement project 2018/19. Months where filters didn’t achieve the LRV was mainly due to incidents related to filter ripening spikes post backwash. ETSW implementation project is underway which will help prevent ripening spikes. Months where filter didn't reach 3.5 or 4.0 log it was due to filter ripening. Update R.A 2021: ETSW implementation ongoing | 2017-10-27 09:00 |  | Protozoa
Mudgeeraba WTP | South | 10486 | TMU-RW-A-10486 Improvement Opportunity: Develop filter performance reports using continuous online data against the HBT criteria to assist in informing WTP Planning. | Improvement Opportunity (raised R.A review 2017): Develop filter performance reports using continuous online data against the HBT criteria to assist in informing WTP Planning Long Term Planning Report. TMU - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) when required Medium (5) (TMU-36) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update R.A 2019: As part of this FY projects, the PE team is engaged in Central Historian eDNA project trails, where HBT reporting and WTP process performance reporting will be trialled. The filter performance will be included along with other processes within the WTP reporting. Update October 2019: PE has undergone a HBT assessment currently in Draft form. Rex Ref. D19/81746. A. HBT assessment done for filter (ONLY) performance from Jan to Dec 2018 at 1 min interval as part of process improvement project 2018/19. Months where filters didn’t achieve the LRV was mainly due to incidents related to filter ripening spikes post backwash. ETSW implementation project (similar to Molendinar) is underway which will help prevent ripening spikes. B. As part of this FY projects, the PE team is engaged in Central Historian eDNA project trails, where HBT reporting and WTP process performance reporting will be trialled. The filter performance will be included along with other processes within the WTP reporting. Update 2021: Project ongoing. Planned for next financial year. | 2017-10-27 09:00 |  | Protozoa
Rathdowney WTP | South | 10499 | TRA-RW-A 10499 Risk Treatment: Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Refer D15/114408. | TRA - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) TRA - Supernatant Return - Superntatnt return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose Medium (8) TRA - Coagulation - Incorrect coagulant dose Underdose of ACH (dosed neat) including loss of carrier water Or Ineffective coagulation due to elevated pH High (12) TRA - Coagulation - Incorrect coagulant dose Overdose of ACH (dosed neat) Medium (8) TRA - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) TRA - Media Filtration - Filter breakthrough Fitler breakthrough Medium (8) TRA - Media Filtration - Build up of solids leading to elevated turbidity High turbidity filtered water from backwash water tank used to backwash filter leading to filter breakthrough when filter back online Medium (8) | Risk Assessment | High | 12 | DWQ Advisor - Continuous Improvement | 2024-03-31 09:00 | In progress | Refer D15/114408. Project to commence 17/18. Refer APMP 2017 capital planning register. Update R.A 2020: PID02915 TRA: UV Disinfection Upgrade in APMP for delivery 21/22. PLEASE DO NOT CLOSE THIS ACTION UNTIL IMPROVEMENT HAS BEEN DELIVERED ON SITE. Update 2022 RA: UV is in delivery program. | 2017-10-27 09:00 |  | Protozoa
Rathdowney WTP | South | 10500 | TRA-RW-A 10500 Risk Treatment: Supernatant return flow rate maximum is designed to be controlled by SCADA to not exceed 10% of raw water flow. At the time of conducting the R.A review the automation was not enabled and supernatant return flow rate was manually throttled by Operators. Observation is that automation works when WTP running at 5L/s but struggles at current rate of 4 L/s. Process Engineer to investigate improvements to automation control. | In addition a return rate of <5 % of the raw water flow is recommended by the AWWA, Water Treatment Alliance and the WaterRA report 1079 Good Practice Guide to the Operation of Drinking Water Supply Systems for the Management of Microbial Risk 2015. Opportunities to meet this requirement using current assets should be investigated with a view to making recommendations for future upgrades if required to meet this target. TRA - Supernatant Return - Supernatant return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose Medium (8) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2022-10-31 09:00 | Completed | Update R.A 2020: Rate of return control Opportunities to meet this requirement using current assets should be investigated with a view to making recommendations for future upgrades if required to meet this target currently not being progressed on PE program. Seqwater currently putting together BC to progress a research project with WaterRA and other utilities to investigate and make recommendations on the 10% supernatant return rule (hyperlink below). https://www.waterra.com.au/research/current-opportunities/2019/investigating-supernatant-return-management-practices-in-drinking-water-treatment/ Update RA 2022'Comments: The supernatant return process is well controlled and no issues relating return rate or turbidity are apparent. In case of new developments or knowledge regarding return rate or similar this process will be reassessed. There is awareness around protozoan lg removal shortage which results in upcoming plant upgrades (UV). | 2017-03-01 09:00 | 2022-09-27 11:37 | Protozoa
Heinemann Road Reservoir Complex 2&3 | Central | 11134 | Heinemann Road Reservoirs - Add new additional chlorine instruments to individual reservoir outlets 2 and 3. | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-07-30 09:00 | In progress | Now Part of the Facility Risk Review process. RTP205. This action is to remain open until the RTP is closed for tracking purposes as this improvement is now flagged in the Supply System HACCP Risk Assessment. | 2019-12-19 00:46 |  | Bacteria
Heinemann Road Reservoir Complex 2&3 | Central | 11201 | Heinemann Road Reservoirs - Locate drawings of the chemical dosing arrangement, the sample return water or instrument water draw arrangements in Reservoirs 2 & 3. If they are not available,new drawings need to be done. | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-03-31 09:00 |  | ION1382 raised to address unavailability of drawing - not in their scope - Regional Ops Manager approved altering ER7 to address PID This action is to remain open until completed as it is being used for tracking purposes as this improvement is now flagged in the Supply System HACCP Risk Assessment. | 2020-01-09 09:00 |  | Bacteria
Heinemann Road Reservoir Complex 2&3 | Central | 11202 | Heinemann Road Reservoirs - Locate documentation detailing chlorine dosing control in Reservoirs 2 & 3. If documentation can not be located, new documentation is to be developed. | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-08-30 09:00 | Completed | ION1382 raised to address unavailability of drawing - This action is to remain open until completed as it is being used for tracking purposes as this improvement is now flagged in the Supply System HACCP Risk Assessment. | 2020-01-09 09:00 |  | Bacteria
Hinze Dam WTP | South | 11264 | THZ-RW-A 11264 Risk Treatment: Reduce frequency of Hinze distribution system pipework breaks/leaks. | Risk Treatment (raised R.A review 2019): Reduce frequency of Hinze distribution system pipework breaks/leaks. ION raised. THZ - Distribution Pipeline - Contamination due to pipe break Ingress of contaminants into reticulation system affecting treated water quality Medium (8) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | ION raised. Update 21/07/2020: Hinze Dam Potable Reticulated Water Supply Network replacement project has commenced to BC development Extended 12 months to allow for changes in DWQ advisor staff (new and acting arrangements). Will be reassigned once DWQ advisor south position is stable. | 2017-06-22 09:00 |  | Bacteria
Amity Point WTP | South | 11280 | TAP-RW-A-11280 Risk Treatment: Introduce protozoa treatment at Amity Point WTP to meet Category 2 minimum pathogen log reduction requirements. | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk Medium (8) Target risk (5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | In progress | Raised R.A 2017: Undertake Pathogen Assessment of NSI Township WTPs and review of preventative measures and monitoring for managing risk of abstraction of contamination groundwater is required including condition of bore casings, bore location in relation to flood level, condition of seals on above ground assets. Update R.A 2019: Based on having a shallow aquifer and, other than the Seqwater bores, having no control over the confines of the aquifer there has to be an assumed level of interaction whether it be continuous or intermittent. Therefore Amity Point WTP has been assessed as Source Category 2 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 3.0 LRV; protozoa 2.5 LRV under WSAA HBT Manual. Refer Risk Treatment Disinfection (primary) for improvements to C.t (TAP-RW-A-TBC) Protozoa treatment required in the form of UV disinfection to achieve protozoa 2.5 LRV. Update 26/03/2020: Attached email with work order inspections checklists | 2017-11-21 09:00 |  | Protozoa
Amity Point WTP | South | 11281 | TAP-RW-11281 Risk Treatment: Update HACCP plan to include oPRP for monitoring Bore asset integrity. Current Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) includes steps 19-21 to check for leaks on pipeline assets which can be referenced. Install online raw water turbidity monitoring to detect bore integrity failure and prevent impacts to CCT from turbidity. | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk Medium (8) Target risk (5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | In progress | Raised R.A 2017: Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity (raised HACCP internal audit 2016) Upgrade R.A 2019: Ingress issued identified. ION 00237 raised. Identified Issues resolved Jan 2019 by Operations Maintenance team. Ongoing inspections of bores (and all WTP assets) to be included in CIS routine work orders. Inspection criteria to be specific as per reservoir inspections checklist. Progression of UV disinfection to treat for hazards is preferable to installing additional online monitoring as standard online monitoring techniques is unlikely to be sensitive enough to detect a surface hazard and ground water interaction. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Update 15/05/2020: ION01366 has been raised for installing on-line turbidity monitoring of the combined raw. No updates / not yet commenced - date extended to allow for annual review until completed or closed out/risk tolerated. Reassigned to new DWQ Advisor South - Dan Guinea | 2017-11-21 09:00 |  | Protozoa
Amity Point WTP | South | 11284 | TAP-RW-A-11284 Undertake Disinfection (primary) CCP C.t improvements to achieve minimum bacteria and virus log reduction requirements at Amity Point WTP point of supply. | Note: C.t calculation currently includes councils town reservoir located near Amity WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | In progress | Update R.A 2015: C.t is currently not met at the BSP. WTP Planning preparing a draft options assessment report. Update R.A 2017: Concept design complete to achieve C.t and BSP. Consultant engaged. Preliminary design complete. Update R.A 2019: Amity Point WTP has been assessed as Source Category 2 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 3.0 LRV under WSAA HBT Manual. Minimum C.t 8 mg.min/L required to achieve 3.0 LRV virus. PID01902 TAP: Upgrade CWS Tank Capacity - improve contact time and instrumentation for disinfection in delivery for 20/21 21/22. Ref APMP 2019. Update 26/03/2020: Amity Point C.t Options being reviewed. Stakeholder meeting 23/03/2020. Lead WTP Planning leading. Contact pipe expected to be installed as part of disinfection upgrade to be completed during 23/24 year. Reassigned to new DWQ Advisor south - Dan Guinea | 2017-11-21 09:00 |  | Viruses
Dunwich WTP | South | 11292 | TDU-RW-A 11292 Risk Treatment: Undertake Health Based Target assessment of NSI Township WTPs and upgrade WTPs accordingly. | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: Risk: Medium (8) Target Risk: Medium (5) - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | Undertake Pathogen Assessment of NSI Township WTPs and review of preventative measures and monitoring for managing risk of abstraction of contamination groundwater is required including condition of bore casings, bore location in relation to flood level, condition of seals on above ground assets Update R.A 2019: Based on having a shallow aquifer and essentially no control over the confines of the aquifer there is an assumed level of interaction whether it be continuous or intermittent. There is also point source hazards such as septic systems on Rainbow Cres. Therefore Dunwich WTP, when using Bore 1, 2, 4 is likely to be Source Category 3 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 4.0 LRV; protozoa 3.5 LRV under WSAA HBT Manual however this assessment has not formally been done. This would likely increase to Category 4 if Bore 3 were to be reinstated or based on other known point source risks such as septic system and cattle. Refer Risk Treatment Disinfection (primary) for improvements to C.t. Protozoa treatment required in the form of UV disinfection to achieve protozoa LRV. Update 26/03/2020: Pathogen log shortfalls being addressed under TDU – Dunwich WTP Secondary Disinfection Preliminary BC | 2017-11-21 09:00 |  | Protozoa
Dunwich WTP | South | 11293 | TDU-RW-A 11293 Risk Treatment: Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity to detect contamination of aquifer due to bore failure or other pathway. | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: Risk: Medium (8) Target Risk: Medium (5) - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | Raised R.A 2017: Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Upgrade R.A 2019: ION raised. Ingress issued fixed on production bores 2018/2019? Ongoing inspections to be addressed. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Period inspections of ingress Closed. Update 15/05/2020: ION01367 has been raised to install online raw water turbidity monitoring for the purpose of real time detection of contaminated ground water that exceeds treatment capacity. | 2017-11-21 09:00 |  | Protozoa
Dunwich WTP | South | 11296 | TDU-RW-A 11296 Risk Treatment: install solid adequate cover on top of media filter. | TDU - Media Filtration - Contamination by ingress Contamination of Media Filter Risk: Medium (8) Target Risk: Medium (5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress |  | 2019-08-07 09:00 |  | Viruses
Dunwich WTP | South | 11297 | TDU-RW-A-11297 Risk Treatment: Investigate options to meet C.t. Will need to liaise with Redlands due to 'change' that customers will receive in free chlorine levels. Options could include increasing min res level. If not able to be reasonably achieved operationally then issue to be handed over to Planning. | TDU - Disinfection (primary) - Insufficient C.t Insufficient C.t due to: - low chlorine - high pH due to incorrect Stabilisation pH control - insufficient contact time - high treated water turbidity Risk: Medium (8) Target Risk: Medium (5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | In progress | Update R.A 2019: WTP Planning developing Dunwich WTP Pathogen Contamination Mitigation Preliminary Business Case to address pathogen treatment requirements. Update 26/03/2020: Virus and bacteria log shortfalls being addressed under TDU – Dunwich WTP Secondary Disinfection Preliminary BC | 2015-12-02 09:00 |  | Viruses
Point Lookout WTP | South | 11308 | TPL-RW-A-11308 Risk Treatment: Remove CCT bypass | Risk Treatment (raised HACCP Team meeting 2016): Bypass is thought to exist on outlet of 45 kL tank bypassing treated water reservoir. Bypass existence and condition requires confirmation and, if confirmed, removal. Refer REX 724654 Drawing I-DWG-TPL-601 PID Treated Water Storage. TPL - Disinfection (primary) - Failure or incorrect operation of a bypass valve Failure or incorrect operation of treated water reservoir bypass (dosed water to balance tank to treated water pumps) Risk: Medium (8) Target Risk: Medium (5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2026-09-30 09:00 | In progress | Bypass exists on outlet of 45 kL tank bypassing treated water reservoir. Refer REX 724654 Drawing I-DWG-TPL-601 PID Treated Water Storage. Update R.A 2019: Bypass valve closed 2019. ION raised for valve and intermediate balance tank to be removed. ION00430 No further project work to date - due date extended for annual review until completed or risk tolerated/closed out. Reassigned to new DWQ Advisor South - Dan Guinea DG 28062023: Due date extended in response to resourcing. DG This improvement will take considerable work and is of low priority. DWQ will work to include with plant augmentation in medium term. | 2017-11-21 09:00 |  | Viruses
North Stradbroke Island WTP | South | 11389 | TNS-RW-A-11389 Risk Treatment: review anti syphon assets at NSI WTP. Are they effective to mitigate syphon risk. Refer alum dosing pump standard. | TNS - Coagulation - Incorrect Incorrect Coagulant dose. For Herring Lagoon: Overdose of alum leading to ineffective coagulation Medium (8) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2022-08-31 09:00 | Completed | Raised R.A review 2018. Process Engineering to confirm is a loading valve is installed - when pump is operational, then the loading valve is open (unseated under pressure), when the pump is not operational it will be closed and prevents siphoning. 26-08-2022 Confirmed with NSI Operators that a pressure loading valve is installed on the discharge of alum dosing pumps. | 2015-01-28 09:00 | 2022-08-26 16:41 | Protozoa
North Pine WTP | North | 11390 | TNP- Raw Water Abstraction- Cyanobacteria bloom For Lake Samsonvale; Blooms of cyanobacteria and other problem algae that could result in treated water contamination Low (2). | Risk Treatment (raised R.A 2020): long term planning to improve north pine PAC in APMP | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress |  | 2020-02-11 09:00 |  | Cyanotoxins
Noosa WTP | North | 11397 | TNO- Raw Water Abstraction- Rain event in catchment Contaminant load exceeds treatment capacity Medium (8). (due to crypto short fall) | Risk Treatment (raised R.A 2019): Online visibility at the Mary river and Lake Macdonald intakes is required to enable real time source selection. This could be achieved by using existing remote catchment monitoring devices currently stationed at Coles Crossing(Mary River Intake) and Lake Macdonald, which monitor turbidity, pH conductivity, temperature and dissolved oxygen. Alternatively analyser racks could be installed at both of these intakes. Either option must have the signals from these analysers fed back to SCADA. Long term planning should be looking to add another cryptosporidium barrier such as UV in order to meet the required log credits under the HBT assessment. Update 2021 RA: Long term planning should be looking to add another cryptosporidium barrier to meet the required log credits under the HBT assessment. - contunied development (2021 ra) (create new RW for higher priority) - roll into a tier 1.5 assessment /QMRA for noosa (done before next RA (so <2 years from july 2021) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2023-07-01 09:00 | Completed | closed out. moved to long term planning as noosa is up for rebuild. In addition, due to the update to the ADWG, the log shortfall is now only 1 LRV, which is still within the green zone on the continuum. | 2019-07-17 09:00 | 2023-06-09 10:13 | Protozoa
Noosa WTP | North | 11398 | TNO- Coagulation Incorrect lime dose Non-optimised coagulation Medium (8). (due to crypto short fall) | Risk Treatment (raised R.A 2019): investigate lime and alum control with focus on start up and lake only water investigate poly as a floc/settling aid install alum dosing flow meter to verify alum dose investigate CO2 dosing to enable formation of calcium carbonate to a higher degree of reliability includine reactivator importance in coag pH validation and control | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress |  | 2019-07-17 09:00 |  | Protozoa
Noosa WTP | North | 11401 | TNO- Media Filtration Filter breakthrough Potential contamination of treated water Medium (8). from crypto short fall | Risk Treatment (raised R.A 2019): Install appropriate instrumentation, monitoring and control systems to enable effective monitoring and control of filtration. Install /improve filter to waste option (2021: filter to waste operational on timers) Investigate poly dosing as a filter-aid. - potential to introduce air scour (2021: completed) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress | raised 2021: link to 11397 Long term planning should be looking to add another cryptosporidium barrier to meet the required log credits under the HBT assessment. - contunied development (2021 ra) (create new RW for higher priority) - roll into a tier 1.5 assessment /QMRA for noosa (done before next RA (so <2 years from july 2021) | 2019-07-17 09:00 |  | Protozoa
Amity Point WTP | South | 11604 | TAP-RW-A-11604 Improvement Opportunity: Introduce dynamic C.t monitoring in SCADA. | TAP - Disinfection (primary) - Insufficient C.t Insufficient C.t resulting from: - low chlorine - insufficient contact time - high pH due to dosed filtered water caustic overdose - high treated water turbidity Medium (5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | Not yet started | Process Engineering have a schedule for this work across the southern region completing three(+) WTPs per year. Date extended for annual review until completed. Reassigned to new DWQ advisor south - Daniel Guinea | 2019-06-03 09:00 |  | Viruses
Kooralbyn WTP | South | 11738 | TKO-RW-A 11738 Risk Treatment: introduce low raw water pH HACCP action limit to detect change in pH when on Bigfoot Lagoon which could indicate a change in source water conditions requiring a re-assessment of coagulation chemical dosing. | TKO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TKO-16) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-05-31 09:00 | Not yet started | Date extension due to caustic dosing installation. Monitoring of corrective actions will be undertaken once dosing is operational. | 2020-05-20 09:00 |  | Protozoa
Kooralbyn WTP | South | 11740 | TKO-RW-A 11740 Risk Treatment: determine filtered water turbidity assessment for HBT assessment. E.g four filters or two filters | TKO - Media Filtration- Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (8) (KOO13) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | Not yet started | Check with Process Engineering how HBT assessment has been undertaken. If two filters with filtered water turbidity monitoring on each filter then these are considered individually monitored filtered. If four filters with combined filtered water turbidity monitoring for two filters then these are considered combined monitoring. Check how Beaudesert and Capalaba WTP filters have been assessed under HBT framework as they are multi-celled filtered with single filtered water turbidity analyser. Update Kooralbyn HACCP plan and risk assessment with LRV for Media Filtration CCP accordingly. | 2020-05-20 09:00 |  | Protozoa
Image Flat WTP | North | 11747 | TIF - Raw Water Abstraction Rain event in catchment Increased contaminant loads due to wash-in from the catchments, resulting in contaminated treated water High (12). | Risk Treatment (raised R.A 2020): The plant is difficult to operate, thus the likelihood of failure is higher, leading to the higher risk score. Whilst historical data shows the operators have been able to run the plant effectively, there is grave concern about the ongoing operability of particularly the coagulation and filtration barriers. Therefore, an additional Prozoa Treatment barrier is required to address the shortfall against the HBT tier 1 assessment. All sources are HBT Category 4 and so source selection alone is not good enough to mitigate the shortfall. Consideration should be given to -> Quantitative/tier 2 HBT assessment -> real-time water quality and flow monitoring of raw water sources. This will give the operators the ability to chose the most treatable source and consequently mitigate the associated hazards. If the operators had the capacity to see the change in the river in real time, they could move to Wappa, which has some buffer from the rain, or Poona, if manganese and taste and odour are accounted for. -> Lime dosing system improvement to account for colour and alkalinity from the river and wappa ->Alum Mixing improvement | Risk Assessment | High | 12 | Senior DWQ Advisor - North | 2026-04-27 09:00 | In progress |  | 2020-04-27 09:00 |  | Protozoa
Image Flat WTP | North | 11748 | TIF - Raw Water Abstraction Change in raw water source Contaminant load exceeds treatment capacity (T&O) Medium (9). | Risk Treatment (raised R.A 2020): There is a risk around feed from Wappa Dam direct to plant due to issues with Mn. Valves are physically locked and require a manual changeover to access the Wappa source. Source selection procedures consider the level of all storages and consideration of depth samples on dams is taken into account to assess WQ in conjunction with catchments, intake weir and dams. Therefore, consideration to be given to taste and odour treatment improvements (there is an existing project in place to upgrade PAC dosing plant, but this will only assist in operatability and not in the reduction of TO) and manganese treatment options (there is a BC proposed for reinstating potperm dosing - however it is unlikely to go ahead due to budget constraints). Manganese treatment options would greatly improve the operatability of the plant as if manganese could be dealt with effectively during a TO bloom then the sources can be switched to deal with the manganese. This is currently unavailable and as such most of the time the all of sources cannot be treated effectively | Risk Assessment | Medium | 9 | Senior DWQ Advisor - North | 2026-04-27 09:00 | In progress |  | 2020-04-27 09:00 |  | Manganese
Ewen Maddock WTP | North | 11760 | TEM - Raw Water Abstraction Rain event in catchment Contaminant load exceeds treatment capacity Medium (8). | Risk Treatment (raised R.A 2020): 'Undertake HBT Tier 1.5 Assessment to confirm risk | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress |  | 2020-01-17 09:00 |  | Protozoa
Ewen Maddock WTP | North | 11762 | TEM - Coagulation Incorrect lime dose Coagulation process failure Medium (8). | Risk Treatment (raised R.A 2020): Review of pre lime dosing system to include the following: - Not use raw water as service water for pre-lime (still in use - because its prior to treatment) - Change lime makeup water to plant service water instead of raw water (still in use - because its prior to treatment) - Pressure switches on lime makeup water (Mike Burns to check) - Auto shutdown on lime system failure (In place - close out) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress |  | 2020-01-17 09:00 |  | Protozoa
Ewen Maddock WTP | North | 11763 | TEM - Supernatant Return Change in raw water source Contamination of treated water Medium (8). | Risk Treatment (raised R.A 2020): ' VSD for the separated water return pumps the return water tank | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress |  | 2020-01-17 09:00 |  | Manganese
Ewen Maddock WTP | North | 11764 | TEM -Supernatant Return Stormwater entering the process Contamination of treated water Medium (8). | Risk Treatment (raised R.A 2020): Online turbidity and pH instruments to be installed on supernatant return line | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress |  | 2020-01-17 09:00 |  | Protozoa
Ewen Maddock WTP | North | 11765 | TEM -Ozone (intermediate) Contamination incident - accidental/intentional Introduction of pathogens Medium (8). | Risk Treatment (raised R.A 2020): 'Erect contamination signage on/at the BAC filters. Work instructions for working over the BAC should also consider the risk of accidental contamination | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress |  | 2020-01-17 09:00 |  | Protozoa
Ewen Maddock WTP | North | 11766 | TEM -Ozone (intermediate) Contamination incident - accidental/intentional Introduction of pathogens Medium (8). | Risk Treatment (raised R.A 2020): Investigate further prevention of post barrier contamination to the top of the BAC filters (such as ingress, animals, etc). Covering BACs completely is challenging because of the residual ozone present in the atmosphere. Ozone is heavier than air and invisible to the eye. People and animals can become intoxicated quickly if there is too much ozone in the air. However, there is a potential for contamination of the water on top of the BAC filters (water that has just been ozonated). BAC filters do not provide any log reduction credits for protozoa and as such effectively, anything that contaminates the ozonated water prior to BAC filtration could potentially make its way through to the treated water and the public. There are no further barriers to protozoan. Chlorine disinfection does not get any impact on protozoan parasites. Therefore it is imperitive to - ensure there is no ingress points to the ozonated water prior to BAC and provide an additional treatment barrier for protozoa downstream of the BAC. (not in place yet. but speaking to extra protozoan barriers ala other protozoan limiting hazard risk treatments, as well as reducing the likelihood of introducing contamination to the BACs) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress |  | 2020-01-17 09:00 |  | Protozoa
Maroon Dam WTP | South | 11773 | TMD-RW-A 11773 Risk Treatment: Investigate causes and opportunities to prevent alum dosing system blockages. | TMD - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - low pH in raw water Medium (8) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | Not yet started | P.E investigating options to address mixing/blockage issue e.g swap out devices. Update 28/09/2020: PE unable to progress at this time. Operations are trialling a double contained tubing with an expected longer shelf life. | 2019-03-08 09:00 |  | Protozoa
Moogerah WTP | South | 11775 | TMG-RW-A-11775 Risk Treatment: Investigate causes and opportunities to prevent alum dosing system blockages. Refer HACCP Critical Limit excursion RW incident 6526. | TMG - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - high pH Medium (8) P.E investigating options to prevent blockages e.g earthing of static mixer. Operations supervisor to initiate 3 monthly work order for swap out/replacement of alum dosing line. | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | Update 28/09/2020: PE unable to progress at this time. Operations are trialing a double contained tubing with an expected longer shelf life. Alum dose flow monitoring is working well, SCADA interlock implemented on alum flow. All HACCP documents are to be undated after the HACCP risk assessment in mid-February. | 2020-02-28 09:00 | 2023-01-30 14:52 | Protozoa
Rathdowney WTP | South | 11777 | TRA-RW-A 11777 Risk Treatment: Undertake HBT performance assessment to determine log credits bacteria/virus through coag/floc/settling and filtration process steps following change from Magnasol 589 to ACH to confirm if 6 LRV for bacteria/virus is achieved. | D15/114408 Rathdowney WTP Pathogen Assessment did not assess performance data for bacteria/virus log credits. It was considered likely that filtration performance is sufficient at Rathdowney WTP to consistently achieve 1 log reduction for bacteria and viruses. However, due to the known floc carryover (poor settling) issues with the use of Magnasol 589 it is considered likely that no credit for settling would be achieved. Bacteria/Virus 6 LRV required: WTP process has capacity to achieve 0 log coag/floc settling, 1 log media filtration, 4 log disinfection primary (min C.t 15 mg.min/L based on pH >8). Total 5.0 LRV. 1 log bacteria/virus shortfall. ACH trial commenced 26/8/2019 and settled water turbidity has improved. Undertake performance assessment to determine log credits for protozoa and bacteria/virus through coag/floc/settling and filtration process steps. TRA - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-06-30 09:00 | Completed | Report on change from Magnasol to ACH in progress. To be completed along with process assessment to log credits by approx Dec 22. Update 29-06-2023: A complete HBT assessment has been conducted towards coagulation, filtration and disinfection processes for a 1 year period. Results of the assessment will be discussed with the DWQ team in early FY- 2023/24. | 2020-06-03 09:00 | 2023-06-29 09:05 | Protozoa
Mt Crosby Eastbank WTP | Central | 12001 | Eastbank WTP - Supernatant Return - Supernatant return quality exceeds treatment capacity. Supernatant return volumes exceed treatment capacity leading to Protozoa in the treated water. High (12) | 1). It should be determined if it would be advantageous to fit interlocks such that the supernatant pumps cannot run when the raw water pumps are offline or if the turbidity critical limit is triggered - Technical Specialist has identified that this would be advantageous. 2). Consideration should be given to undertaking a mass balance of polyacrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for acrylamide monomer in the treated water. 3). VSDs is to be installed on the supernatant return pumps which in conjunction with raw water flow meters will facilitate improved control to ensure that the supernatant to raw water ratio does not exceed 10% of the raw water flow rate. 4) Make modifications and improvements to the current supernatant return process to minimise the impact to stage 3 and 4 basins. | Risk Assessment | High | 12 | Senior DWQ Advisor - Continuous Improvement | 2025-12-26 09:00 | Not yet started | Refer to Eastbank Solids Handling Upgrade - CIS project code C201005427 for further information. | 2020-07-15 09:00 |  | Protozoa
Somerset WTP | Central | 12012 | Somerset WTP - flocculation and settling Inadequate mixing; Carry over of floc, sludge or algae in settled water; Build up of solids leading to elevated turbidity; Anoxic sludge Medium (5). | - Installation of an inline mixer d/s of alum dose point to improve mixing for coagulation - Improvement to flocculation zone/energy - Improvement to sludge withdrawal from clarifier, particularly flocculation zone (including automation of sludge withdrawal) - Improvements to variable intake to allow this to be operated - Addition of pre-filter chlorination for manganese removal (if variable intake modification does not see sufficient improvement in manganese levels) - EIC upgrade to improve visibility and automation. The upgrade will include level instruments, filter DP, valve automation, and better control of VSD raw water and filter feed pumps (allowing flow to be matched). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-09-30 09:00 | In progress | Coagulation-flocculation improvements have been completed by Process Engineering. Intake improvements (pump replacement has been completed. No further work proposed for valves etc. In-line mixer, EIC upgrades etc yet to be determined - date extended 12 months for future review. | 2019-07-16 09:00 |  | Protozoa
Supply System (All) | Central | 12031 | Supply System - Reservoir - Elevated water age. Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. Medium (8) | 1. Review options around performance (efficient mixing), replacement and installation of reservoir mixers in Supply System. 2. Investigate installation of mixer at Mt Cotton to assist with water age issues. Common Inlet/Outlet. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 09:00 | In progress | 1. Refer to ION 01413 for further information. The following RTPs are noted in the Supply System Facility Risk Review for Mixers: - Aspley Reservoir Mixers - RTP 28 - Wellers Hill Reservoir Mixers - RTP 124 - Alexandra Hills Reservoirs 1, 4, 5 Mixers - RTP 126 - Narangba Reservoir 2 Mixer - RTP 219 - Heinemann Road Reservoirs 2, 3 and Alexandra Hills Reservoirs 1, 3, 4, 5 Mixers - RTP 313 | 2020-07-17 09:00 |  | Bacteria
Supply System (All) | Central | 12033 | Supply System - Disinfection (secondary) - Incorrect chlorine dose Under dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water. High (12) | NPI Supply Zone 1. Conduct Process Assessment of Noosa Connection dosing system. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2025-07-01 09:00 | Not yet started |  | 2020-07-20 09:00 |  | Bacteria
Supply System (All) | Central | 12034 | Supply System - Disinfection (secondary) - Incorrect ammonia dose. Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water. Medium (8) | Brisbane Supply Zone - Implement recommendations from Mt Crosby ICAM investigation for ammonia failure. - Undertake a review in conjunction with relevant trades and WHS staff to determine if flushing of aqueous ammonia dosing lines is required to safely remove and inspect the injection spears; and if an annual inspection of the spears is the correct frequency. RW 12165. Completed - Modify all critical valves associated with the chemical dosing system, so that they can be locked to avoid accidental operation by Seqwater staff. RW 12166 Completed - Install isolation valves on suction side of all dosing pumps and install non-return valve on tank outlet. Note – this requires extensive planning and will be either delivered through the ammonia tank replacement project or operations-led project. Ensure valves can be locked out. RW 12167. This was review and found that an additional project would need to be done to incorporate this. - Temporarily commission the ChemScan analyser located in the Holts Hill laboratory that is currently plumbed into the Camerons Hill No. 1 treated water sample line. RW 12168 Completed - Permanently install and commission the above mentioned ChemScan analyser, and undertake the installation works and programming in a manner that will easily facilitate the installation of a second analyser. RW 12169 Completed - Advise the Project Owner for the Supply System WQMF ChemScan Analyser Project, to roll out the installation of these analysers in order of the highest to lowest risk Facility. Note Gramzow Rd deferred. RW 9462 Refer ION 01633. - Work with Asset Planning to ensure the Business Case for the replacement of the aqueous ammonia tank addresses some of the single points of failure of the ammonia system RW 12175 Completed - Review the efficacy of service water backflow arrangements from a process and public health perspective and ensure that compliance with all relevant Standards is met. RW 12176 Completed - Investigate the merits of modifying the chemical dosing lines at the injection spears to facilitate the flushing of chemical to a portable catch tank, rather than into the trunk mains. This will also facilitate the timely charging of these lines with chemical upon reinstatement. (this item has been incorporated into the THH static mixer project for both dosing lines also TEB hypo dosing line upgrade 5/05/2020). Note - Included in THH Static Mixer project scope. RW12177 Completed - Ensure that all flushing activities (including hypo) can be accurately quantified by having flushing water pass through the chemical flow meters. RW12178. WO A-0339930 raised for investigation action. On inspections of areas it was deemed that we would need a project to complete works as multiple pipe work modifications would need to be completed. - Ascertain if it would be beneficial to implement changes to the control system to facilitate the generation of alarms when unexpected rises in tank level are observed in a bulk chemical storage. Similarly, also considering including in the control system relevant trended calculations for secondary disinfection related parameters that will help better inform Operators and Process Staff. (it is likely to trigger false alarm on the existing tank, will implement the alarm to the tank being renewed within FY20/21 05/05/2020). Note – considered beneficial but unlikely to be incorporated into the Aqueous Ammonia Tank project. May have opportunity to include in secondary disinfection project. RW12179 Completed. - Implement a review of the mothballed anhydrous ammonia dosing plant and other redundant infrastructure associated with ammonia dosing at Holts Hill, to ascertain what infrastructure can be removed, without exposing Seqwater to an unacceptable level of risk. Note – considered beneficial but unlikely to be incorporated into the Aqueous Ammonia Tank project. May have opportunity to include in secondary disinfection project. RW12180 - Develop/review a flushing procedure that also includes flushing times, and references. RW12182 Completed - Implement a program of labelling works for all relevant assets associated with the chemical dosing system. Note – undertaken in line with audit recommendations. Further work being done by PID project (Richard Blackburn). RW12183 Completed - Update the existing East Bank WTP HACCP Wall Chart to include additional secondary disinfection parameters such as free chlorine, free ammonia [as N]and monochloramine [as Cl2]. RW12184 - Incorporate conditional formatting into PODMS to flag exceedances of HACCP limits for secondary disinfection parameters. RW12185 Completed - Modify the existing WTP and Supply System treated water total chlorine CCP corrective actions, to include the need to test for monochloramine [as Cl2] and free chlorine in the advent of action or critical limits being triggered. RW12186 - Develop a toolbox style presentation for all WTP and Supply System staff with respect to chloramination chemistry and the lesson learnt from this and other recent secondary disinfection related incidents. RW12187. Completed - Develop a program/plan to undertake thorough risk assessments (e.g. HAZOP, CHAZOP) of the dosing systems to understand where our primary risks are, including single points of failure, WQ and safety risks. RW12188 Increase the SL1000 testing frequency for the WTP secondary disinfection trains to each shift - update Mt Crosby East Bank Operational Monitoring Plan (PLN-00014). RW12189 Completed - Lessons learnt from this incident need to be documented for future reference and to allow better informed decision making in the advent of unintentional or intentional conversion of a chloraminated supply system to a free chlorinated one and then back again. Note – also incorporated into DWQ training. RW12190 Completed | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2022-08-31 09:00 | Completed | Refer D19/173039 ICAM Investigation Brisbane, Ipswich and Logan Supply Areas Free Chlorinated Water (06/08/19). Individual actions have been identified in this report. Please refer to this for further information and Risk Wizard Actions. All actions investigated.. | 2020-07-20 09:00 | 2022-08-17 15:29 | Bacteria
Supply System (All) | Central | 12035 | Supply System - Disinfection (secondary) - Incorrect ammonia dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water. Medium (8) | NPI Supply Zone Conduct Process Assessment of Caloundra Street WQMF dosing systems. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-12-29 09:00 | Not yet started | Dapo K advised that this Process Assessment will be conducted in the 21/22 financial year. | 2020-07-20 09:00 |  | Bacteria
Supply System (All) | Central | 12036 | Supply System - Whole of System - Inaccurate online instruments Due to: - maintenance practices/activities; - sample line issues; - instrument and component failure. leading to - potential under or overdosing of treatment chemicals; - failure to notifiy the Control Room of water quailty issues or failures in the system. Medium (8) | Redland Supply Zone Implementation of updated PRO-02120 Corporate HACCP - Management of WQ Online instruments Procedure which now incorporates wet rack cleaning. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2023-01-31 09:00 | Completed | Instrument wet rack cleaning is now scheduled to be completed 6 monthly and is incorporated in Management of WQ Online Instruments Procedure. | 2020-07-20 09:00 | 2023-02-03 11:17 | Bacteria
Maroon Dam WTP | South | 12073 | TMD-RW-A 12073 Risk Treatment: commence daily settled water UV254 monitoring for the purpose of monitoring coagulation effectiveness | TMD - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - low pH in raw water Medium (8) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | Status update 28/09/2020: Process Laboratory to provide instrument capable of monitoring UV254, provide all consumables needed and supply training to competency of UV254 analysis. DWQA to update HACCP documents. Operators are familiar with UV254 monitoring as it is being performed at Kalbar WTP. 29/8/2022 completed and working well. | 2020-02-28 09:00 | 2022-08-29 08:50 | Protozoa
Maroon Dam WTP | South | 12074 | TMD-RW-A 12074 Risk Treatment: investigate opportunities to mitigate sludge build up in settled water balance tank. WTP Operations to raise works request for inlet pipework modification to improve hydraulic mixing in tank. Trial at Moogerah WTP. | TMD - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMD-19) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | In progress | Update 14/05/2020: ION01363 raised for TMD- Energy dissipation to the inlet of the balance tank. If successful at Maroon dam WTP this should be installed at Moogerah dam WTP. | 2020-02-28 09:00 |  | Protozoa
Moogerah WTP | South | 12089 | TMG-RW-A-12089 Risk Treatment: relocate raw water analyser from raw water pumps at dam to inlet to raw water balance tank as per Maroon Dam WTP. | TMG - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMG-15) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | Check with maintenance to see if this can be done under a works request. If not, raise ION. Work is not required as we evaluated the proposed change, and it wasn't necessary. The operational monitoring plan has a draft change of the turbidity monitoring point and goes an update (REX) along with other documentation relating to recent changes in the pant and after the upcoming risk assessment review. | 2017-09-06 09:00 | 2023-01-30 11:32 | Protozoa
Moogerah WTP | South | 12090 | TMG-RW-A-12090 Risk Treatment: commence daily dosed filtered UV254 monitoring for the purpose of UV disinfection | TMG - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - high pH Medium (8) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | UV 254 monitoring implemented. | 2020-02-28 09:00 | 2022-08-29 08:57 | Protozoa
Moogerah WTP | South | 12091 | TMG-RW-A-12091 Risk Treatment: investigate opportunities to mitigate sludge build up in settled water balance tank. WTP Operations to raise works request for inlet pipework modification to improve hydraulic mixing in tank. Trial at Moogerah WTP. | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-02-28 09:00 | Completed | Status update: ION01363 raised for TMD- Energy dissipation to the inlet of the balance tank. If successful at Maroon dam WTP this should be installed at Moogerah dam WTP. Flocculation and Settling - Carryover of floc, sludge or algae in settled water causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build-up of solids in settled water balance tank. Note: modification to pipework improve mixing of coagulant, drain clarifier manually, sludge carry over. close. | 2017-09-06 09:00 | 2023-01-30 10:43 | Protozoa
Hinze Dam WTP | South | 12154 | THZ-RW-A-12154 Risk Treatment: Instigate dial out alarm if raw water flow detected and WTP not running to detect untreated raw water flows entering WTP. | THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water Medium (8) (HNZ-5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | SCADA work request or ION to be raised. Due date extended 12 months to allow for changes in DWQ advisor staff (new and acting arrangements). To be re-assigned once southern advisor position is filled. | 2019-12-03 09:00 |  | Protozoa
Kooralbyn WTP | South | 12161 | TKO-RW-A 12161 Risk Treatment: CO2 injection point delivered with alum dosing system however CO2 dosing system not delivered. CO2 system assessed as not being feasible. Coagulation process would benefit from acid dosing when running on Bigfoot Lagoon. | TKO - Coagulation - Incorrect coagulant dose Overdose of alum resulting in contaminated treated water including underdose of caustic Medium (8) (TKO-18) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2023-12-31 09:00 |  | Update 15/2/2022: During the ION review Mick Drews commented that “Planning for design and construction of additional treatment process at treatments plants should be considered by the Asset Planning Team”. There is nothing further that we can do to address the issue. Update 24/08/2020: PE raised ION00592 to introduce acid dosing for when sourcing Bigfoot lagoon Assigned to JC following discussion in HACCP team meeting August 2020 D20/154460. Update 2022: ION00592 has been passed to Planning to implement new dosing system. PLEASE DO NOT CLOSE THIS ACTION UNTIL IMPROVEMENT HAS BEEN DELIVERED ON SITE. | 2017-07-19 09:00 |  | Protozoa
Kirkleagh WTP | North | 12268 | TKR- Raw Water Abstraction Contaminant load exceeds treatment capacity Medium (8). (due to crypto short fall) | Risk Treatment (raised R.A 2020): Consider re-evaluating/conducting HBT tier 2/1.5 assessment to verify risk and investigate requirements for upgrades. Installation of UV is in the program to be delivered 2022 as part of the KKR project. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress |  | 2019-07-17 09:00 |  | Protozoa
Jimna WTP | North | 12269 | TJI- Raw Water Abstraction Intake of raw water that exceeds the treatment capacity of the plant affecting treated water quality. Medium (8). (due to crypto short fall) | Risk Treatment (raised R.A 2020): An additional Prozoa Treatment barrier is required to address the shortfall against the HBT tier 1 assessment. Alternatively investigation into a tier 1.5/2 assessment to verify the risk | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress |  | 2019-07-17 09:00 |  | Protozoa
Landers Shute WTP | North | 12756 | Investigate additional ongoing continuous improvements such as - introduction of interlocking mechansim on filters that closed the outlet instead of the inlet valve, introduction of a secondary critical limit at 1 NTU for >1 minute on individual filters, introduction of 95th percentile critical limit on filtered water turbidity, introduction of interlock on dosed water pH. | NB the interlocking of critical limits is currently managed under the MOC# 1268 Interlocks being worked on - enterprise risk treatment plan tracker - john klowse - fiore is owner. HACCP function blocks - OTE in conjunction with the CSM. Presently - In the event of breakthrough: inlet will close and an autobackwash will begin, taking the filter offline; however - the volume of the filter will still pass through the broken through filter should this occur. Ideally, the outlet should close and the filter should drain to waste. Flashmixer pH - Out of 2198 samples, the minimum was 6.1 units the 5th percentile was 6.5 (6.5, 6.5) units, the mean was 6.7 (6.7, 6.7) units, the 95th percentile was 6.9 (6.9, 6.9) units and the maximum result was 7.3 units. σ = 0.135 (0.131,0.139). Data:Jan-2015 to Jan-2021. 95% Confidence Intervals in brackets. - Filtered Water Turbidity - Out of 2190 samples, the minimum was 0.011 NTU the 5th percentile was 0.04 (0.04, 0.04) NTU, the mean was 0.071 (0.07, 0.072) NTU, the 95th percentile was 0.12 (0.11, 0.12) NTU and the maximum result was 0.55 NTU. σ = 0.0266 (0.0258,0.0274). Data:Jan-2015 to Jan-2021. 95% Confidence Intervals in brackets. There is a common outlet channel. No individual flow meters. Filter control valve position is displayed on the SCADA. There is a setpoint for filter control rate which determines if filters come on or off. Filter rate control mode is auto or manual. All filters that are to be backwashed go offline and into a queue. Further - investigate the options to include alarming on variance or stdev of trends, as this will give the plant the capability to detect flatlining events (i.e. where the instrument is producing a false superstable reading for any reason). Recent Audit (Task 19145) conducted on 16/2/21 by Kelly Dempster identified issue with flatline trend on filter 5. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2023-12-30 09:00 | In progress | NB the interlocking of critical limits is currently managed under the MOC# 1268 and the introduction of standard HACCP blocks. This is anticipated to be fully completed by end of june 2022. time extended to reflect MOC progress. prog/rep: still on track for end of june implementation according to Michael Burns. 7/7/2022: John Klowss: can the date be changed until the end of the year? Mike, can we get together over July/Aug to plan and then aim to deliver in September. If otherwise urgent look to do sooner. Just staff shortages and current demands through to September. Hope this can assist in scheduling and implementing before wet season (if such a thing exists – better than dry). John 1/12/2022 John Klowss: Due to a number of factors, the movement of the interlocking has moved to the project to deliver. With that in mind, should this be moved to be apart of the projects scope to deliver and close this risk wizard? NE 8/12/2022 No - we will keep it open until it is implemented. I will extend the date to end of fy. I will re-assign action manager since Cam is no longer the right person. NE: 31/5/2023 - Further extension required. Extending another 6 months. | 2021-03-09 09:00 |  | Protozoa
Lowood WTP | Central | 12845 | Central Region- Somerset South- Lowood WTP- HBT assessment | 16 June - Access to SCADA denied 21 June - Access to data issues in SCADA. Call logged by Hany for Kevin 2 July - Data issues resolved 5 July - Filtered water turbidity data gaps identified by Kevin and reported to Control System Engineers | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2022-11-30 09:00 | In progress | 13/01/2022 (EH): A tool to streamline and complete frequent HBT assessment is underway. This utilises the available TLO historian, SQL to query the historian and excel for data analysis. A template has been produced and coding is progressing well. The current due date (30/06/2022) has been discussed and agreed with DWQ. PE are currently on track to meet this date. 14/12/2021 Extension needed to complete assessment. (AC) 29/08/2022 Discussed extension of due date with Dan Healy to 30/11/2022. 29/11/2022 TLO HBT assessment for Nov 2021 to March 2022 has been completed and initial dashboard virtually shared with stakeholders. | 2021-04-06 09:00 | 2022-11-29 17:05 | Protozoa
Lowood Intake Raw Water Pump Station | Central | 12894 | Central Region- Somerset South- Lowood WTP- place back up generator at raw water PS | There is a project in planning stage including the placement of a generator at the raw water PS | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-12-30 09:00 | Not yet started |  | 2021-04-19 09:00 |  | Protozoa
Lowood WTP | Central | 12897 | Central Region- Somerset South- Lowood WTP- installation of UV to implement additional barrier to meet log removal requirements for protozoans | Project is in planning stage and delivery scheduled for 2021/ 2022 | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-06-30 09:00 | Not yet started | Project is on its way and completion scheduled towards the end of this year. Update - planning underway. B Hester is representing DWQ. Review at end of 23/24 year. | 2021-04-19 09:00 |  | Protozoa
Lowood WTP | Central | 12899 | Central Region- Somerset South- Lowood WTP- Validate and document inhibit timeframe for turbidity instruments. | Review current instrument locations, analysers locations and instrument type to ensure timely and accurate monitoring. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-01-31 09:00 |  | Date extended to allow time for Elyse and Harish to work on higher priority work and to return from Xmas leave. It is understood that they have completed this in recent work at Lowood. Process Engineering Lead - Schedule meeting to review in Jan 24.. | 2021-04-19 09:00 |  | Protozoa
Lowood WTP | Central | 12900 | Central Region- Somerset South- Lowood WTP- additional clarifier to mitigate supply and water water quality risks | Additional clarifier is in delivery stage change of action ownership to Dan Healy Currently in early planning/design stage - date pushed out to end of FY 24/25 to allow for project completion. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2025-06-30 09:00 | Not yet started |  | 2021-04-19 09:00 |  | Protozoa
Molendinar WTP | South | 13006 | TMO-RW-A-13006 Risk Treatment: To 1) determine monitoring and alarming to detect high level in the backwash overflow chamber and determine a subsequent response and recovery plan, and 2) progress infrastructure changes required to prevent high level in the backwash overflow chamber. | Refer linked incident. Assigned to Brian Johns, Craig Bolin and team. Prevention of overflow to CCT will require infrastructure change therefore this would require ION or the new EAR (Emerging Asset Risk) process. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Brian Johns to talk to Sam and P.E about design options. Will likely have to go through MoC and drawings updated. Will need to be commissioned hydraulically to demonstrate effectiveness in order to close out risk treatment item. In addition, to improve detection of an overflow event, investigate multitrode option. This will enable early determination to drain CCT. 26/11/2021 Works request raised to have reliable alarming with a High and HighHigh system in place using a Multitrode | 2021-04-30 09:00 |  | Protozoa
Mt Crosby Eastbank WTP | Central | 13242 | East Bank WTP - Media Filtration - Filter Breakthrough (Medium 8) | Review more data related to new filter performance. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-01-31 09:00 | Not yet started | Date extended as this work has not yet commenced | 2021-08-12 09:38 |  | Protozoa
Mt Crosby Eastbank WTP | Central | 13243 | Mt Crosby Holts Hill - Disinfection (Secondary) - Incorrect Ammonia Dose - Under dosing of ammonia. (Medium 8) | Planned Ammonia upgrade works for Holts Hill | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-06-30 09:00 | In progress | 1. New ammonia ring main. Replacement of all valves. Flexible hose on dosing tank to ring main replaced. Completed 2. Ammonia dosing tank to be replaced. Stage 2 replacing tank, Design Only Contract awarded to Aurecon. Project currently in design stage. Construct contract PC 30/6/22 HAZOP and RA under taken (June 2023) Date extended to allow for completion of project. | 2021-08-12 09:55 |  | Bacteria
Mt Crosby Eastbank WTP | Central | 13244 | East Bank WTP - Whole of System - Loss of SCADA system or loss of PLC (Medium 8) | Upgrade of system platform across all sites. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2025-12-31 09:00 | Not yet started | Training for operations or Manual? | 2021-08-12 10:27 |  | Protozoa
Landers Shute WTP | North | 13523 | Investigate options for control of biomass growth in filters. - pre ozonation replacement project including prefilter chlorine - project underway - plant trials underway. Still in asset planning. |  | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-12-14 09:00 | Not yet started |  | 2021-12-14 09:00 |  | Protozoa
Landers Shute WTP | North | 13524 | Investigate options for collection of chemical waste from site labs. (Complete) install turbidity and pH instrument on return water line. ( see ION https://waternet.corporate.local/forms/Pages/ION.aspx?formId=458) Improvement to stop >10% seperated water return. MOC: https://waternet.corporate.local/forms/Pages/ION.aspx?formId=479 Alysha - mass balance acrylamide - potential for contamination |  | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-12-14 09:00 | Not yet started |  | 2021-12-14 09:00 |  | Protozoa
Supply System (All) | Central | 14893 | Supply System - Brisbane Zone - Reservoir - Elevated water age. Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. High (12) | Historian (when implemented) to develop metric for water age of reservoirs. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2025-12-31 09:00 | Not yet started | EAR to be raised for this item. | 2023-07-19 09:00 |  | Bacteria
Supply System (All) | Central | 14894 | Supply System - Brisbane Zone - Reservoir - Elevated water age. Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. High (12) | Investigate additional dosing facilities in the network. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2028-12-31 09:00 | Not yet started | EAR to be raised for this item. | 2023-07-19 12:00 |  | Bacteria
Supply System (All) | Central | 14895 | Supply System - Brisbane Zone - Disturbance of Sediment Due to one or more of the following events leading to out of specification treated water: - Low level; - Significant rate up or draw; - Valving change altering flow dynamics. Medium (8) | Investigate most effective way to clean Supply System Reservoirs. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-06-30 09:00 | Not yet started | Trial conducted at Capalaba. Details to come. Procedure to be updated to include new process for determining what needs cleaning. Robot cleaning to be added to the panel of providers. | 2023-07-19 14:01 |  | Protozoa
Supply System (All) | Central | 14896 | Supply System - Brisbane Zone - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | - Review the current reservoir inspection program/schedule to ensure effectiveness. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-06-30 09:00 | Not yet started | The main issue here is understand the process. Who puts items in WOs, Ears. Does the process cover Ears currently? Lack of comms from maintenance also an issue. Update the procedure to clarify the above. | 2023-07-19 14:49 |  | Bacteria
Supply System (All) | Central | 14897 | Supply System - Brisbane Zone - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | Replace/repair Green Hill Reservoir membrane. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-06-30 09:00 | Not yet started | Identified in the IAMP with completion expected by July 2026.Project. Also identified in the Facility Risk Review Register. RTP 103. | 2023-07-19 15:34 |  | Bacteria
Supply System (All) | Central | 14898 | Supply System - Brisbane Zone - Incorrect Ammonia Dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water Medium (8) | Review low flow conditions for dosing at Aspley WQMF. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-07-31 09:00 | Not yet started | MOC to be raised to kick off this investigation. | 2023-07-20 12:13 |  | Bacteria
Supply System (All) | Central | 14899 | Supply System - Brisbane Zone - Incorrect Ammonia Dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water Medium (8) | - Investigate sizing of ammonia dosing pumps to ensure adequate dosing at low levels. MOC and EAR to be raised. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-06-30 09:00 | Not yet started |  | 2023-07-20 12:42 |  | Bacteria
Supply System (All) | Central | 14916 | Supply System - Brisbane Zone - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water. Medium (8) | - Investigations to find customers with direct connections to mains. - Brisbane City Council Mt Coot-tha Botanical Gardens. - Reticulation Connections - Mt Crosby reticulation connections, Brighton. Investigate around Council depots from legacy Brisbane Water connections. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 09:00 | Not yet started |  | 2023-07-24 11:48 |  | Protozoa
Supply System (All) | Central | 14917 | Supply System - Brisbane Zone - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water. Medium (8) | - Either give mains back to Urban Utilities, or retrace another main (real bulk transfer). Brisbane CC Mt Coot-tha Botanical Gardens. Reticulation Connections - Mt Crosby reticulation connections, Brighton. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 09:00 | Not yet started |  | 2023-07-24 11:53 |  | Protozoa
Supply System (All) | Central | 14918 | Supply System - Brisbane Zone - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water. Medium (8) | - Need to have discussions with Water Service Providers to install networks to support their customers. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 09:00 | Not yet started |  | 2023-07-24 12:03 |  | Protozoa
Supply System (All) | Central | 14919 | Supply System - Brisbane Zone - Decommissioned or offline assets not properly isolated. Leading to out of specification treated water. Medium (8) | Investigate removal of decommissioned assets. Assets include: Pipe over Mt Crosby Road at Ugly Gully (determine ownership). Camerons Hill Booster PS isolated but not properly decommissioned. Pump 4 and 5 at Stones Road isolated but not decomissioned. 2 offtakes at My Crosby Road - old connection to lockbar main. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-03-31 09:00 | Not yet started | EAR to be raised. | 2023-07-24 13:36 |  | Bacteria
Supply System (All) | Central | 14920 | Supply System - Brisbane Zone - Decommissioned or offline assets not properly isolated. Leading to out of specification treated water. Medium (8) | Add decommissioned equipment layer within GIS. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-09-30 09:00 | Not yet started |  | 2023-07-24 13:44 |  | Bacteria
Supply System (All) | Central | 14947 | Supply System - NPI Zone - Bulk Pipeline - Contamination due to pipe depressurisation Ingress of contaminants through: - Pipe joints. - Air valves. - Leaking valves and hydrants. - Aging infrastructure. - Scours. Ingress caused by loss of pressure in main during: - Pipe burst. - Pipe repairs. - Very high flows (e.g. fire fighting) . - Incorrect isolation for maintenance Medium (8) | - SCADA PLC upgrade on NPI which includes full commissioning to the operating philosophy of NPI. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2027-12-31 09:00 | Not yet started |  | 2023-07-25 16:01 |  | Protozoa
Supply System (All) | Central | 14948 | Supply System - NPI Zone - Bulk Pipeline - Contamination due to pipe depressurisation Ingress of contaminants through: - Pipe joints. - Air valves. - Leaking valves and hydrants. - Aging infrastructure. - Scours. Ingress caused by loss of pressure in main during: - Pipe burst. - Pipe repairs. - Very high flows (e.g. fire fighting) . - Incorrect isolation for maintenance Medium (8) | - Investigate the valve pit inspection programs that it includes the effectiveness of drainage pits. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-07-31 09:00 | Not yet started |  | 2023-07-25 16:06 |  | Protozoa
Supply System (All) | Central | 14956 | Supply System - NPI Zone - Reservoirs - Elevated water age Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. High (12) | - Investigate mixers at Narangba as its a more urgent requirement. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2024-05-31 09:00 | Not yet started |  | 2023-07-27 09:34 |  | Bacteria
Supply System (All) | Central | 14957 | Supply System - NPI - Disinfection (secondary) - Incorrect Sulfuric Acid Dose Under dose of sulfuric acid leading to reduced secondary disinfection for break point chlorination High (12) | Complete the commissioning of the Sulfuric Acid dosing system at Caloundra Street WQMF. Essential for RSDOP to progress. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2024-07-31 09:00 | Not yet started | Business case was being finalised in Sept 2023. MW-00449 - W07 - Sulphuric Acid Dosing System Redesign and Commissioning | 2023-07-27 13:07 |  | Bacteria
Supply System (All) | Central | 14958 | Supply System - SRP - Reservoirs - Elevated water age Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. Medium (8) | - Review operating philosophy of hybrid flows for the SRP | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-12-31 09:00 | Not yet started |  | 2023-07-28 10:51 |  | Bacteria
Supply System (All) | Central | 14960 | Supply System - SRP - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | Investigate when Stapylton Reservoir is due for refurbishment and identify any works planned to reduce the risk of ingress due to the size of roof sheeting. Determine when Ventilation at Molendinar reservoir is being upgraded and escalate if required. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-01-31 09:00 | Not yet started |  | 2023-07-31 09:55 |  | Bacteria
Supply System (All) | Central | 14975 | Supply System - Gold Coast/NIP - Reservoir - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | - Investigate replacing box gutters at Molendinar 3 and 4 reservoirs. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-12-31 09:00 | Not yet started | Raise EAR for this. | 2023-07-31 16:57 |  | Bacteria
Supply System (All) | Central | 14977 | Supply System - EPI - Whole of System Decommissioned or offline assets not properly isolated Leading to out of specification treated water. Medium (8) | '- Investigate removal of Kimberley Park Temporary tank. - Determine business position on the NSI Booster Pump Station and either decommission or start maintaining these assets. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-08-31 09:00 | Not yet started |  | 2023-08-02 13:50 |  | Bacteria
Supply System (All) | Central | 14995 | Supply System - Redland Zone - Bulk Pipeline - Contamination due to pipe depressurisation Ingress of contaminants through: - Pipe joints. - Air valves. - Leaking valves and hydrants. - Aging infrastructure. - Scours. Ingress caused by loss of pressure in main during: - Pipe burst. - Pipe repairs. - Very high flows (e.g. fire fighting) . - Incorrect isolation for maintenance Medium (8) | - Implement automated controls for the valves between NSI and Serpentine Creek (MoC #1928). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-07-31 09:00 | Not yet started |  | 2023-08-04 15:00 |  | Protozoa
Supply System (All) | Central | 14996 | Supply System - Redland Zone - Reservoir - Inadequate Mixing Poor mixing in a reservoir leading to: - Pockets of reduced quality water. - Increase the possibility of nitrification. - Temperature issues. Medium (8) | - Replacement of Mixers at Alexandra Hills Reservoirs 1,3,4 and 5 as well as Heinemann Road Reservoirs 2 and 3 as a priority due to mixing issues. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-09-30 09:00 | Not yet started | EAR has been raised and this item has been added to the Facility Risk Review process for Supply System - RTP 313 | 2023-08-04 15:45 |  | Bacteria
Supply System (All) | Central | 14997 | Supply System - Redland Zone - Reservoirs - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris High (12) | - Roof replacement for Heinemann Road Reservoir 1. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2024-12-31 09:00 | Not yet started | Included in Reservoir package 1 works. Due for completion July 2024. | 2023-08-04 15:55 |  | Bacteria
Supply System (All) | Central | 14998 | Supply System - Redland Zone - Reservoirs - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris High (12) | - Investigate box gutters at Alexandra Hills 4 Reservoir. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2027-12-31 09:00 | Not yet started | Replace roof including re-design of gutter for Alexandra Hills Reservoir 4 is in the IAMP Capital Program for delivery in 2026/2027 | 2023-08-04 04:00 |  | Bacteria
Supply System (All) | Central | 14999 | Supply System - Redland Zone - Disinfection (Secondary) - Incorrect Chlorine dose Underdosing of sodium hypochlorite causing overdose of chlorine leading to out of specification treated water. Medium (8) | - Conduct a Process Assessment of Heinemann Road and Alex Hills dosing. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-12-31 09:00 | Not yet started |  | 2023-08-07 09:50 |  | Bacteria
Supply System (All) | Central | 15000 | Supply System - Redland Zone - Whole of System - Loss of power Loss of power impacting treated water quality Medium (8) | - Investigate installation of a generator to run Heinemann Rd PS (can be trailer mounted) including shelter. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-12-31 09:00 | Not yet started | Included in the Supply System Facility Risk Register - RTP 161 | 2023-08-07 10:20 |  | Bacteria
Supply System (All) | Central | 15005 | Supply System - Logan Zone - Reservoirs - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | - Investigate possible solutions to reduce the likelihood of WQ related issues with the Break of Head Tank. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-10-30 09:00 | Not yet started |  | 2023-08-08 15:23 |  | Bacteria
Supply System (All) | Central | 15008 | Supply System - Logan Zone - Loss of Power Leading to out of specification treated water. Medium (8) | - Investigate implementation of permanent generator at Trinder Park. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2027-07-30 09:00 | Not yet started |  | 2023-08-09 10:40 |  | Bacteria
Dayboro WTP | North | ION: 1293 | TDY - UV disinfection - Insufficient UV dose for viruses | The plant has no online UVT monitoring and hence no way to validate or enact this requirement. There is a risk that if the plant were to fall below 90% UVT and it is not identified, the required pathogenic log reduction may not be achieved. | Risk Assessment | High | 12 | Senior DWQ Advisor - North | 2025-03-27 | In progress | Installation of UVT analyser and validation of virus log reduction (in order to validate at least 1 log credit for viruses) by trojan/manufacturer. Install dynamic Ct (Mike Burns program) | 2020-03-27 |  | Viruses