## North
Northern Operational Region - Register of changes to HACCP plans, procedures or related documents
# | Document Ref | WTP/System | HACCP Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | QWSR Amendment Required (by Principal DWQ)
272 | PLN-00045 | Landers Shute WTP | HACCP Plan | Various | Updates to the document to reflect consistency improvements including updates to the formatting of the chemicals table, updates to the PFD and schematic. Also this version makes clear the distinction between interozone and BAC and documents polymer flocculation aid. |  | NE | 2022-07-19 | y
273 | PRO-02025 | Image Flat WTP | Wall Chart Procedure | Various | Ops Protocols table update and various reporting message updates |  | NE | 2022-07-27 | y
274 | PRO-02107 | Landers Shute WTP | Wall Chart Procedure | Various | Ops Protocols table update and various reporting message updates |  | NE | 2022-07-27 | y
275 | PRO-02108 | North Pine WTP | Wall Chart Procedure | Various | Ops Protocols table update and various reporting message updates |  | NE | 2022-07-27 | y
276 | PRO-02026 | Dayboro WTP | Wall Chart Procedure | Various | Ops Protocols table update and various reporting message updates |  | NE | 2022-07-27 | y
277 | PRO-02074 | Noosa WTP | Wall Chart Procedure | Various | Ops Protocols table update and various reporting message updates |  | NE | 2022-07-27 | y
278 | PLN-00068 | North Pine WTP | Operational Monitoring Plan | Various | use the current HACCP language, highlighted the HACCP reportable parameters and added the additional monitoring we are conducting according to the PDL (i.e. the UV254) added Raw water Abstraction- DO, Online, Continuous Monitoring |  | NE | 2022-08-19 | Y
279 | PRO-02223 | Kilcoy WTP | Wall Chart Procedure | Various | Ops Protocols table update and various reporting message updates. Update to format. |  | NE | 2022-08-19 | Y
280 | PLN-00033 | Landers Shute WTP | Operational Monitoring Plan | Various | Update to consistency with PDL and HACCP language |  | NE | 2022-09-12 | Y
281 | PRO-02108 | North Pine WTP | Wall Chart Procedure | Treated water section | Update to include manganese and turbidity action limits |  | NE | 2022-10-11 | Y
282 | PLN-00067 | Dayboro WTP | Operational Monitoring Plan | various | small update to the OMP for dayboro with a few changes to some of the step names for consistency |  | NE | 2022-10-14 | Y
283 | PLN-00082 | Jimna WTP | HACCP Plan | Whole document | - Added constraints to process descriptions - Updated HBT assessment to be consistent with chapter 5 adwg - Updated naming conventions to current standard - Added new manganese action limit (filtered water free chlorine) - Added validation to limits - Updated scope to current standard - Updated haccp team description to current standard - Updated HACCP flow diagram (and signed off) - Updated schematic diagram - Added aerial photo - Added improved map to site - Added description of spray-back aeration process - Improved Ct calculation - Updated operational challenges - Updated oPRP descriptions - Updated chemical descriptions - Added reporting and review sections - Corrected section numbering - Added >0.99 for >1min filtered water critical limit |  | NE | 2022-10-27 | Y
284 | PLN-00083 | Jimna WTP | Operational Monitoring Plan | Various | updates to bring up to current standard and include changes from the large update to the haccp plan |  | NE | 2022-11-01 | Y
285 | PRO-02225 | Jimna WTP | Wall Chart Procedure | Various | updates to bring up to current standard and include changes from the large update to the haccp plan |  | NE | 2022-11-01 | Y
286 | PRO-02026 | Dayboro WTP | Wall Chart Procedure | Various | change to filtered water turbidity limit |  | NE | 2022-11-23 | Y
287 | PRO-02419 | Linville WTP | Wall Chart Procedure | 2nd stage filtration | Just action limit update to haccp plan and wall chart Change of 2nd stage filtered water turbidity >0.2 for >1 min to >0.2 for >4 min This is due to the implementation of the softener system which adds a little turbidity at start up. No changes to the critical limits (or anything else) in the haccp plan or wall charts |  | NE | 2022-11-25 | Y
288 | PLN-00080 | Linville WTP | HACCP Plan | Validation | Just action limit update to haccp plan and wall chart Change of 2nd stage filtered water turbidity >0.2 for >1 min to >0.2 for >4 min This is due to the implementation of the softener system which adds a little turbidity at start up. No changes to the critical limits (or anything else) in the haccp plan or wall charts |  | NE | 2022-11-25 | Y
289 | PLN-00066 | Dayboro WTP | HACCP Plan | various | The changes are: • Max instantaneous treated water flow moved from 15 L/s to 16 L/s • Recalculated Ct with new information, no change required to existing critical limit of 0.6 mg/L • Various formatting changes to bring up to the current standard • Inclusion of oprp table • Update to UV validation – now including filtered water turbidity • Addition of total manganese as QCP testing for greensand media filtration • Updated catchment description and various other components (schematics etc) to reflect the relatively elevated risk of Well 2 (due to the proximity to the river and the STP) • Updated the description of the fluoride component • Updated the chemicals section • Renumbered sections to align with corporate standards • Added process constraint descriptions to all processes • Moved raw water abstraction to oPRP from CCP • Updated haccp team description • Updated haccp flow diagram and schematic diagram • Updated the microbial HBT assessment with an ADWG compliant estimation utilising existing source water data • Updated Sec. 5 – Reporting and Sec. 6 – Review to refer to risk wizard process |  | NE | 2022-12-20 | Y
290 | PLN-00031 | Ewen Maddock WTP | Operational Monitoring Plan | Whole document | The columns now aligned with a reading of the PDL This enables easier verification of the OMP against the PDL. |  | NE | 2023-01-20 | Y
291 | PRO-02184 | Ewen Maddock WTP | HACCP Plan | Whole document | the changes are cosmetic, however I have changed the following limits Dosed filtered water: Free chlorine & pH action limits (as discussed at haccp team meeting) Treated water Free chlorine, ph action limits (as discussed at haccp team meeting) Added >0.99 NTU for >1min critical limit (MOC in the approval process, awaiting cam endorsement) (as discussed at haccp team meeting, regarding all sites) Renamed separated water return to supernatant return (to comply with validation standard names) Introduced supernatant return action limit of >5% for >1 day (to show the intent of the limit i.e. keeping usual flows low) – happy to be flexible with this Introduced supernatant return critical turbidity limit of 100 NTU as a grab. I don’t expect us to see this kind of turbidity and this is just a starting point so we have a limit in place. We will introduce it to the OMP as a regular monitoring program until we get the analyser installed (and the limit will be revised) I have added to the table at the back better describing the critical shutdown process and some words around critical control points failures. |  | NE | 2023-03-01 | Y
292 | PRO-02026 | Dayboro WTP | Wall Chart Procedure | Disinfection filtered water action limit: | change from 0.5 from 0.4 due to alignment with limitation in scada (can only have one limit) |  | NE | 2023-03-03 | Y
293 | PLN-00066 | Dayboro WTP | HACCP Plan | Validation | change from 0.5 from 0.4 due to alignment with limitation in scada (can only have one limit) |  | NE | 2023-03-03 | Y

## Central
Central Operational Region - Register of changes to HACCP plans, procedures or related documents
# | Document Ref | WTP/System | HACCP Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | QWSR Amendment Required (by Principal DWQ)
435 | PR0-02089 | Supply System | HACCP Plan Wall Chart Procedure | Whole document | Included new sample point codes for whole of document |  | KM | 2023-06-29 | Y
436 | PR0-02089 | Supply System | HACCP Plan Wall Chart Procedure | Caloundra Street South | Added monochloramine action and critical limit. Added free ammonia action limits. |  | KM | 2023-06-29 | Y
437 | PR0-02089 | Supply System | HACCP Plan Wall Chart Procedure | Chambers Flat North | Added monochloramine action and critical limit. Added free ammonia action limits. |  | KM | 2023-06-29 | Y
438 | PR0-02089 | Supply System | HACCP Plan Wall Chart Procedure | Kimberley Park East Panel | Added operational targets, action limits and critical limits for chlorine, pH and turbidity. Added Roof Hatch alarm. |  | KM | 2023-06-29 | Y
439 | PR0-02089 | Supply System | HACCP Plan Wall Chart Procedure | Kimberley Park West Panel | Changed name of Kimberley Park Reservoir Outlet to Kimberley Park East Panel |  | KM | 2023-06-29 | Y
440 | PR0-02089 | Supply System | HACCP Plan Wall Chart Procedure | Whole document | Removed reference to REG links associated with WTP HACCP Wall Charts |  | KM | 2023-06-29 | Y
446 | PRO-02015 | Lowood WTP | HACCP plan wall chart procedure | Whole document | Update to new corporate style Corrective actions updated for flocculation & settling oPRP |  | D Healy | 2023-03-14 | Y
447 | PRO-02016 | Esk WTP | HACCP plan wall chart procedure | Whole document | Update op fluoridation CCP to be consistent with SPE-00320 |  | D Healy | 2022-12-19 | Y
448 | PRO-02015 | Lowood WTP | HACCP plan wall chart procedure | Whole document | Update op fluoridation CCP to be consistent with SPE-00320 |  | D Healy | 2022-12-19 | Y

## South
Southern Operational Region - Register of changes to HACCP plans, procedures or related documents
# | Document Ref | WTP/System | HACCP Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | QWSR Amendment Required (by Principal DWQ)
476 | PLN-00040 | North Stradbroke Island WTP | HACCP Plan | Table of contents Associated Documents HACCP TeamSystem Overview PRP Materials and Chemicals Reporting | °Updated table of contents *Updated Associated documents *Removed HACCP Team table and referred to PLN-00004 *Updated System Overview with new minin lease info *Removed oPRP table *Updated Chemical information *Updated reporting to the new requirements |  | NF | 2022-07-15 | Y
477 | PLN-00037 | Capalaba WTP | HACCP Plan | Whole document | update to new corporate style included detail of fitler valvle positioning sensor project completion adjusted coag action limit to pH 6.1 updates to check previous QCP and change to oPRP where apprpriate | N/A | DG | 2023-06-29 | Y
478 | PLN-00120 | Capalaba WTP | Operational Monitoring Plan | Whole document | update to new corporate style adjusted coag action limit to pH 6.1 updates to check previous QCP and change to oPRP where apprpriate | N/A | DG | 2023-06-29 | Y
479 | PRO-02057 | Capalaba WTP | HACCP Plan Wall Chart Procedure | Whole document | update to new corporate style updates to check previous QCP and change to oPRP where apprpriate | N/A | DG | 2023-06-29 | Y
480 | PRO-01929 | Maroon WTP | HACCP plan wallchart | Whole document | • Raw water abstraction oPRP limits set for true colour, UV 254 and pH • Inclusion of alum dose rate CL into the SCADA limit settings • Settled water UV254 limit settings • The document has been transferred into the new format | N/A | AC | 2023-05-22 | Y
481 | PLN-00108 | Maroon WTP | HACCP plan operational monitoring plan | Whole document | • Raw water abstraction oPRP limits set for true colour, UV 254 and pH • Inclusion of alum dose rate CL into the SCADA limit settings • Settled water UV254 limit settings • The document has been transferred into the new format | N/A | AC | 2023-05-22 | Y
482 | PRO-01929 | Moogerah Dam WTP | HACCP plan wallchart | Whole document | • Raw water abstraction inclusion of true colour, UV254 and pH AL • Coagulation alum dose rate CL • Settled water UV 254 AL • Documents were transferred into the new format | N/A | AC | 2023-05-22 | Y
483 | PLN-00108 | Moogerah Dam WTP | HACCP plan operational monitoring plan | Whole document | • Raw water abstraction inclusion of true colour, UV254 and pH AL • Coagulation alum dose rate CL • Settled water UV 254 AL • Documents were transferred into the new format | N/A | AC | 2023-05-22 | Y
484 | SPE-00504 | Gold Coast Desalination Plant | HACCP Treated Water Quality Specification | Refer Veolia doc management system | Alignment of WQ values and terminology with BWSA with City of Gold Coast | Veolia BMS number: TEM 7200 | Veolia/TF | 2023-01-06 | N
486 | PRO-02591 | Gold Coast Desalination Plant | HACCP Corrective Actions | Refer Veolia doc management system | Updated based on MOC 21.041 (GCDP Water Quality Risk Assessment Outcomes from 2021 RA) | Veolia BMS number: TEM 4255 | Veolia/TF | 2022-12-06 | N
487 | PRO-02591 | Gold Coast Desalination Plant | HACCP Corrective Actions | Refer Veolia doc management system | Updated as per MOC 22.023 Changes to TEM-7200 Water Quality Requirements. GC is now WQL and SON is now WQN. | Veolia BMS number: TEM 4255 | Veolia/TF | 2023-02-08 | N
488 | REG-01114 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated & mitigated) | Refer Veolia doc management system | Annual review | Veolia BMS number: WIS 9395 | Veolia/TF | 2022-11-01 | N
489 | REG-01114 | Gold Coast Desalination Plant | HACCP Risk Register (unmitigated & mitigated) | Refer Veolia doc management system | Annual review | Veolia BMS number: WIS 9395 | Veolia/TF | 2023-05-29 | N
491 | PLN-00476 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Flow Diagram updated QCP COP numbering changes Updated Membrane Management Tool Updated HACCP Team and PRP | Veolia BMS number: MAN 9393 | Veolia/TF | 2022-11-08 | N
492 | PLN-00476 | Gold Coast Desalination Plant | HACCP Plan | Refer Veolia doc management system | Updated terminology SON and GC limits to WQN and WQL | Veolia BMS number: MAN 9393 | Veolia/TF | 2023-01-06 | N
493 | PLN-00486 | Gold Coast Desalination Plant | Monitoirng Plan | Refer Veolia doc management system | updated SON, GC, references to WQN and WQL as per TEM 7200. J. Jo 12/1/23 review comments - amended Acceptance Criteria for Potable Water SZ-GCDPW-G in Ref C1-Plant Operations and Ref C2-Hot Standby RFRT Op to reflect TEM-7200 changes. Changes in red, proposed removal has strikethroughs. | Veolia BMS number: WIS 7204 | Veolia/TF | 2023-01-06 | N
494 | PLN-00486 | Gold Coast Desalination Plant | Monitoirng Plan | Refer Veolia doc management system | Virus testing 6 monthly removed Cryptosporidium oocysts added as required to event monitoring Other micro monitoring updates | Veolia BMS number: WIS 7205 | Veolia/TF | 2023-03-30 | N

## DWQMP & Support Programs
Register of changes to DWQMP and supporting programs
# | Document Ref | Plan/Procedure | Section/Para | Brief description / justification of change | Additional Comments | Originator | Date | QWSR Amendment Required (by Principal PQ)
39 | TEM-00002 | Corporate HACCP - Internal Audit Template. | P1 and p14 | Page 1: - Remove reference to JSEA and replace with Take 5 - Reference to IMS reporting template removed - Reference to REX folder F18/102 for record keeping purposes included - Reference to corrective actions recordings into Riskwizard included Page 14: - Update of PRP audit items - Including audit item of management of Riskwizard relating to corrective actions and close out process |  | A Clement | 2022-09-16
40 | FRM-00988 | Corporate HACCP – DWQ Quality Management – DWQ & Quality Audit and Inspection form |  | minor changes to the wording |  | A Clement | 2022-10-21
41 | PRO-01455 | Tankering of Drinking Water Supplies Procedure | P4 and P5 | S 3 Add definition of hypo to refer to the SPE-00465 Operational Sites – Specification Chemical Quality – Sodium Hypochlorite 10% (Coogee Chemicals) S 5 Add comments point 6 to allow for requirements of hygiene checks prior to filling the reservoir Update details of new supplier in the Somerset/ north/ south region.E48 |  | A Clement | 2022-11-07
42 | PRO-02120 | HACCP - Management of Water Quality Online Instruments Procedure | s6 1. s6.2.1 WTP laboratory results forms appendix 4 Water quality laboratory result forms App 5 add Wallace and Tiernan Depolox 400 | minor changes to the wording Addition of the Chemscan analyser Wet Rack Maintenance frequency changed to 3-monthly |  | A Clement | 2023-06-29
46 | PRO-02360 | Creating a water quality notification in Risk Wizard work instruction | Whole Document | Updated images/screenshots |  | D Healy | 2022-11-15