## DWQIP
SITE | REGION | PROTECHT # | RISK WIZARD # | ISSUE | DESCRIPTION | ORIGIN OF IMPROVEMENT | SIGNIFICANT RISK | SIGNIFICANT RISK LEVEL | RESPONSIBLE | DUE FOR COMPLETION | STATUS | RISK TREATMENT COMMENTS | DATE RAISED | DATE CLOSED | LIMITING HAZARD
Supply System (All) | Central | 1004003 | 9461 | Supply System - Disinfection (secondary) - Incorrect chlorine dose Under dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water. Medium (8). | Redlands Supply Zone - Investigation of having duplicate single instruments for Heinemann Road Reservoirs 1, 2 3. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2027-10-31 | In progress | Refer to ION 01629 for further information on this improvement. | 2019-04-24 |  | Bacteria
Supply System (All) | Central | 1003959 | 9462 | Supply System - Disinfection (secondary) - Incorrect ammonia dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water Medium (5) - EPI Medium (8) - NPI Medium (5) - SRP | 1). Online ammonia instruments to be installed and commissioned at Chambers Flat and Caloundra Street WQMFs. 2). Install Chemscan analyser at Gramzow Road WQMF. 3). Conduct Process Assessment of chambers Flat WQMF dosing systems. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-07-31 | In progress | 1). Instruments have been installed at Caloundra Street WQMF and Chamber Flat WQMF and are operating. All Alarms are programed and alarm. | 2019-04-24 |  | Bacteria
Mt Crosby East Bank WTP | Central | 1004019 | 9464 | Eastbank WTP - Raw Water Abstraction - Change in Raw Water Source Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. High (12) | 1). Undertake HBT Assessment for this site. Completed. Refer Rex D19/46266 Eastbank WTP - HBT Assessment 2017-18 - HBT Assessment Report July 2017 - June 2018. 2) Long term planning is underway for this WTP. | Risk Assessment | High | 12 | Senior DWQ Advisor - Continuous Improvement | 2028-12-31 09:00 | In progress | RA Review 12 Sep 24: - Undertake HBT Assessment for this site. [completed] - Long term planning is underway for the Mt Crosby WTPs - major WTP upgrade with additional barrier at West Bank enabling East bank to gofline during dirty water event peaks. MSC staged projects expected to improve interlock capabilities. Update as at 28 Oct 24: The Mt Crosby Resilience Improvements Strategic Assessment (Draft) identified the highest ranking option to address the resilience service need to be “1b Improve Existing: Install additional pathogen treatment barrier”. The Project Planning team, led by BH, will lead evaluation of this option. As the Strategic Assessment will very likely meet the requirements for a Strategic Business Case, we will move straight to preparation of a Preliminary Business case. We (BH) have prepared a draft Project Plan for preparation of the Preliminary Business Case which is located here: Record D24/265948: Mt Crosby Health based target pathogen barrier - Project Plan Project plan very roughly: • Preliminary business case – complete January 2026 • Detailed business case – complete January 2027 • Investment approval – June 2027 • Construction start July 2027 and complete December 2028 | 2019-04-24 09:00 |  | Protozoa
Mt Crosby East Bank WTP | Central | 1003977 | 9470 | Eastbank WTP - Coagulation - Flash mixer failure. Ineffective coagulation, flocculation and sedimentation, filter breakthrough and out of specification treated water. Medium (8). | 1). Installation of jet flash mixers for Sedimentation Basins No. 3 and 4. RTP ID 70 - Captured in the Facility Risk Review for Central - Sitting with ASP | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2023-12-29 09:00 | In progress | Refer to ION 01639 for further information. Installation of jet flash mixers for Sedimentation Basins No. 3 and 4. [Installed but never commissioned successfully - didn't work. Upgrades to chanels and riser in basin 3 have sufficiently improved mixing.] | 2019-04-24 09:00 | 2024-09-12 | Protozoa
Mt Crosby West Bank WTP | Central | 1004021 | 9506 | Westbank WTP - Raw Water Abstraction - Change in raw water source Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. Medium (8). | 1). Undertake HBT Assessment for this site; 2). Long term planning is underway for this WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2028-12-29 09:00 | In progress | 1). QMRA Mid Brisbane River study is currently underway. 2). Mid Brisbane River Water Supply Strategy Review is currently underway. Findings from this study will help inform long term planning requirements for Mt Crosby Eastbank and Westbank WTPs. Integrated Asset Management Plans - Mt Crosby to be completed by Oct 2022. | 2019-04-24 09:00 |  | Protozoa
Mt Crosby West Bank WTP | Central | 1003999 | 9507 | Westbank WTP - Disinfection (primary) - Contamination of service water distribution system due to main break or backflow incident. Potential contamination of treated water. Medium (8). | Conduct audit of the the service water to ensure that there are adequate measures in place to stop backflow events. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2027-07-30 | In progress | Audit completed. Recommendations to be delivered. Refer to ION 01642 for further information. Update 16/01/2024: ION 01642 (raised 2020) is still in the initiation phase and has not yet been assigned by the Change Coordinator. Risk to be discussed at the next HACCP Team meeting (Mar 24) to determine priority and moving things forward through the Change Coordinator. Review/Due date extended 3 years to allow for ION to progress and design/capital works to be undertaken through the subsequent ION stages. | 2019-04-24 09:00 |  | Bacteria
North Stradbroke Island WTP | South | 1003513 | 9562 | TNS-RW-A-6562 Risk Treatment: Undertake upgrades to Coagulation CCP. | TNS - Coagulation - Incorrect lime dose/ Incorrect Coagulant dose. For Herring Lagoon (pre lime): Underdose of lime into raw water main leading to: - low alkalinity for coagulation - incorrect dosed water pH Overdose of lime into raw water main leading to: - incorrect dosed water pH Risk Treatment (raised R.A review 2015 and DWQ Report to WTP Planning 2015 D14/149372): It is recommended that the coagulation process at NSI WTP is upgraded. This upgrade should consider: - paging of dosed water pH alarms to the Operator (Complete 2017) - interlock of WTP operation to dosed water pH alarms. This must include a full WTP HAZOP to ensure that all actions required to facilitate the interlock are identified and actioned, such that other unintentional adverse consequences are avoided (Complete Sep 2018) - feed forward control of coagulant dose - single set of alum dosing pumps (automatic changeover ‘duty’/’standby’ arrangement) that are capable of delivering the required dose across the range of flow and alum doses expected - flow meters on the alum dosing line, interlocked to WTP operation, such that the detection of no alum flow will shutdown the WTP - flow pacing of the alum dose to raw water flow meters on the inlet to each DAF train or installation of appropriate control such that the flow to the DAF basins is equal or known - relocation of the alum dosing points to immediately upstream of the inline rapid mixers currently work to improve process issues at TNS are being investigated - inc those in this RWA. these are planned to be fast tracked. time line extended 1 year capture project deliverables. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-12-31 09:00 | In progress | Update R.A 2017: 1) Operations South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included improvements to Lime System. Project cancelled Oct 2017. Project to be restarted. Update R.A 2018: 1) Interlocks programed Sep 2018 - Complete 2) APMP 2019 doc includes TNS: MCS Renewal: TNS: MCS Preliminary design for 20/21 and 21/22 3) APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Update 12/03/2020: timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 Update 12/03/2020: timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 | 2015-01-28 09:00 |  | Protozoa
North Stradbroke Island WTP | South | 1004017 | 9565 | TNS-RW-A-9565 Risk Treatment: Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF (oPRP). Under no circumstances would these bypasses be operated. | TNS - Dissolved Air Flotation (DAF) - Failure or incorrect operation of a bypass valve. Failure or incorrect operation of bypass from flash mixer to settled water main, or Failure or incorrect operation of bypass from supernatant return line to settled water main". | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2028-06-30 | In progress | Update R.A 2018: Raised RR workshop 2018. Update 25/03/2020: ION raised (ION01324): Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF oPRP). Under no circumstances would these bypasses be operated. DG ops do not run in direct filtration mode (never have). this is a significant project and not a focuss of the improvement plan for the next many years. if not supported by 2028 consider close out. | 2017-11-20 09:00 |  | Protozoa
North Stradbroke Island WTP | South | 1003273 | 10182 | TNS-RW-A-10182 Risk Treatment: Improvements to dosing, monitoring and alarming relating to poly system. Current impact of failure is minimal under normal conditions however when required, if poly dosing fails, subsequent processes are likely to fail. Improvements required. | TNS - Coagulation - Incorrect coagulant aid dose. For Herring Lagoon: Overdose of AN905 into inlet flocculation tank leading to ineffective coagulation or acrylamide > ADWG OR Underdose of AN905 into inlet flocculation tank leading to ineffective coagulation | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-12-12 | In progress | Update R.A 2018: APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime buildup in the reservoirs) for 22/23 and 23/24. Timelines under review. Update 11/03/2020: APMP 2019 doc includes TNS: Treatment Upgrades: Upgrade of DAF plant to improve automation, investigate filtration and chemical system improvements including pH correction (to mitigate lime build-up in the reservoirs) for 22/23 and 23/24. Timelines under review. Refer APMP code 20191125. REX Ref. D19/53107 note: poly is now LT20/DW20. DG to investigate and seek mitigations as appropriate. due date changed to reflect. | 2017-11-20 09:00 |  | Protozoa
Capalaba WTP | South | 1003453 | 10261 | TCP-RW-A-10261 Risk Treatment: Box gutter roof on Reservoir 1 roof subject to intrusion. | TCP - Disinfection (primary) - Contamination by animals - Contamination of chemical dosing chamber and/or treated water tanks | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2025-12-30 | In progress | Box gutter roof on Reservoir 1 roof subject to intrusion. Refer recommended improvements to Reservoir Condition Assessment Capalaba Reservoir 1 and Reservoir 2 2017 (GHD) Update R.A 2019: Southern Maintenance team in delivery of vermin proofing items Refer D21/83417 Capalaba WTP Facility Risk Register. Tracked in D22/48823 Southern Risk Forum: APMP 20200429 - Reservoir 1 Roof Renewal DG 28062023: due date extended as this work is associated with a res roof replacement that is scheduled to be delivered in September 2024. DG 28112024: roof replacement currently planned for delivery in 12m but will extend due date to end of 2025 and review then. | 2017-08-15 09:00 |  | Viruses
Molendinar WTP | South | 1003023 | 10321 | TMO-RW-A-10321 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. | TMO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatment capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update October 2019: Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81738 Molendinar WTP - HBT Assessment 2018/19 - Draft Report. Note this does not incorporate review of source water category. Rex Ref. D19/81738. Update 21/07/2020: Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled for August 2020 Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. | 2017-11-03 09:00 | 2024-07-22 | Protozoa
Molendinar WTP | South | 1003035 | 10339 | TMO-RW-A-10339 Risk Treatment: WTP shutdown takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Under high flow conditions this is not insignificant. Review and optimise interlock sequencing. Develop recovery plans where required if impacts to CCPs during high flow conditions require recovery. | TMO - Whole of System - Loss of control system. Loss of SCADA system or loss of PLC leading to impacts to treated water quality Risk Treatment (raised R.A 2017): Raw water pump shut down takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Review and optimise interlock sequencing. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update R.A 2019: WTP shutdown takes 20 mins because raw water valve takes 20 mins to close due to functionality set. This improvement may not be possible until new valve installed. Update R.A 2021: Being actioned under Risk Wizard incident 26864 HACCP critical limit exceedance no coag flow. HACCP crash stop is 12 mins. Detail provided in 2021 RA shows that the plant HACCP interlock for coag >+- 25% discrepancy in flow is 12 mins. this addresses the risk and no further action is required. | 2017-11-03 09:00 | 2024-07-22 | Protozoa
Beaudesert WTP | South | 1120120 | 10351 | TBE-RW-A-10351 Risk Treatment: Tag out bypass to ensure clear identification of valve and prevent accidental use. | TBE - Flocculation and Settling - Failure or incorrect operation of a bypass valve Failure or incorrect operation of a clarifier bypass valve. | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | Not yet started | Update R.A 2020: increased to Risk Treatment due to relocation of alum dosing after the aerator this bypass is now a raw water to filtered water bypass which is an unacceptable risk. Remove bypass pipework to create air gap. Currently two closed valves in place. Check if maintenance can remove section of pipework between valves as interim until blanking plates can be installed via ION process. 29/9/2022 update: We have an alum dosing point into the aerator to allow for operational flexibility including direct filtration. Consideration of removing the bypass is given as soon as SW pipeline is completed. 28/2/2024 update: Bypass valve is tagged out. No change - risk not reduced until removed/blanked. Added to Protecht. | 2017-06-07 09:00 | 2024-02-28 | Protozoa
Hinze Dam WTP | South | 1003809 | 10397 | THZ-RW-A 10397 Risk Treatment: Although this is not known to have occurred at Hinze Dam WTP there is occurrences of coag dosing pipe breakages at other WTPs. There is currently a coagulant flow switch interlocked to WTP operation however coag flow monitoring interlocked to WTP operation is required. | THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2025-12-31 09:00 | In progress | Update R.A review 2017: Confirmed as viable WTP and will continue operating. Project will be pursued by Process Improvement Specialists based on current understanding that WTP will remain for the foreseeable future. To be included in Minor Works upgrade 17/18. Note Control System is very limited in terms of adding any further alarms or monitoring. Sludge upgrade project would trigger upgrade of PLC. Update R.A review 2019: Not delivered at time of R.A. Update 9/07/2021: Sen. DWQ Advisor Sth: wait for outcome of Moogerah and Maroon Dam coag flow meter projects. Similar flow rate and project currently in delivery. Issues with measuring such low flow rate may or may not be overcome. Update 21/09/2021: Senior DWQ Advisor Continuous Improvement to escalate ION184 or raise a new ION to install ACH coag flow meter. In the short term identify options to get existing signals available on the ACH dose pump into SCADA that can be used as the HACCP critical limit to interlock the WTP. Update Hinze Dam WTP HACCP Wall Chart and HACCP Plan Validation 3.2 to document signal in use for this HACCP critical limit. Update 29 NOV 21: Date extended 12 months as this work has not yet included in any program. Management of this risk to be reviewed on-site and then discussed at next HACCP team meeting (Mar 22). Due date extended 12 months to allow for changes in DWQ advisor staff (new and acting arrangements). Will be reassigned once DWQ advisor south position is stable. investigate current condition, confirm need for flow meter over switch to control risk (both should indicate flow when offline - DG to investigate) and facilitate flow switch replacement for flow meter if needed. date changed to reflect. | 2015-03-23 09:00 |  | Protozoa
Hinze Dam WTP | South | 1003527 | 10398 | THZ-RW-A-10398 Improvement Opportunity: Static mixer post ACH dose point would improve coagulation and clarifier performance. | THZ - Coagulation - Inadequate mixing Lack of mixing resulting in poor floc formation resulting in filter breakthrough | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-12-31 09:00 | In progress | Update R.A review 2017: Confirmed as viable WTP and will continue operating. Project will be pursued by Process Improvement Specialists based on current understanding that WTP will remain for the foreseeable future. To be included in Minor Works upgrade 17/18. Process Engineers to perform assessment of ACH mixing at Hinze Dam WTP due to lack of static mixer or mechanical flocculator to ensure mixing of coagulant (batched with water) is sufficient. Note Control System is very limited in terms of adding any further alarms or monitoring. Sludge upgrade project would trigger upgrade of PLC. Update R.A review 2019: refer APMP 2020. | 2015-03-23 09:00 |  | Protozoa
Moogerah Dam WTP | South | 1003989 | 10411 | TMG-RW-A 10411 Risk Treatment: HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP requires additional protozoa removal (i.e UV). | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Deterioration of Granular Activated Carbon (GAC) media resulting in inadequate removal of TO (primarily) and organics and manganese (secondary) due to: exceed GAC lifespan Medium (8) (TMG-15) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2027-05-31 | In progress | Update R.A 2020: Conservative assessment at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP will require additional protozoa treatment (i.e UV). Update 2020: ION01470 raised for the installation of UV | 2017-09-06 09:00 |  | Protozoa
Moogerah Dam WTP | South | 1003639 | 10413 | TMG-RW-A 10413: Risk Treatment: Investigate opportunities to address clarifier sludge build up requiring manual draining and hose out on a regular basis. | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-16) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2025-02-28 09:00 | In progress | Update R.A 2020: P.E to investigate replacement or modification of clarifier. Reference P.E action item 2024: Clarifier flow valve needs to be automated and to be manged over SCADA to optimize the level at the settled water tank during normal operations but particular during start up and back wash processes. Avoid manual handling. Operators don’t have to be onsite to adjust clarifier inlet flow. Remains open. | 2017-09-06 09:00 |  | Protozoa
Kooralbyn WTP | South | 1003677 | 10446 | TKO-RW-A 10446 Risk Treatment: Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146. Additional protozoa treatment required i.e UV Disinfection | TKO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TKO-15) TKO - Coagulation - Incorrect coagulant dose Underdose of alum resulting in contaminated treated water including incorrect dosed water pH Medium (8) (TKO-15) TKO - Coagulation - Incorrect CO2 dose Underdose (absence) of CO2 causing high dosed water pH resulting in contamination of treated water Medium (8) (TKO-15) TKO - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) (TKO-15) TKO - Flocculation and Settling - Failure or incorrect operation of a bypass valve Failure or incorrect operation of a clarifier bypass valve Medium (8) (TKO-15) TKO - Media Filtration - Filter breakthrough Filter breakthrough Medium (8) (TKO-15) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2025-04-30 09:00 | In progress | Raised Kooralbyn WTP - pathogen treatment assessment report June 2015 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19. Update R.A 2020: PID02914 TKO: UV Disinfection Upgrade in APMP for delivery 21/22. Additional need to confirm if filters have individual or combined filter monitoring as this can drop the LRV. There are four cells and two filtered water turbidity instruments. Refer TKO-RW-A 11740 Risk Treatment: determine filtered water turbidity assessment for HBT assessment. E.g four filters or two filters. | 2017-07-19 09:00 |  | Protozoa
Mudgeeraba WTP | South | 1003037 | 10476 | TMU-RW-A-10476 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. | Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatement capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. TMU - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water (HUI LND) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-07-31 09:00 | In progress | Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81746 Mudgeeraba WTP - HBT Assessment 2018 - Draft Report. Note this does not incorporate review of source water category. Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. | 2017-10-27 09:00 | 2024-07-22 | Protozoa
Mudgeeraba WTP | South | 1003049 | 10485 | TMU-RW-A-10485 Risk Treatment: Undertake improvements to improve filter performance for filters which don't consistently achieve protozoa LRV log reduction credits due to filter ripening spikes. | Risk Treatment (Raised HACCP internal audit 2014): Review of filtration performance at Mudgeeraba WTP to identify inadequacies to Planning. Following the filter optimisation project the individual filtered data will need to be assessed. If operational changes do not improve filter performance then capital improvements such as addressing the filter to waste restriction or an additional process step (eg UV) should be considered as log removal credits under the Health Based Targets standard cannot be applied based on the current HACCP limits. TMU - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) when required | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2026-01-31 | In progress | Update R.A 2017: Further quantitative assessment in Pathogen Treatment Assessment for Mudgeeraba WTP performed June 2015 (D15/116852) confirmed filters don't meet performance expectations on ripening and overall don't meet the HBT filter performance targets for 3.0 log protozoa reduction. Process Engineering team are preparing to trial an extended terminal sub-fluidisation wash (ETSFW) sequence in the filters to determine whether this improves the ripening issues. D17/120476 Mudgeeraba (TMU) Long Term Planning Report has also captured that for individual filters, ripening times are a significant performance issue. Update R.A 2019: HBT assessment done for filter performance from Jan to Dec 2018 at 1 min interval as part of process improvement project 2018/19. Months where filters didn’t achieve the LRV was mainly due to incidents related to filter ripening spikes post backwash. ETSW implementation project is underway which will help prevent ripening spikes. Months where filter didn't reach 3.5 or 4.0 log it was due to filter ripening. Update R.A 2021: ETSW implementation ongoing | 2017-10-27 09:00 |  | Protozoa
Mudgeeraba WTP | South | 1003051 | 10486 | TMU-RW-A-10486 Improvement Opportunity: Develop filter performance reports using continuous online data against the HBT criteria to assist in informing WTP Planning. | Improvement Opportunity (raised R.A review 2017): Develop filter performance reports using continuous online data against the HBT criteria to assist in informing WTP Planning Long Term Planning Report. TMU - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) when required | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2026-01-31 | In progress | Update R.A 2019: As part of this FY projects, the PE team is engaged in Central Historian eDNA project trails, where HBT reporting and WTP process performance reporting will be trialled. The filter performance will be included along with other processes within the WTP reporting. Update October 2019: PE has undergone a HBT assessment currently in Draft form. Rex Ref. D19/81746. A. HBT assessment done for filter (ONLY) performance from Jan to Dec 2018 at 1 min interval as part of process improvement project 2018/19. Months where filters didn’t achieve the LRV was mainly due to incidents related to filter ripening spikes post backwash. ETSW implementation project (similar to Molendinar) is underway which will help prevent ripening spikes. B. As part of this FY projects, the PE team is engaged in Central Historian eDNA project trails, where HBT reporting and WTP process performance reporting will be trialled. The filter performance will be included along with other processes within the WTP reporting. Update 2021: Project ongoing. Planned for next financial year. | 2017-10-27 09:00 |  | Protozoa
Rathdowney WTP | South | 1003811 | 10499 | TRA-RW-A 10499 Risk Treatment: Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Refer D15/114408. | TRA - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) TRA - Supernatant Return - Superntatnt return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose Medium (8) TRA - Coagulation - Incorrect coagulant dose Underdose of ACH (dosed neat) including loss of carrier water Or Ineffective coagulation due to elevated pH High (12) TRA - Coagulation - Incorrect coagulant dose Overdose of ACH (dosed neat) Medium (8) TRA - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) TRA - Media Filtration - Filter breakthrough Fitler breakthrough Medium (8) TRA - Media Filtration - Build up of solids leading to elevated turbidity High turbidity filtered water from backwash water tank used to backwash filter leading to filter breakthrough when filter back online Medium (8) | Risk Assessment | High | 12 | DWQ Advisor - Continuous Improvement | 2025-12-31 | In progress | Refer D15/114408. Project to commence 17/18. Refer APMP 2017 capital planning register. Update R.A 2020: PID02915 TRA: UV Disinfection Upgrade in APMP for delivery 21/22. PLEASE DO NOT CLOSE THIS ACTION UNTIL IMPROVEMENT HAS BEEN DELIVERED ON SITE. Update 2022 RA: UV is in delivery program. | 2017-10-27 09:00 |  | Protozoa
Supply System (All) | Central | 1003957 | 11134 | Heinemann Road Reservoirs - Add new additional chlorine instruments to individual reservoir outlets 2 and 3. | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-07-30 09:00 | In progress | Now Part of the Facility Risk Review process. RTP205. This action is to remain open until the RTP is closed for tracking purposes as this improvement is now flagged in the Supply System HACCP Risk Assessment. | 2019-12-19 00:46 |  | Bacteria
Supply System (All) | Central | 1003669 | 11201 | Heinemann Road Reservoirs - Locate drawings of the chemical dosing arrangement, the sample return water or instrument water draw arrangements in Reservoirs 2 & 3. If they are not available,new drawings need to be done. | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-03-31 09:00 | In progress | ION1382 raised to address unavailability of drawing - not in their scope - Regional Ops Manager approved altering ER7 to address PID This action is to remain open until completed as it is being used for tracking purposes as this improvement is now flagged in the Supply System HACCP Risk Assessment. | 2020-01-09 09:00 |  | Bacteria
Supply System (All) | Central | 1003197 | 11202 | Heinemann Road Reservoirs - Locate documentation detailing chlorine dosing control in Reservoirs 2 & 3. If documentation can not be located, new documentation is to be developed. | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 | In progress | ION1382 raised to address unavailability of drawing - This action is to remain open until completed as it is being used for tracking purposes as this improvement is now flagged in the Supply System HACCP Risk Assessment. This information needs to be retrieved out of the archives. Timeframe has been extended to allow this to be done. | 2020-01-09 09:00 |  | Bacteria
Amity Point WTP | South | 1003695 | 11280 | TAP-RW-A-11280 Risk Treatment: Introduce protozoa treatment at Amity Point WTP to meet Category 3 minimum pathogen log reduction requirements. | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2025-06-30 | In progress | Raised R.A 2017: Undertake Pathogen Assessment of NSI Township WTPs and review of preventative measures and monitoring for managing risk of abstraction of contamination groundwater is required including condition of bore casings, bore location in relation to flood level, condition of seals on above ground assets. Update R.A 2019: Based on having a shallow aquifer and, other than the Seqwater bores, having no control over the confines of the aquifer there has to be an assumed level of interaction whether it be continuous or intermittent. Therefore Amity Point WTP has been assessed as Source Category 2 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 3.0 LRV; protozoa 2.5 LRV under WSAA HBT Manual. Refer Risk Treatment Disinfection (primary) for improvements to C.t (TAP-RW-A-TBC) Protozoa treatment required in the form of UV disinfection to achieve protozoa 2.5 LRV. Update 26/03/2020: Attached email with work order inspections checklists DG update 2024: the Source water assessment determined the catchment is a category 3 and therefore will require greater treatment. | 2017-11-21 09:00 |  | Protozoa
Amity Point WTP | South | 1003937 | 11281 | TAP-RW-11281 Risk Treatment: Update HACCP plan to include oPRP for monitoring Bore asset integrity. Current Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) includes steps 19-21 to check for leaks on pipeline assets which can be referenced. Install online raw water turbidity monitoring to detect bore integrity failure and prevent impacts to CCT from turbidity. | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2026-06-30 | In progress | Raised R.A 2017: Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity (raised HACCP internal audit 2016) Upgrade R.A 2019: Ingress issued identified. ION 00237 raised. Identified Issues resolved Jan 2019 by Operations Maintenance team. Ongoing inspections of bores (and all WTP assets) to be included in CIS routine work orders. Inspection criteria to be specific as per reservoir inspections checklist. Progression of UV disinfection to treat for hazards is preferable to installing additional online monitoring as standard online monitoring techniques is unlikely to be sensitive enough to detect a surface hazard and ground water interaction. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Update 15/05/2020: ION01366 has been raised for installing on-line turbidity monitoring of the combined raw. No updates / not yet commenced - date extended to allow for annual review until completed or closed out/risk tolerated. Reassigned to new DWQ Advisor South - DG | 2017-11-21 09:00 |  | Protozoa
Amity Point WTP | South | [not transferred to Protecht] | 11284 | TAP-RW-A-11284 Undertake Disinfection (primary) CCP C.t improvements to achieve minimum bacteria and virus log reduction requirements at Amity Point WTP point of supply. | Note: C.t calculation currently includes councils town reservoir located near Amity WTP. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | Completed | Update R.A 2015: C.t is currently not met at the BSP. WTP Planning preparing a draft options assessment report. Update R.A 2017: Concept design complete to achieve C.t and BSP. Consultant engaged. Preliminary design complete. Update R.A 2019: Amity Point WTP has been assessed as Source Category 2 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 3.0 LRV under WSAA HBT Manual. Minimum C.t 8 mg.min/L required to achieve 3.0 LRV virus. PID01902 TAP: Upgrade CWS Tank Capacity - improve contact time and instrumentation for disinfection in delivery for 20/21 21/22. Ref APMP 2019. Update 26/03/2020: Amity Point C.t Options being reviewed. Stakeholder meeting 23/03/2020. Lead WTP Planning leading. Contact pipe expected to be installed as part of disinfection upgrade to be completed during 23/24 year. Reassigned to new DWQ Advisor south - DG 2024 Project complete – CT pipe install and SCADA now included dynamic CT CL. | 2017-11-21 09:00 | 2024-05-24 | Viruses
Dunwich WTP | South | 1003813 | 11292 | TDU-RW-A 11292 Risk Treatment: Undertake Health Based Target assessment of NSI Township WTPs and upgrade WTPs accordingly. | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2023-12-31 09:00 | In progress | Undertake Pathogen Assessment of NSI Township WTPs and review of preventative measures and monitoring for managing risk of abstraction of contamination groundwater is required including condition of bore casings, bore location in relation to flood level, condition of seals on above ground assets Update R.A 2019: Based on having a shallow aquifer and essentially no control over the confines of the aquifer there is an assumed level of interaction whether it be continuous or intermittent. There is also point source hazards such as septic systems on Rainbow Cres. Therefore Dunwich WTP, when using Bore 1, 2, 4 is likely to be Source Category 3 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 4.0 LRV; protozoa 3.5 LRV under WSAA HBT Manual however this assessment has not formally been done. This would likely increase to Category 4 if Bore 3 were to be reinstated or based on other known point source risks such as septic system and cattle. Refer Risk Treatment Disinfection (primary) for improvements to C.t. Protozoa treatment required in the form of UV disinfection to achieve protozoa LRV. Update 26/03/2020: Pathogen log shortfalls being addressed under TDU – Dunwich WTP Secondary Disinfection Preliminary BC ADWG method for SWA undertaken in 2023 and confirm source as Category 4. project is in delivery to increase treatment accordingly. due date extended to after project expected due date - close once project has been completed. | 2017-11-21 09:00 | 2024-11-22 | Protozoa
Dunwich WTP | South | 1003815 | 11293 | TDU-RW-A 11293 Risk Treatment: Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity to detect contamination of aquifer due to bore failure or other pathway. | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2025-12-31 | In progress | Raised R.A 2017: Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Upgrade R.A 2019: ION raised. Ingress issued fixed on production bores 2018/2019? Ongoing inspections to be addressed. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Period inspections of ingress Closed. Update 15/05/2020: ION01367 has been raised to install online raw water turbidity monitoring for the purpose of real time detection of contaminated ground water that exceeds treatment capacity. facility risk review has stated "Score is too low to bring into program". raw water monitoring is not likely to detect contamination. due date extended by 2 years. i will discuss with Jop and close if appropriate. - following discussions with Jop we determined the following - Dunwich WTP is in the process of being upgraded to treat category 4 source water. this will be delivered in the coming 2 years. at this point raw water monitoring will not be required. after delivery close out action. | 2017-11-21 09:00 |  | Protozoa
Dunwich WTP | South | 1003929 | 11296 | TDU-RW-A 11296 Risk Treatment: install solid adequate cover on top of media filter. | TDU - Media Filtration - Contamination by ingress Contamination of Media Filter | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2026-06-15 | In progress | DG investigating current condition. - due date pushed back to january. DG progressing but need more time due to staff away, date changed to march. Given current works focusing on limestone bed before the filter this is unlikely to progress until after the limestone work and the due date has been changed to reflect this. | 2019-08-07 09:00 |  | Viruses
Dunwich WTP | South | 1004668 | 11297 | TDU-RW-A-11297 Risk Treatment: Investigate options to meet C.t. Will need to liaise with Redlands due to 'change' that customers will receive in free chlorine levels. Options could include increasing min res level. If not able to be reasonably achieved operationally then issue to be handed over to Planning. | TDU - Disinfection (primary) - Insufficient C.t Insufficient C.t due to: - low chlorine - high pH due to incorrect Stabilisation pH control - insufficient contact time - high treated water turbidity | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | Completed | Update R.A 2019: WTP Planning developing Dunwich WTP Pathogen Contamination Mitigation Preliminary Business Case to address pathogen treatment requirements. Update 26/03/2020: Virus and bacteria log shortfalls being addressed under TDU – Dunwich WTP Secondary Disinfection Preliminary BC CT is being met onsite. note: additional treatment is being installed for SWA category change and increase LRV requirements. | 2015-12-02 09:00 | 2024-05-24 | Viruses
Point Lookout WTP | South | 1003965 | 11308 | TPL-RW-A-11308 Risk Treatment: Remove CCT bypass | Risk Treatment (raised HACCP Team meeting 2016): Bypass is thought to exist on outlet of 45 kL tank bypassing treated water reservoir. Bypass existence and condition requires confirmation and, if confirmed, removal. Refer REX 724654 Drawing I-DWG-TPL-601 PID Treated Water Storage. TPL - Disinfection (primary) - Failure or incorrect operation of a bypass valve Failure or incorrect operation of treated water reservoir bypass (dosed water to balance tank to treated water pumps) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2026-09-30 09:00 | In progress | Bypass exists on outlet of 45 kL tank bypassing treated water reservoir. Refer REX 724654 Drawing I-DWG-TPL-601 PID Treated Water Storage. Update R.A 2019: Bypass valve closed 2019. ION raised for valve and intermediate balance tank to be removed. ION00430 No further project work to date - due date extended for annual review until completed or risk tolerated/closed out. Reassigned to new DWQ Advisor South - Dan Guinea DG 28062023: Due date extended in response to resourcing. DG This improvement will take considerable work and is of low priority. DWQ will work to include with plant augmentation in medium term. | 2017-11-21 09:00 |  | Viruses
North Pine WTP | North | 1003685 | 11390 | Water treatment capability inadequate for seasonal taste and odour compounds | The existing PAC (Powdered Activated Carbon) system at North Pine Water Treatment Plant struggles to effectively treat elevated levels of 2-methylisoborneol and geosmin (>20ng/L combined) during warm months when cyanobacterial blooms occur in Lake Samsonvale. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress | Improve North Pine PAC system capacity and effectiveness through long-term planning in Asset Portfolio Management Plan (APMP). (Note: While cyanobacteria blooms present a low risk (2) for treated water contamination, the taste and odour compounds present a medium risk (8) requiring attention) | 2020-02-11 09:00 |  | Cyanotoxins
Noosa WTP | North | 1003807 | 11398 | Coagulation optimisation and control inadequate | Lime and alum dosing control systems, particularly during startup and lake-only water scenarios, are not optimized for effective coagulation, potentially impacting cryptosporidium removal capability | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress | 1. Investigate lime and alum control with focus on startup and lake-only water 2. Investigate polymer as flocculation/settling aid 3. Install alum dosing flow meter to verify doses 4. Investigate CO2 dosing for reliable calcium carbonate formation 5. Include reactivator importance in coagulation pH validation and control | 2019-07-17 09:00 |  | Protozoa
Noosa WTP | North | 1003831 | 11401 | Filter performance issues creating risk of breakthrough | Current filtration monitoring and control systems are inadequate to prevent potential filter breakthrough events, posing a risk for cryptosporidium treatment compliance | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress | 1. Install appropriate instrumentation for filter monitoring and control 2. Implement filter to waste capability (completed 2021 - operational on timers) 3. Investigate polymer dosing as filter aid (completed 2021) 4. Add additional cryptosporidium barrier to meet required log credits under HBT assessment 5. Conduct tier 1.5 assessment/QMRA (<2 years from July 2021) (in progress) | 2019-07-17 09:00 |  | Protozoa
Amity Point WTP | South | 1002795 | 11604 | TAP-RW-A-11604 Improvement Opportunity: Introduce dynamic C.t monitoring in SCADA. | TAP - Disinfection (primary) - Insufficient C.t Insufficient C.t resulting from: - low chlorine - insufficient contact time - high pH due to dosed filtered water caustic overdose - high treated water turbidity | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-06-30 09:00 | Completed | Process Engineering have a schedule for this work across the southern region completing three(+) WTPs per year. Date extended for annual review until completed. Reassigned to new DWQ advisor south - DG Update 17-01-2024: Dynamic Ct implementation is done as part of the TAP Ct improvement project. The construction of new Ct pipeline commences on the 31st of Jan 2024. Mipac (Consultant) are doing the control systems implementation. Update 24-06-2024: Dynamic Ct implementation has been completed as part of the TAP Ct improvement project. Section 6.4 within the FD Part-A (B-REP-TAP-001) describes the Ct monitoring along with calculations. | 2019-06-03 09:00 | 2024-06-24 | Viruses
Kooralbyn WTP | South | [not transferred to Protecht] | 11738 | TKO-RW-A 11738 Risk Treatment: introduce low raw water pH HACCP action limit to detect change in pH when on Bigfoot Lagoon which could indicate a change in source water conditions requiring a re-assessment of coagulation chemical dosing. | TKO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TKO-16) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-05-31 09:00 | Completed | Date extension due to caustic dosing installation. Monitoring of corrective actions will be undertaken once dosing is operational. 7/5/2024: Data to date confirm that controls are adequate and oPRP is managed well by operations. Project to install acid dosing to reduce sludge/ waste in place to aid in pH correction process. The intent is to review limits when acid dosing comes online. | 2020-05-20 09:00 | 2024-05-07 | Protozoa
Kooralbyn WTP | South | [not transferred to Protecht] | 11740 | TKO-RW-A 11740 Risk Treatment: determine filtered water turbidity assessment for HBT assessment. E.g four filters or two filters | TKO - Media Filtration- Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (8) (KOO13) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | Completed | Check with Process Engineering how HBT assessment has been undertaken. If two filters with filtered water turbidity monitoring on each filter then these are considered individually monitored filtered. If four filters with combined filtered water turbidity monitoring for two filters then these are considered combined monitoring. Check how Beaudesert and Capalaba WTP filters have been assessed under HBT framework as they are multi-celled filtered with single filtered water turbidity analyser. Update Kooralbyn HACCP plan and risk assessment with LRV for Media Filtration CCP accordingly. | 2020-05-20 09:00 | 2024-05-28 | Protozoa
Image Flat WTP | North | 1003871 | 11747 | Raw water quality deterioration during rain events exceeds treatment capability | Plant operability challenges, particularly with coagulation and filtration barriers, increase risk of treatment failure during high contaminant loads from catchment wash-in events. All sources are HBT Category 4, limiting mitigation options. | Risk Assessment | High | 12 | Senior DWQ Advisor - North | 2026-04-27 09:00 | In progress | 1. Conduct quantitative/tier 2 HBT assessment 2. Install real-time water quality and flow monitoring of raw water sources for optimal source selection 3. Upgrade lime dosing system to handle variable color and alkalinity (completed) 4. Improve alum mixing 5. Add additional protozoa treatment barrier to address HBT tier 1 shortfall | 2020-04-27 09:00 |  | Protozoa
Ewen Maddock WTP | North | 1003601 | 11760 | Raw water quality deterioration during rain events exceeds treatment capability | Treatment process capacity may be insufficient to handle elevated contaminant loads during rainfall events in catchment, requiring risk assessment validation | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress | Undertake HBT Tier 1.5 Assessment to confirm risk | 2020-01-17 09:00 |  | Protozoa
Ewen Maddock WTP | North | 1003607 | 11762 | Pre-lime dosing system configuration creating coagulation reliability risks | Current pre-lime system uses raw water for service water and makeup, potentially compromising dosing reliability and coagulation performance | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress | Review pre-lime dosing system to include: Change service water source from raw to treated water Change lime makeup water to plant service water Install pressure switches on lime makeup water Implement auto shutdown on lime system failure (completed) | 2020-01-17 09:00 |  | Protozoa
Ewen Maddock WTP | North | 1003621 | 11763 | Separated water return system lacks flow control | Return water system operation is not optimized, potentially affecting treatment process stability | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress | Install VSD for separated water return pumps on return water tank | 2020-01-17 09:00 |  | Manganese
Ewen Maddock WTP | North | 1003651 | 11764 | Stormwater ingress risk to supernatant return | Potential for stormwater contamination of process water via supernatant return system | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress | Install online turbidity and pH instruments on supernatant return line | 2020-01-17 09:00 |  | Protozoa
Ewen Maddock WTP | North | 1003655 | 11766 | BAC filter contamination risk requires additional barriers or vermin proofing | Risk Treatment (raised R.A 2020): Investigate further prevention of post barrier contamination to the top of the BAC filters (such as ingress, animals, etc). Covering BACs completely is challenging because of the residual ozone present in the atmosphere. Ozone is heavier than air and invisible to the eye. People and animals can become intoxicated quickly if there is too much ozone in the air. However, there is a potential for contamination of the water on top of the BAC filters (water that has just been ozonated). BAC filters do not provide any log reduction credits for protozoa and as such effectively, anything that contaminates the ozonated water prior to BAC filtration could potentially make its way through to the treated water and the public. There are no further barriers to protozoan. Chlorine disinfection does not get any impact on protozoan parasites. Therefore it is imperitive to - ensure there is no ingress points to the ozonated water prior to BAC and provide an additional treatment barrier for protozoa downstream of the BAC. (not in place yet. but speaking to extra protozoan barriers ala other protozoan limiting hazard risk treatments, as well as reducing the likelihood of introducing contamination to the BACs) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-01-17 09:00 | In progress | 1. Investigate prevention methods for post-barrier contamination (complete) 2. Assess ingress points for post-barrier contamination (complete) 3. Assess ingress points to ozonated water (completed) 4. Add protozoa treatment barrier downstream of BAC (not required/need changed): 5. Implement contamination prevention measures (completed - BAC filters now covered and vermin proofed). | 2020-01-17 09:00 | 2024-11-27 | Protozoa
Maroon Dam WTP | South | [not transferred to Protecht] | 11773 | TMD-RW-A 11773 Risk Treatment: Investigate causes and opportunities to prevent alum dosing system blockages. | TMD - Coagulation - Incorrect coagulant dose Underdose of alum due to: - alum dose pump fault/failure - alum dosing line blockage/split - inadequate mixing - low pH in raw water Medium (8) | Risk Assessment | Medium | 8 | DWQ Advisor - Continuous Improvement | 2024-02-29 09:00 | Completed | P.E investigating options to address mixing/blockage issue e.g swap out devices. Update 28/09/2020: PE unable to progress at this time. Operations are trialling a double contained tubing with an expected longer shelf life. 22/02/2024: Alum dosing has an interlock on low/ no dosing. Alum blockages occur at times but alum dosing (all dosing equipment) are managed through plant inspections. Double contained tubing protects dosing lines from vermin damage. | 2019-03-08 09:00 | 2024-02-22 | Protozoa
Mt Crosby East Bank WTP | Central | 1003797 | 12001 | Eastbank WTP - Supernatant Return - Supernatant return quality exceeds treatment capacity. Supernatant return volumes exceed treatment capacity leading to Protozoa in the treated water. High (12) | 1). It should be determined if it would be advantageous to fit interlocks such that the supernatant pumps cannot run when the raw water pumps are offline or if the turbidity critical limit is triggered - Technical Specialist has identified that this would be advantageous. 2). Consideration should be given to undertaking a mass balance of polyacrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for acrylamide monomer in the treated water. 3). VSDs is to be installed on the supernatant return pumps which in conjunction with raw water flow meters will facilitate improved control to ensure that the supernatant to raw water ratio does not exceed 10% of the raw water flow rate. 4) Make modifications and improvements to the current supernatant return process to minimise the impact to stage 3 and 4 basins. | Risk Assessment | High | 12 | Senior DWQ Advisor - Continuous Improvement | 2027-12-31 | Not yet started | Refer to Eastbank Solids Handling Upgrade - CIS project code C201005427 for further information. DWQ RA Review 12 Sep 24: - It should be determined if it would be advantageous to fit interlocks such that the supernatant pumps cannot run when the raw water pumps are offline or if the turbidity critical limit is triggered - Technical Specialist has identified that this would be advantageous. Update: Been capturedEast Bank Solids Handling Upgrade Project - Unable to waste superntant return water to Holts Hill storages. Only centrate. Exception is if temporary pumping set up is established. No fixed pumps and pipework. Important to be able to waste supernatant during extreme dirty water events when treatment is difficult. - Consideration should be given to undertaking a mass balance of polyacrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for acrylamide monomer in the treated water.[Checked with BH - change in floc aid from SEP to PWG products may have resolved this issue.] - VSDs is to be installed on the supernatant return pumps which in conjunction with raw water flow meters will facilitate improved control to ensure that the supernatant to raw water ratio does not exceed 10% of the raw water flow rate. - Two train project to make modifications and improvements to the current supernatant return process to minimise the impact to stage 3 and 4 basins. | 2020-07-15 09:00 |  | Protozoa
Somerset Dam WTP | Central | 1003279 | 12012 | Somerset WTP - flocculation and settling Inadequate mixing; Carry over of floc, sludge or algae in settled water; Build up of solids leading to elevated turbidity; Anoxic sludge Medium (8). | - Installation of an inline mixer d/s of alum dose point to improve mixing for coagulation - Improvement to flocculation zone/energy - Improvement to sludge withdrawal from clarifier, particularly flocculation zone (including automation of sludge withdrawal) - Improvements to variable intake to allow this to be operated - Addition of pre-filter chlorination for manganese removal (if variable intake modification does not see sufficient improvement in manganese levels) - EIC upgrade to improve visibility and automation. The upgrade will include level instruments, filter DP, valve automation, and better control of VSD raw water and filter feed pumps (allowing flow to be matched). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-09-30 09:00 | Completed | Coagulation-flocculation improvements have been completed by Process Engineering. Intake improvements (pump replacement has been completed. No further work proposed for valves etc. In-line mixer, EIC upgrades etc yet to be determined - date extended 12 months for future review. Update 31/05/2024: Work completed. Action can be closed. | 2019-07-16 09:00 | 2024-05-31 | Protozoa
Supply System (All) | Central | 1004025 | 12031 | Supply System - Reservoir - Elevated water age. Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. Medium (8) | 1. Review options around performance (efficient mixing), replacement and installation of reservoir mixers in Supply System. 2. Investigate installation of mixer at Mt Cotton to assist with water age issues. Common Inlet/Outlet. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2028-12-29 | In progress | 1. Refer to ION 01413 for further information. The following RTPs are noted in the Supply System Facility Risk Review for Mixers: - Aspley Reservoir Mixers - RTP 28 - Wellers Hill Reservoir Mixers - RTP 124 - Alexandra Hills Reservoirs 1, 4, 5 Mixers - RTP 126 - Narangba Reservoir 2 Mixer - RTP 219 - Heinemann Road Reservoirs 2, 3 and Alexandra Hills Reservoirs 1, 3, 4, 5 Mixers - RTP 313 04/12/24 - Work underway to install Wears mixers in Heinemann Road Reservoir 2 and 3. Failed Pax mixers have been removed. Reservoir cleaning for Res 2 and 3 is planned for mid Jan 2025 with new mixers being installed after that. Strategy meeting on mixer replacement going forward is planned for 11 Dec 2024. | 2020-07-17 09:00 |  | Bacteria
Supply System (All) | Central | 1003741 | 12033 | Supply System - Disinfection (secondary) - Incorrect chlorine dose Under dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water. High (12) | NPI Supply Zone 1. Conduct Process Assessment of Noosa Connection dosing system. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2025-07-01 09:00 | Not yet started | 04/12/24 -This site has a lower priority than some other sites so will be done after those. | 2020-07-20 09:00 |  | Bacteria
Supply System (All) | Central | 1003067 | 12035 | Supply System - Disinfection (secondary) - Incorrect ammonia dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water. Medium (8) | NPI Supply Zone Conduct Process Assessment of Caloundra Street WQMF dosing systems. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 | In Progress | 26/07/24 - Assessment of Caloundra Street is well underway and is expected to be completed in September 2024. Fortnightly progress meetings are being held with stakeholders. Time frame is being extended to allow for completion of report. 08/10/24 - Finalization fo this report has been delayed due to the commissioning of the SWP. Timeline extended. | 2020-07-20 09:00 |  | Bacteria
Hinze Dam WTP | South | 1003291 | 12154 | THZ-RW-A-12154 Risk Treatment: Instigate dial out alarm if raw water flow detected and WTP not running to detect untreated raw water flows entering WTP. | THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water Medium (8) (HNZ-5) | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-12-12 | In progress | SCADA work request or ION to be raised. Due date extended 12 months to allow for changes in DWQ advisor staff (new and acting arrangements). To be re-assigned once southern advisor position is filled. DG investigating current condition and planned works - due date changed to reflect. DG 01102024: investigating with PE, time extended | 2019-12-03 09:00 |  | Protozoa
Kirkleagh WTP | North | 1003861 | 12268 | Raw water treatment capacity insufficient for cryptosporidium removal | Treatment process requires validation of capability against pathogen removal requirements | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress | 1. Conduct HBT tier 2/1.5 assessment (not yet started) 2. Install UV treatment (planned 2026 (moved from 2022) - KKR project) | 2019-07-17 09:00 |  | Protozoa
Jimna WTP | North | 1003863 | 12269 | Raw water quality exceeds plant treatment capability | Treatment barriers insufficient for cryptosporidium removal based on HBT assessment | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-02-11 09:00 | In progress | 1. Add protozoa treatment barrier (not yet started) 2. Conduct tier 1.5/2 assessment to verify risk (currently re-assessing under the ADWG Chapter 5 framework - log shortfall moves from 1.5 to 1) | 2019-07-17 09:00 |  | Protozoa
Landers Shute WTP | North | 1003591 | 12756 | Investigate additional ongoing continuous improvements such as - introduction of interlocking mechansim on filters that closed the outlet instead of the inlet valve, introduction of a secondary critical limit at 1 NTU for >1 minute on individual filters, introduction of 95th percentile critical limit on filtered water turbidity, introduction of interlock on dosed water pH. | Presently - In the event of breakthrough: inlet will close and an autobackwash will begin, taking the filter offline; however - the volume of the filter will still pass through the broken through filter should this occur. Ideally, the outlet should close and the filter should drain to waste. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2024-12-01 | In progress | NB the interlocking of critical limits is currently managed under the MOC# 1268 and the introduction of standard HACCP blocks. This is anticipated to be fully completed by end of june 2022. time extended to reflect MOC progress. prog/rep: still on track for end of june implementation according to MB. 7/7/2022: JK: can the date be changed until the end of the year? MB, can we get together over July/Aug to plan and then aim to deliver in September. If otherwise urgent look to do sooner. Just staff shortages and current demands through to September. Hope this can assist in scheduling and implementing before wet season (if such a thing exists – better than dry). JK 1/12/2022 JK: Due to a number of factors, the movement of the interlocking has moved to the project to deliver. With that in mind, should this be moved to be apart of the projects scope to deliver and close this risk wizard? NE 8/12/2022 No - we will keep it open until it is implemented. I will extend the date to end of fy. I will re-assign action manager since Cam is no longer the right person. NE: 31/5/2023 - Further extension required. Extending another 6 months. MB: 29/12/2023 This work (introduction of HACCP standard function blocks and implementation of HACCP interlocks) is being delivered as a package (with TEM/ TKR). Contacts for this are DR and BH NE: Extended as per MB comments until end of FY2324 NE 5/2024 - Reliant on landers shute upgrade works. Extended to coincide with their completion. | 2021-03-09 09:00 |  | Protozoa
Lowood WTP | Central | 1003535 | 12897 | Central Region- Somerset South- Lowood WTP- installation of UV to implement additional barrier to meet log removal requirements for protozoans | Project is in planning stage and delivery scheduled for 2021/ 2022 Project is underway with delivery expected to be finalised by Dec 24. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-12-31 | Not yet started | Project is on its way and completion scheduled towards the end of this year. Update - planning underway. BH is representing DWQ. Review at end of 23/24 year. Date extension to 31 Dec to allow for completion of construction/commissioning. | 2021-04-19 09:00 |  | Protozoa
Lowood WTP | Central | [not transferred to Protecht] | 12899 | Central Region- Somerset South- Lowood WTP- Validate and document inhibit timeframe for turbidity instruments. | Review current instrument locations, analysers locations and instrument type to ensure timely and accurate monitoring. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-01-31 09:00 | Completed | Date extended to allow time for E and H to work on higher priority work and to return from Xmas leave. It is understood that they have completed this in recent work at Lowood. Process Engineering Lead - Schedule meeting to review in Jan 24.. Meeting now deferred to HACCP team meeting to be held Feb-March 24. Site inspection held 28/03/24 to review this Action. The following information was confirmed in support of closing this Action out: - Nil significant incidents relating to analyser delay in the past 12 months - currently the delay is estimated to be seconds (almost instant) with the analyser located immediately below the filters - the replacement of the HACH analysers with the new TU5300 models has occurred since this Action was raised - there is no masking or inhibit timeframes applicable at present (may have been on the former RADTEL system when this Action was raised). | 2021-04-19 09:00 | 2024-03-15 | Protozoa
Lowood WTP | Central | 1003703 | 12900 | Central Region- Somerset South- Lowood WTP- additional clarifier to mitigate supply and water water quality risks | Additional clarifier is in delivery stage change of action ownership to DH Currently in early planning/design stage - date pushed out to end of FY 24/25 to allow for project completion. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2025-06-30 09:00 | Not yet started |  | 2021-04-19 09:00 |  | Protozoa
Molendinar WTP | South | 1003085 | 13006 | TMO-RW-A-13006 Risk Treatment: To 1) determine monitoring and alarming to detect high level in the backwash overflow chamber and determine a subsequent response and recovery plan, and 2) progress infrastructure changes required to prevent high level in the backwash overflow chamber. | Refer linked incident. Assigned to BJ, CB and team. Prevention of overflow to CCT will require infrastructure change therefore this would require ION or the new EAR (Emerging Asset Risk) process. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2024-12-31 | In progress | BJ to talk to S and P.E about design options. Will likely have to go through MoC and drawings updated. Will need to be commissioned hydraulically to demonstrate effectiveness in order to close out risk treatment item. In addition, to improve detection of an overflow event, investigate multitrode option. This will enable early determination to drain CCT. 26/11/2021 Works request raised to have reliable alarming with a High and HighHigh system in place using a Multitrode This proposed infrastructure would have high costs, current preventative measures are limited to monitoring and SCADA controls. | 2021-04-30 09:00 |  | Protozoa
Mt Crosby East Bank WTP | Central | 1003087 | 13242 | East Bank WTP - Media Filtration - Filter Breakthrough (High 12) | Review more data related to new filter performance. | Risk Assessment | High | 12 | Senior DWQ Advisor - Continuous Improvement | 2028-12-31 | Not yet started | Date extended as this work has not yet commenced Date extended - to be included in the Mt Crosby RA review to be held Jun-Jul 24. Noted that these filter now have full SCADA interlocks and can filter to waste. Update 08/07/2024: Due date extended to end of quarter to allow for completion of Mt Crosby East Bank WTP Risk Assessment review where this improvement plan action will be reviewed/updated. DWQ RA Review 12 Sep 24: Filter refurbishment completed. Review more data related to new refurbished filter performance. Date extended to same date as UV business case/project plan: • Preliminary business case – complete January 2026 • Detailed business case – complete January 2027 • Investment approval – June 2027 • Construction start July 2027 and complete December 2028 | 2021-08-12 09:38 |  | Protozoa
Mt Crosby East Bank WTP | Central | 1003295 | 13243 | Mt Crosby Holts Hill - Disinfection (Secondary) - Incorrect Ammonia Dose - Under dosing of ammonia. (Medium 8) | Planned Ammonia upgrade works for Holts Hill | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2024-06-30 09:00 | In progress | 1. New ammonia ring main. Replacement of all valves. Flexible hose on dosing tank to ring main replaced. Completed 2. Ammonia dosing tank to be replaced. Stage 2 replacing tank, Design Only Contract awarded to Aurecon. Project currently in design stage. Construct contract PC 30/6/22 HAZOP and RA under taken (June 2023) Date extended to allow for completion of project. | 2021-08-12 09:55 | 2024-09-12 | Bacteria
Mt Crosby East Bank WTP | Central | 1003817 | 13244 | East Bank WTP - Whole of System - Loss of SCADA system or loss of PLC (Medium 8) | Upgrade of system platform across all sites. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Continuous Improvement | 2025-12-31 09:00 | Not yet started | Training for operations or Manual? Update 29/10/2024: Upgrade of system platform across all sites. Still progressing. EB mud plant still to be done. | 2021-08-12 10:27 |  | Protozoa
Landers Shute WTP | North | 1003903 | 13523 | Excessive biomass growth in filters impacting filtration performance. | Filters are experiencing problematic biomass accumulation affecting their operation and efficiency, potentially impacting water quality and filter run times. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-12-14 09:00 | In progress | Replace pre-ozonation system with polydosing alternative Implement prefilter chlorine dosing Conduct plant trials to validate solutions (Note: Project in asset planning phase) | 2021-12-14 09:00 |  | Protozoa
Landers Shute WTP | North | 1003905 | 13524 | 1. Laboratory chemical waste collection lacks standardisation. 2. Return water line quality monitoring capability is insufficient. 3. High percentage (>10%) of separated water in returns. 4. Potential acrylamide contamination risk in system. | 1. Site laboratories' chemical waste handling and collection practices are inconsistent, creating potential safety and compliance risks. 2. Return water line operates without adequate real-time quality monitoring of critical parameters (turbidity and pH). 3. System is experiencing excessive separated water returns above the 10% threshold, indicating process inefficiency. 4. System may have unidentified acrylamide contamination pathways requiring investigation. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2026-12-14 09:00 | In progress | 1.Review and implement standardized chemical waste collection system for site laboratories. (complete) 2. Install turbidity and pH monitoring instruments on return water line (ref: ION 458). 3. Implement process improvements to reduce separated water returns below 10% threshold (ref: MOC 479). 4. Conduct acrylamide mass balance analysis to identify and address potential contamination pathways. | 2021-12-14 09:00 |  | Protozoa
Supply System (All) | Central | 1003821 | 14893 | Supply System - Brisbane Zone - Reservoir - Elevated water age. Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. High (12) | Historian (when implemented) to develop metric for water age of reservoirs. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2025-12-31 09:00 | Not yet started | EAR to be raised for this item. 04/12/24 - This will be looked at after the implementation of PODMS which is need for this project to be completed. | 2023-07-19 09:00 |  | Bacteria
Supply System (All) | Central | 1004027 | 14894 | Supply System - Brisbane Zone - Reservoir - Elevated water age. Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. High (12) | Investigate additional dosing facilities in the network. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2028-12-31 09:00 | Not yet started | EAR to be raised for this item. 04/12/24 - Will be informed by long term planning for the Supply System. | 2023-07-19 12:00 |  | Bacteria
Supply System (All) | Central | 1002837 | 14895 | Supply System - Brisbane Zone - Disturbance of Sediment Due to one or more of the following events leading to out of specification treated water: - Low level; - Significant rate up or draw; - Valving change altering flow dynamics. Medium (8) | Investigate most effective way to clean Supply System Reservoirs. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-06-30 09:00 | In Progress | Trial conducted at Capalaba. Details to come. Procedure to be updated to include new process for determining what needs cleaning. Robot cleaning to be added to the panel of providers. 04/12/24 - Heinemann Road Reservoirs 2 & 3 will be the first reservoirs to be lelaned using this system. They cleaned out in mid January using robots and the Clearpro/No Des system. | 2023-07-19 14:01 |  | Protozoa
Supply System (All) | Central | 1002839 | 14896 | Supply System - Brisbane Zone - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | Review the current reservoir inspection program/schedule to ensure effectiveness. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-02-28 | Not yet started |  | 2023-07-19 14:49 |  | Bacteria
Supply System (All) | Central | 1003949 | 14897 | Supply System - Brisbane Zone - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | Replace/repair Green Hill Reservoir membrane. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-06-30 09:00 | Not yet started | Identified in the IAMP with completion expected by July 2026.Project. Also identified in the Facility Risk Review Register. RTP 103. | 2023-07-19 15:34 |  | Bacteria
Supply System (All) | Central | 1003765 | 14898 | Supply System - Brisbane Zone - Incorrect Ammonia Dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water Medium (8) | Review low flow conditions for dosing at Aspley WQMF. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-07-31 09:00 | In Progress | MOC to be raised to kick off this investigation. 04/12/24 - Initial meetings started with operations and Process Engineering. | 2023-07-20 12:13 |  | Bacteria
Supply System (All) | Central | 1003715 | 14899 | Supply System - Brisbane Zone - Incorrect Ammonia Dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water Medium (8) | Investigate sizing of ammonia dosing pumps to ensure adequate dosing at low levels. MOC and EAR to be raised. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-06-30 09:00 | Not yet started |  | 2023-07-20 12:42 |  | Bacteria
Supply System (All) | Central | 1003717 | 14909 | Supply System - Brisbane Zone - Incorrect Ammonia Dose Over dosing of aqueous ammonia NH3(aq) leading to out of specification treated water Medium (8) | Investigate sizing of ammonia dosing pumps to ensure adequate dosing at low levels. MOC and EAR to be raised. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-06-30 09:00 | Not yet started |  | 2023-07-20 12:42 |  | Bacteria
Supply System (All) | Central | 1003609 | 14916 | Supply System - Brisbane Zone - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water. Medium (8) | - Investigations to find customers with direct connections to mains. - Brisbane City Council Mt Coot-tha Botanical Gardens. - Reticulation Connections - Mt Crosby reticulation connections, Brighton. - Investigate around Council depots from legacy Brisbane Water connections. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 09:00 | In progress | 04/12/24 - Initial discussions held with Urban Utilities. BCC are responsible for backflow prevention so will need to follow up further. | 2023-07-24 11:48 |  | Protozoa
Supply System (All) | Central | 1003611 | 14917 | Supply System - All Zones - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water. Medium (8) | - Either give mains back to Urban Utilities, or retrace another main (real bulk transfer). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 09:00 | Not yet started |  | 2023-07-24 11:53 |  | Protozoa
Supply System (All) | Central | 1003613 | 14918 | Supply System - All Zones - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water. Medium (8) | Need to have discussions with Water Service Providers to install networks to support their customers. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-01-31 09:00 | Not yet started |  | 2023-07-24 12:03 |  | Protozoa
Supply System (All) | Central | 1003897 | 14919 | Supply System - Brisbane Zone - Decommissioned or offline assets not properly isolated. Leading to out of specification treated water. Medium (8) | Investigate removal of decommissioned assets. Assets include: Pipe over Mt Crosby Road at Ugly Gully (determine ownership). Camerons Hill Booster PS isolated but not properly decommissioned. Pump 4 and 5 at Stones Road isolated but not decomissioned. 2 offtakes at My Crosby Road - old connection to lockbar main. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-03-31 09:00 | Not yet started | EAR to be raised. | 2023-07-24 13:36 |  | Bacteria
Supply System (All) | Central | 1003787 | 14920 | Supply System - Brisbane Zone - Decommissioned or offline assets not properly isolated. Leading to out of specification treated water. Medium (8) | Add decommissioned equipment layer within GIS. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-09-30 09:00 | Not yet started |  | 2023-07-24 13:44 |  | Bacteria
Supply System (All) | Central | 1004009 | 14947 | Supply System - NPI Zone - Bulk Pipeline - Contamination due to pipe depressurisation Ingress of contaminants through: - Pipe joints. - Air valves. - Leaking valves and hydrants. - Aging infrastructure. - Scours. Ingress caused by loss of pressure in main during: - Pipe burst. - Pipe repairs. - Very high flows (e.g. fire fighting) . - Incorrect isolation for maintenance Medium (8) | SCADA PLC upgrade on NPI which includes full commissioning to the operating philosophy of NPI. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2027-12-31 09:00 | In Progress | This will be included in a SCADA project being completed in 2027. | 2023-07-25 16:01 |  | Protozoa
Supply System (All) | Central | 1003767 | 14948 | Supply System - NPI Zone - Bulk Pipeline - Contamination due to pipe depressurisation Ingress of contaminants through: - Pipe joints. - Air valves. - Leaking valves and hydrants. - Aging infrastructure. - Scours. Ingress caused by loss of pressure in main during: - Pipe burst. - Pipe repairs. - Very high flows (e.g. fire fighting) . - Incorrect isolation for maintenance Medium (8) | Investigate the valve pit inspection programs that it includes the effectiveness of drainage pits. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-07-31 09:00 | Not yet started | 28/02/24 - Currently condition assessments of valves, valve pits and pipes are underway. The outcome of these assessments will inform how the future inspection program will look. | 2023-07-25 16:06 |  | Protozoa
Supply System (All) | Central | 1004035 | 14956 | Supply System - NPI Zone - Reservoirs - Elevated water age Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. High (12) | Investigate mixers at Narangba as its a more urgent requirement. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2030-12-31 | Not yet started | This has been included in the Networks Facility Risk Review process. | 2023-07-27 09:34 |  | Bacteria
Supply System (All) | Central | 1003097 | 14957 | Supply System - NPI - Disinfection (secondary) - Incorrect Sulfuric Acid Dose Under dose of sulfuric acid leading to reduced secondary disinfection for break point chlorination High (12) | Complete the commissioning of the Sulfuric Acid dosing system at Caloundra Street WQMF. Essential for RSDOP to progress. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2025-01-31 | In Progress | Business case was being finalised in Sept 2023. MW-00449 - W07 - Sulphuric Acid Dosing System Redesign and Commissioning 26/07/24 - Project is currently in delivery and expected to be completed by October 2024. Timeframe extended to allow for project completion. 22/11/24 - Time frame extended. Waiting on update from Project Manager. 04/12/24 - Installation completed but waiting to commission system. | 2023-07-27 13:07 |  | Bacteria
Supply System (All) | Central | 1003565 | 14958 | Supply System - SRP - Reservoirs - Elevated water age Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. Medium (8) | Review operating philosophy of hybrid flows for the SRP | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-12-31 09:00 | Not yet started |  | 2023-07-28 10:51 |  | Bacteria
Supply System (All) | Central | 1003983 | 14960 | Supply System - SRP - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | - Investigate when Stapylton Reservoir is due for refurbishment and identify any works planned to reduce the risk of ingress due to the size of roof sheeting. - Determine when Ventilation at Molendinar reservoir is being upgraded and escalate if required. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-12-31 | Not yet started | 1. Stapylton Balance Tank has been fed into the Facility Risk Review Register for Supply System via EAR196. Facility Risk Review RTP ID 324. This item has been discussed with Engineering Standards, Maintenance and Supply System Ops team. Due to overall reservoir vermin proofing being done and due to the type of breathers under the roof, the risk has been assessed as low compared to other reservoirs in the network. Ventilator upgrade completed in Feb 2024 which included vermin mesh. This risk will be checked annually to make sure it has not increased. Stapylton Balance Tank is not in the capital program for the next 10 years. 2. Molendinar Reservoir 7 has been fed into the Facility Risk Review Register for Supply System via EAR199. Facility Risk Review RTP ID 326 | 2023-07-31 09:55 |  | Bacteria
Supply System (All) | Central | 1003823 | 14975 | Supply System - Gold Coast/NIP - Reservoir - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | Investigate replacing box gutters at Molendinar 3 and 4 reservoirs. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-12-31 09:00 | Not yet started | Raise EAR for this. | 2023-07-31 16:57 |  | Bacteria
Supply System (All) | Central | 1003783 | 14977 | Supply System - EPI - Whole of System Decommissioned or offline assets not properly isolated Leading to out of specification treated water. Medium (8) | - Investigate removal of Kimberley Park Temporary tank. - Determine business position on the NSI Booster Pump Station and either decommission or start maintaining these assets. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-08-31 09:00 | Not yet started |  | 2023-08-02 13:50 |  | Bacteria
Supply System (All) | Central | 1003769 | 14995 | Supply System - Redland Zone - Bulk Pipeline - Contamination due to pipe depressurisation Ingress of contaminants through: - Pipe joints. - Air valves. - Leaking valves and hydrants. - Aging infrastructure. - Scours. Ingress caused by loss of pressure in main during: - Pipe burst. - Pipe repairs. - Very high flows (e.g. fire fighting) . - Incorrect isolation for maintenance Medium (8) | Implement automated controls for the valves between NSI and Serpentine Creek (MoC #1928). | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-07-31 09:00 | In Progress | 04/12/24 - Functional Design A document is currently being drafted to determine control philosophy of these valves. | 2023-08-04 15:00 |  | Protozoa
Supply System (All) | Central | 1003305 | 14996 | Supply System - Redland Zone - Reservoir - Inadequate Mixing Poor mixing in a reservoir leading to: - Pockets of reduced quality water. - Increase the possibility of nitrification. - Temperature issues. Medium (8) | Replacement of Mixers at Alexandra Hills Reservoirs 1,3,4 and 5 as well as Heinemann Road Reservoirs 2 and 3 as a priority due to mixing issues. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-10-31 | In Progress | EAR has been raised and this item has been added to the Facility Risk Review process for Supply System - RTP 313 BWSA Exceedance on 24/07 24 for elevated free chlorine. 27-09-2024: Root cause analysis on PAX failures completed. PAX units being pulled out of HR 2 and 3, week of the 16th of October. One is being sent offsite to be dismantled to see what is causing the failure. No further update on replacement of these failed mixers. Action due date being extended out to allow for business to acquire new mixers. 04/12/24 - Work underway to install Wears mixers in Heinemann Road Reservoir 2 and 3. Failed Pax mixers have been removed. Reservoir cleaning for Res 2 and 3 is planned for mid Jan 2025 with new mixers being installed after that. Strategy meeting on mixer replacement going forward is planned for 11 Dec 2024. | 2023-08-04 15:45 |  | Bacteria
Supply System (All) | Central | 1003567 | 14997 | Supply System - Redland Zone - Reservoirs - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris High (12) | Roof replacement for Heinemann Road Reservoir 1. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2024-12-31 09:00 | In Progress | Included in Reservoir package 1 works. Due for completion July 2024. | 2023-08-04 15:55 |  | Bacteria
Supply System (All) | Central | 1004011 | 14998 | Supply System - Redland Zone - Reservoirs - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris High (12) | Investigate box gutters at Alexandra Hills 4 Reservoir. | Risk Assessment | High | 12 | Senior DWQ Advisor - Central | 2027-12-31 09:00 | Not yet started | Replace roof including re-design of gutter for Alexandra Hills Reservoir 4 is in the IAMP Capital Program for delivery in 2026/2027 | 2023-08-04 04:00 |  | Bacteria
Supply System (All) | Central | 1003985 | 14999 | Supply System - Redland Zone - Disinfection (Secondary) - Incorrect Chlorine dose Underdosing of sodium hypochlorite causing overdose of chlorine leading to out of specification treated water. Medium (8) | Conduct a Process Assessment of Heinemann Road and Alex Hills dosing. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-12-31 09:00 | Not yet started | 04/12/24 - Lower priority site after new mixers installation is done. | 2023-08-07 09:50 |  | Bacteria
Supply System (All) | Central | 1003825 | 15000 | Supply System - Redland Zone - Whole of System - Loss of power Loss of power impacting treated water quality Medium (8) | Investigate installation of a generator to run Heinemann Rd PS (can be trailer mounted) including shelter. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2025-12-31 09:00 | Not yet started | Included in the Supply System Facility Risk Register - RTP 161 | 2023-08-07 10:20 |  | Bacteria
Supply System (All) | Central | 1003971 | 15005 | Supply System - Logan Zone - Reservoirs - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water: - Vermin - Rain - Dust or other debris Medium (8) | Investigate possible solutions to reduce the likelihood of WQ related issues with the Break of Head Tank. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-10-30 09:00 | Not yet started |  | 2023-08-08 15:23 |  | Bacteria
Supply System (All) | Central | 1003951 | 15007 | Supply System - Logan Zone - Loss of Control System Leading to out of specification treated water. Medium (9) | Implement remote manual capability of the Daisy Hill Pumps to be able to fill up Kimberley Park reservoir when 4G outages occur at this site. | Risk Assessment | Medium | 9 | Senior DWQ Advisor - Central | 2026-06-30 | Not yet started |  | 2023-09-08 |  | Loss of Supply
Supply System (All) | Central | 1004001 | 15008 | Supply System - Logan Zone - Loss of Power Leading to out of specification treated water. Medium (8) | Investigate implementation of permanent generator at Trinder Park. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2027-07-30 09:00 | Not yet started |  | 2023-08-09 10:40 |  | Bacteria
Supply System (All) | Central | [not transferred to Protecht] | 15445 | Supply System - SWP - Gravity Feed Operation - Offline assets not properly isolated Leading to out of specification treated water. Medium (8) | Water Quality training for all contractors who have not been done. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-06-30 09:00 | Completed | Seqwater Water Hygiene and Materials Training [Course Code: 2764] was provided to three (x3) Service Stream staff on the 28 November 2023, and an additional (x1) Service Stream employee and nine (x9) of their subcontractors on the 23 January 2024. The need for this training to occur on a 24 month cycle has also been brought to Major Projects attention for relevant Seqwater staff and contractors, and this has been communicated to Service Stream and has been documented in Commissioning Team minutes as well. Due to this matter being effectively addressed and another Service Stream employee having reach out to do this training, I am happy that this action can now be closed out. | 2023-12-07 11:13 | 2024-05-07 | Protozoa
Supply System (All) | Central | 1003335 | 15446 | Supply System - SWP - Bulk Pipeline - Gravity Feed Operation - Offline assets not properly isolated. Leading to out of specification treated water. Medium (8) | Recommendation for Major Projects to inform construction staff about transition of SWP to gravity feed potable water supply to residents at Beaudesert and the criticality of effective isolation of assets yet to be commissioned. This item is to remain open until gravity feed operation to Beaudesert is ceased and pipeline is commissioned. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2024-01-12 09:00 | In progress | 28/02/24 - KM sighted Lock Out Permit dated 02/02/24 which is still valid. | 2023-12-07 11:38 | 2024-07-25 | Protozoa
Hinze Dam WTP | South | 1003633 | 15547 | THZ-RW-A-15547 Risk Treatment from RA - investigate the if the BOHT and its operation achieve any LRV for HBT. | the 2024 Hinze Dam WTP Source Water Assessment and the 2022 Hinze Dam WTP HBT Assessment indicated there is shortfall in treatment which requires process improvements and possibly additional pathogen barriers, However, the BOHT and its operation were included in these assessment and this may achieve some pathogen LRV's which havent been accounted for. this Risk treatment is targeted at investigating LRV achieved by the BOHT and improvements in its operation as well as the other plant processes. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - South | 2025-02-10 09:00 | Not yet started | raised RA 2024 - begin investigation into BOHT LRV assessment method. | 2024-02-06 14:40 |  | Protozoa
Ewen Maddock WTP | North | 1004067 | 15559 | Fluoride dosing reliability issues at Ewen Maddock facility creating risk of underdosing. | The fluoride dosing system at Ewen Maddock facility has shown inconsistencies that could lead to underdosing events, potentially impacting regulatory compliance and public health outcomes. While currently operational, the system's reliability and robustness needs engineering assessment to identify improvements that would reduce fluoride dosing failures and ensure consistent treatment levels. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - North | 2034-02-15 09:00 | Not yet started | PE to investigate potential improvements to reliability and robustness at ewen maddock to reduce likelihood of underdosing | 2024-02-15 09:00 |  | Fluoride
Dayboro WTP | North | 1003317 | 15560 | Water quality inconsistencies and safety risks in tanker delivery operations due to inadequate quality control measures and procedures. | Water quality variations and potential contamination risks have been identified in the tanker delivery operations. While a tankering procedure exists, it requires updating to strengthen quality control measures and ensure consistent safe water delivery standards. | Risk Assessment | Medium | 8 | Lead Drinking Water Quality | 2025-04-30 | Not yet started | Develop a system to guarantee the water quality available to the tanker . Update to tankering procedure | 2024-02-15 09:00 |  | Chlorine
Image Flat WTP | North | 1003329 | 15561 | Tracking the fluoride upgrade at image flat. | Various improvements to the fluoride dosing system are planned to improve reliability | Risk Assessment | Medium | 9 | Senior DWQ Advisor - North | 2025-12-01 | Not yet started | Existing fluoride upgrade project Implementation anticipated by end 2025. | 2024-02-15 09:00 |  | Fluoride
Esk WTP | Central | 1120120 | 15562 | Esk WTP - Chemical dosing is on the raw water flow meter and not filtered water flow meter - to be rectified. Process Engineering/Operations project - changes triggers for chemical dosing based on flow meters. | Refer to Process Engineering Central MS Teams project schedule. | Risk Assessment | High | 12 | Senior DWQ Advisor - Continuous Improvement | 2027-02-16 09:00 | Not yet started | Captured in Process Engineering Issues Register and is on the Central Risk Forum Register (RTP9) through which forum this action will be tracked. Currently incorporated into Esk Distribution Board Upgrade (APMP 20200086), as this change requires switchboard/relay changes prior to implementing the code functional changes. Process Engineering have completed an initial design for the functionality changes. Update 6/12/24: Transferred into Protecht to tracking with due date 31/12/2028 to allow for prioritisation and delivery. | 2024-02-16 09:00 |  | Viruses
Esk WTP | Central | 1004031 | 15564 | Esk WTP Upgrade - Replacement WTP design-construct-commission (Project IW289700) | Please refer to Project IW289700 for details. | Risk Assessment | High | 12 | Senior DWQ Advisor - Continuous Improvement | 2030-02-19 09:00 | Not yet started |  | 2024-02-19 09:00 |  | Protozoa
Supply System (All) | Central | 1118171 | N/A | Supply System - SWP Zone - Bulk Pipeline - High flow, rapid flow changes or reverse flow in pipelines leading to: Scouring and sloughing of biofilm and sediment. Medium (8) | Operational activity to be undertaken toinspect internal pipeline during defect period. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-12-31 | Not yet started |  | 2024-03-15 |  | Bacteria
Supply System (All) | Central | 1118174 | N/A | Supply System - SWP Zone - Reservoirs - Elevated water age - Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. Medium (8) | Operational philosophy to be developed for the Beaudesert WTP and the SWP, especially in winter. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2026-12-31 | Not yet started |  | 2024-03-15 |  | Bacteria
Supply System (All) | Central | 1118176 | N/A | Supply System - SWP Zone - Reservoirs - Inadequate Mixing - Poor mixing in a reservoir leading to: - Pockets of reduced quality water. - Increase the possibility of nitrification Medium (8) | Verification sampling to be conducted at the pump station for 12 months to obtain data to determine water age risk in reservoir. | Risk Assessment | Medium | 8 | Senior DWQ Advisor - Central | 2027-12-31 | Not yet started |  | 2024-03-15 |  | Bacteria
Dayboro WTP | North | 1116822 | N/A | TDY (& TKE) - UV disinfection - Insufficient UV dose for viruses | The plant has no online UVT monitoring and hence no way to validate or enact this requirement. There is a risk that if the plant were to fall below 90% UVT and it is not identified, the required pathogenic log reduction may not be achieved. | Risk Assessment | High | 12 | Senior DWQ Advisor - North | 2025-03-27 | In progress | Installation of UVT analyser and validation of virus log reduction (in order to validate at least 1 log credit for viruses) by trojan/manufacturer. Install dynamic Ct (MB program) | 2020-03-27 |  | Viruses