## Cover Page
#VALUE!
Template
E-TMP-STD-004
Cable Schedule
Document Number: TEM-00283
This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.
| Rev no. | Description | Process Owner |  | Approved for issue
|  |  | Position | Name | Position | Name | Date
| 1 | Original Version | Lead Engineer - Electrical & Control Systems | Refer Supporting Info in REX | Principal Engineer, Standards and Assurance | Refer Supporting Info in REX | 2019-10-30
| 2 | Amended Version | Lead Engineer Electrical Engineer | Refer Supporting Info in REX | Principal Engineer, Standards and Assurance | Refer Supporting Info in REX | 2026-01-27
Subject Matter Expert Authorisation
| Rev no. | Name |  | Date |  | RPEQ #
| 2 | Refer Document Properties in REX |  | 2026-01-23 |  | Refer Doc. Properties in REX
DOCUMENT SENSITIVITY: OFFICIAL (Public)

## Cable Schedule New
NOTES:
Cable | Route |  | Function | Circuit | kW | Amps | Cbl Rated | No. of | Core Size | Cable | Sheath | Length | Route | Drawing Number | Cable | Comments
No. | From | To |  | Voltage |  |  | Voltage | Cores | (mm²) | Type | Colour | (m) |  |  | Rev.
E9SWB011-P1 | TGL-E-9SWB002 TREATED WATER PUMP STATION MCC | TGL-E-9SWB011 UV DISINFECTION SWITCHBOARD INCOMER 1 | INCOMER 1 POWER | 400V AC | - | 100 | 0.6/1kV | 4C+E | 70 | Cu/V90-PVC/PVC | OG | 96 | U/G CONDUIT | E-DWG-TGL-00171 | 1
E9SWB011-P2 | TGL-E-9SWB002 TREATED WATER PUMP STATION MCC | TGL-E-9SWB011 UV DISINFECTION SWITCHBOARD INCOMER 2 | INCOMER 2 POWER | 400V AC | - | 100 | 0.6/1kV | 4C+E | 70 | Cu/V90-PVC/PVC | OG | 96 | U/G CONDUIT | E-DWG-TGL-00171 | 1
M2PMP003-P1 | TGL-E-9SWB011 UV SWITCHBOARD TIER 2 | TGL-M-2PMP003 RECIRCULATION PUMP 3 MOTOR ISOLATOR | MOTOR POWER | 400V AC | 0.37 | 1 | 0.6/1kV | 3C+E | 2.5 | Cu/V90-PVC/PVC | OG | 17 | U/G CONDUIT | E-DWG-TGL-00166 | 1
M2PMP003-P2 | TGL-M-2PMP003 RECIRCULATION PUMP 3 MOTOR ISOLATOR | TGL-M-2PMP003 RECIRCULATION PUMP 3 MOTOR | MOTOR POWER | 400V AC | 0.37 | 1 | 0.6/1kV | 3C+E | 2.5 | Cu/V90-PVC/PVC | OG | 2 | TRAY | E-DWG-TGL-00166 | 1
M2PMP003-C1 | TGL-E-9SWB011 UV SWITCHBOARD TIER 2 | TGL-M-2PMP003 LOCAL ISOLATOR | MOTOR CONTROL | 24V DC | - | - | 0.6/1kV | 2C+E | 1.5 | Cu/V90-PVC/PVC | BK | 17 | U/G CONDUIT, TRAY | E-DWG-TGL-00166 | 1
M2PMP003-C2 | TGL-E-9SWB011 UV SWITCHBOARD TIER 2 | TGL-M-2PMP003 EMERGENCY STOP | MOTOR CONTROL | 24V DC | - | - | 0.6/1kV | 2C+E | 1.5 | Cu/V90-PVC/PVC | BK | 18 | U/G CONDUIT, TRAY | E-DWG-TGL-00166 | 1
I2FIT004-P1 | TGL-E-9SWB011 UV SWITCHBOARD 24VDC DB SECTION | TGL-I-2FIT004 UV REACTOR 1 INLET FLOW TRANSMITTER | INSTRUMENT POWER | 24V DC | - | 0.5 | 0.6/1kV | 2C+E | 2.5 | Cu/V90-PVC/PVC | BK | 16 | TRAY | E-DWG-TGL-00189 | 2
I2FIT004-A1 | TGL-E-9SWB011 UV SWITCHBOARD RIO SECTION | TGL-I-2FIT004 UV REACTOR 1 INLET FLOW TRANSMITTER | INSTRUMENT SIGNAL | 24V DC | - | 4-20mA | 110Vac/150Vdc | 2PR+OSCN | 0.5 | Cu/V90-PVC/OSCN/PVC | BK | 16 | TRAY | I-DWG-TGL-00068 | 2
E9DBR002\CB7 | TGL-E-9DBR002 UV L&P DISTRIBUTION BOARD CB Q7 | 32A 3PH GPO | GPO POWER | 400V AC | - | 32 | 0.6/1kV | 4C+E | 10 | Cu/V90-PVC/PVC | OG | 25 | TRAY | E-DWG-TGL-00172 | 1
E9DBR002\CB12-01 | TGL-E-9DBR002 UV L&P DISTRIBUTION BOARD CB Q12 | DEWATERING BUILDING EXTERNAL LIGHTING FITTING 1 | LIGHTING | 230V AC | - | 16 | 0.6/1kV | 2C+E | 2.5 | Cu/V90-PVC/PVC | OG | 20 | TRAY, U/G CONDUIT | E-DWG-TGL-00172 | 1
E9DBR002\CB12-02 | DEWATERING BUILDING EXTERNAL LIGHTING FITTING 1 | DEWATERING BUILDING EXTERNAL LIGHTING FITTING 2 | LIGHTING | 230V AC | - | 16 | 0.6/1kV | 2C+E | 2.5 | Cu/V90-PVC/PVC | OG | 10 | U/G CONDUIT | E-DWG-TGL-00172 | 1
Notes:
Pre-filled template data is for example only.
This text box shall be deleted when the template is populated.

## Title Block
REVISIONS | [6 empty] | CONTRACTOR LOGO | FACILITY: eg. GLENSIDE WATER TREATMENT PLANT (EXAMPLE DATA)
NO. | DESCRIPTION | DATE | PREPARED | RPEQ | RPEQ No. | APPROVED
WORK DESCRIPTION: eg. UV DISINFECTION (EXAMPLE DATA)
SEQWATER PROJECT NO.: XXXXXXXX
DOC. NO.: XXXXXXXXXX
CABLE SCHEDULE