## Cover Page (DELETE at TENDER)
Template
E-TMP-STD-005
AC Uninterruptable Power Supply (UPS) Datasheet
Document Number: TEM-00304
This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.
Rev no. | Description | Process Owner |  | Approved for issue
|  | Position | Name | Position | Name | Date
1 | Original Version | Principal, Engineering Standards and Assurance | Refer Supporting Info in REX | Manager, Asset Management | Refer Supporting Info in REX | 2020-02-03
2 | Amended Version (company restructure) | Principal, Engineering Standards and Assurance | Refer Supporting Info in REX | Chief Operating Officer (Acting) | Refer Supporting Info in REX | 2020-02-17
3 | Amended Version | Lead Electrical Engineer | Refer Supporting Info in REX | Principal, Engineering Standards and Assurance | Refer Supporting Info in REX | 2025-12-19
Subject Matter Expert Authorisation
Rev no. | Name |  | Date |  | RPEQ #
3 | Refer Document Properties in REX |  | 2025-12-19 |  | Reer Doc Properties in REX
DOCUMENT SENSITIVITY: OFFICIAL (Public)

## UPS Datasheet
|  |  | AC UNINTERRUPTIBLE POWER SUPPLY(UPS) | [5 empty] | [INSERT CONTRACTOR LOGO]
DATASHEET
Template may be updated and should be accessed from official location prior to each use. Uncontrolled copy valid only at time of printing.
DATA SHEET NUMBER |  | E-DSH-STD-XXX | REV | DATE | DESCRIPTION | PREPARED | CHECKED | APPROVED
REX ID |  | XXXXXXXX | A |  | Issued for Review
PROJECT NUMBER |  | XXXXXXXX
PROJECT DESCRIPTION |  | XXXXXXXX
ASSET LOCATION |  | Mount Crosby West Bank WTP
ITEM | DESCRIPTION |  | UNIT | CLIENT/DESIGNER PREFERRED DATA |  |  |  |  | VENDOR DATA/COMMENTS | REVISION
1 | MANUFACTURER DETAILS | Contractor | - | *
2 |  | Manufacturer | - | *
3 |  | Manufacturer location | - | *
4 |  | Model No. | - | *
5 | EQUIPMENT DETAIL | Equipment Number | - | xxxx
6 |  | Equipment Name | - | xxxx
7 |  | Design Criteria | - | E-SPE-STD-001
8 |  | Technical Specification | - | E-SPE-STD-004
9 |  | Single Line Diagram | - | E-DWG-XXX-XXX
10 |  | Schematic And Wiring Diagram | - | I-DWG-XXX-XXX
11 |  | UPS battery sizing calculation | Y/N | Yes
12 | INSTALLATION CONDITIONS | Installation location | - | Indoor (Air Conditioned switchroom)
13 |  | Design Life UPS | Years | 10 years before major overhaul is required.
14 |  | Design Life batteries | Years | 5 years before replacement.
15 |  | Design ambient temperature | °C | -5 to 45
16 |  | Relative humidity | % | 26 to 85
17 |  | HVAC pressurisation | - | N/A
18 |  | Solar radiation | W/m2 | 1030
19 |  | Pollution Degree | - | Withstand pollution degree 2 (non-conductive) to AS 62040.3
20 |  | Hazardous area | Yes/No | No
21 |  | Vibration | -
22 |  | Seismic Classification | - | N/A
23 | ELECTRICAL SUPPLY | Power System Nominal Voltage Level | V | 400
24 |  | Voltage Tolerance | % | +10/-6
25 |  | Frequency | Hz | 50
26 |  | Frequency Tolerance | % | +/-2
27 |  | Incoming Power System Configuration | - | 3 Phase + Neutral
28 |  | Incoming Power System Earthing Configuration | - | TN-S in accordance with AS/NZS 3000
29 |  | Prospective Short Circuit Current | kA | *
30 | UPS GENERAL | Standard | _ | AS 62040.1.1, AS 62040.2 & AS 62040.3
31 |  | Power, rated - apparent | VA | *
32 |  | Power, rated - active | W
33 |  | Redundancy - rectifier / battery charger |  | N+1
34 |  | Redundancy - inverter |  | N+1
35 |  | Redundancy - Batteries
36 |  | Connection Type |  | Permanent, not pluggable
37 |  | Input AC isolation switch |  | Yes, isolating both normal and bypass supplies
38 |  | Static AC bypass switch |  | Automatic, all poles
39 |  | Maintenance bypass switch
40 |  | UPS Mechanical and Enclosure
41 |  | Enclosure dimensions (HxWxD) | _
42 |  | Enclosure mass with/without batteries | kg/kg
43 |  | Degree of protection against dust and water ingress to UPS external enclosure | _ | IP4X
44 |  | Mounting | _ | Plinth 150 mm (min.) channel iron, galvanised free standing floor
45 |  | Construction type | _ | Single Sided, Metal Clad, Free Standing
46 |  | Construction Material | _ | 2 mm (min.) thick steel
47 |  | Cooling | _ | *
48 |  | Heat Loss | kW
49 |  | Coating type | _ | *
50 |  | Anti-condensation heaters | _ | *
47 |  | Cable entry | _ | Bottom entry
48 |  | Gland plate material | _ | Brass / aluminium
49 |  | Gland plate thickness | mm | 3mm (min)*
50 |  | Electromagnetic Compatibility
51 |  | EMC compatibility - emission and immunity | _ | Comply with AS 62040.2
52 |  | UPS Protection
53 |  | Backfeed protection | _ | Yes
54 |  | Overcurrent and earthfault protection | _ | Yes
55 |  | Inverter Protection | _ | Yes
56 |  | Input reverse polarity | _ | Yes
57 |  | Input inrush current limiting | _ | Yes
58 |  | Input thermal fuse | _ | Yes
59 |  | Input undervoltage | _ | Yes
60 |  | Input overvoltage | _ | Yes
61 |  | Output overload | _ | Yes
62 |  | Safety |  | Yes
63 |  | Access (operator access or restricted access) |  | Operator access
64 |  | Degree of protection of all internal components |  | IP2X
65 |  | Electrical equipment shrouding |  | IP2X
66 |  | Safety interlocks for operator access |  | Yes
67 |  | Means of discharge for capacitive components |  | Yes
68
69 | COMMUNICATIONS | Modbus over Ethernet (TCP/IP) | -
70 |  | SNMP | -
71 |  |  | -
72
73 | EXTERNAL MAINTENANCE BYPASS SWITCH | Manufacturer | -
74 |  | Model / Type No. | -
75 |  | Changeover type | - | Make before break*
76 |  | Number of poles | -
77 |  | Rated current | A
78 |  | Switch padlockable in any position |  | Yes
79 |  | Enclosure material |  | *
80 |  | Enclosure IP rating |  | *
81 |  |  | - | *
82 | OUTPUT - ELECTRICAL | AC power distribution system
83 |  | Earthing system compatibility | - | TN-S in accordance with AS/NZS 3000
84 |  | Phases available | -
85 |  | Neutral available | - | Yes
86 |  | Voltage
87 |  | Rated voltage (steady state, r.m.s.) | V AC
88 |  | Normal mode voltage variation | % | *
89 |  | Stored energy mode voltage variation | % | *
90 |  | THD, 100% load, normal mode - linear | % | *
91 |  | THD, 100% load, normal mode - non linear | % | *
92 |  | THD, 100% load, stored energy mode - linear | % | *
93 |  | THD, 100% load, stored energy mode - non linear | %
94 |  | Voltage unbalance and phase displacement from 100% load unbalance (3 phase only) | %, °
95 |  | Voltage transient and recovery time, 100% step load - linear | %, s
96 |  | Voltage transient and recovery time, 100% step load - non linear | %, s
97 |  | Voltage transient and recovery time - normal mode to stored energy mode and stored energy mode to normal mode (worst case) | %, s
98 |  | Frequency (steady state)
99 |  | Rated | Hz | 50Hz
100 |  | Normal mode variation | %
101 |  | Stored energy mode variation | %
102 |  | Free running (non-synchronised) variation | %
103 |  | Synchronisation (max ± % range of frequency) | %
104 |  | Max synch phase error (referred to a 360° cycle) | °
105 |  | Max slew rate | Hz/s
106 |  | Current (r.m.s.)
107 |  | Rated | A
108 |  | Overload capability (% of rated current / time duration) | % / s
109 |  | Limitation (% of rated current / time duration) | % / s
110 |  | Fault clearing capability (normal / stored energy mode) | A gL fuse
111 |  | Load power factor
112 |  | Rated | -
113 |  | Displacement (permissible lead-lag range) | -
114 |  | AC/AC efficiency in normal mode
115 |  | 100% load | %
116 |  | 75% load | %
117 |  | 50% load | %
118 |  | 25% load | %
119 |  | Bypass
120 |  | Automatic bypass type (static or electro-mechanical) | -
121 |  | Transfer time break | ms
122 |  | Rated current | A
123 |  | Overload current (% of rated current / time duration) | %/s
124 |  | Maintenance bypass type (internal or external) | -
125 |  | Isolation transformer (yes/no) | -
126 |  | Bypass protection fuse or circuit breaker rating | A
127 |  | Additional requirements
128 |  | MEN earthing system maintained in all modes | _ | Yes
129 |  | Fault Contribution | A | *
130 | INPUT - ELECTRICAL | Voltage
131 |  | Rated voltage (steady state, r.m.s.) | V AC
132 |  | Tolerance | %
133 |  | Voltage unbalance tolerance (3 phase only) | %
134 |  | THD of voltage | % | ≤ 5%, with max level of individual harmonic voltages according to AS 61000.2.2
135 |  | Frequency (steady state)
136 |  | Rated | Hz | 50Hz
137 |  | Tolerance | %
138 |  | Current (r.m.s.)
139 |  | Rated current (with battery charged) | A | *
140 |  | Maximum current (with low input voltage and battery charging) | A | *
141 |  | Total harmonic distortion of current (THD pu) | % | *
142 |  | Overload current (% of rated current against time) | %, s | *
143 |  | In-rush current (% of rated current against time) | %, s | *
144 |  | Power factor at rated current | - | *
145 |  | AC power distribution system
146 |  | AC power system compatibility | -
147 |  | Phases required (1, 2 or 3) | -
148 |  | Neutral required (yes/no) | - | Yes
149 |  | Earth leakage characteristics (where in excess of 3.5mA) | mA | *
150 |  | Additional requirements
151 |  | Number of input supplies
152 |  | Active phases and neutral pole isolation of UPS from all sources of AC input supply |  | Yes
153 |  | Suitable for supply by standby generator |  | Yes
154
155 | BATTERIES | Batteries
156 |  | Equipment name | _ | *
157 |  | Panel tag number | _ | *
158 |  | Manufacturer | _ | *
159 |  | Model | _ | *
160 |  | Technology | _ | VRLA / AGM / NiCd. (Lithium prohibited)
161 |  | Quantity of strings | _ | *
162 |  | Quantity of cells per string | _ | *
163 |  | Nominal voltage (individual battery) |  | *
164 |  | Nominal voltage (total) |  | *
165 |  | Design load |  | *
166 |  | Nominal Ah capacity |  | *
167 |  | Ah capacity after 20% load growth and 25% age compensation applied |  | *
168 |  | Stored energy time (back-up time at 100% rated load) |  | 8 hours minimum
169 |  | Restored energy time (recharge time to 90% capacity) |  | 10-12 hours
170 |  | Ambient battery reference temperature |  | 25
171 |  | Earth condition / isolation |  | negatively earthed
172 |  | r.m.s ripple current |  | *
173 |  | Battery cables and protection supplied |  | Yes
174 |  | Battery isolation and protective device |  | Circuit breaker, double pole, DC rated
175 |  | Charging regime |  | *
176 |  | Charge voltage (float, boost) and tolerance band |  | *
177 |  | End of discharge voltage |  | *
178 |  | Charging current limit (or range) |  | *
179 |  | Battery Enclosure
180 |  | Construction type |  | Single sided, metal clad, free standing
181 |  | Construction material |  | 2 mm (min.) thick zincanneal steel *
182 |  | Coating type |  | Powder coating to external surfaces, galvanised interior parts
183 |  | Coating colour |  | RAL 7035
184 |  | Dimensions (HxWxD) |  | *
185 |  | Mass - individual cell |  | *
186 |  | Mass - enclosure with batteries |  | *
187 |  | Battery isolator manufacturer |  | *
188 |  | Battery isolator model / type no. |  | */ *
189 |  | Electrical equipment shrouding |  | IP2X
190 |  | Battery connection access method |  | Front access, withdrawable
191 |  | Cable entry |  | Bottom only
192 |  | Ventilation method - natural / forced |  | *
193 |  | Ventilation exhaust |  | Exterior of switchroom
194 |  | Doors |  | Lockable door *
195 |  | IP rating |  | IP4X
196 |  | Temperature sensor |  | Yes
197 |  | UPS to Battery Cables
198 |  | Cable type |  | Flexible LSZH, tinned
199 |  | Cable connection |  | Between Isolator - External Maintenance Bypass and UPS
200 |  | Size | mm² | *
201 |  | Insulation Voltage | _ | 0.6/1 kV
202 | RECTIFIER / CHARGER | Manufacturer |  | *
203 |  | Model |  | *
204 |  | Type |  | Phase controlled rectifier
205 |  | Conformal coating |  | Yes
206 |  | Phases |  | 1
207 |  | Soft start capability |  | Yes
208 |  | Float volt compensation for battery temperature |  | Yes
209 |  | DC output
210 |  | Rated output current | A | A
211 |  | Max continuous current before current limiting | A | A
212 |  | Float voltage range |  | *
213 |  | Equalizing voltage range |  | *
214 |  | Boost voltage range |  | *
215 |  | Voltage regulation | % | ≤ 1%
216 |  | Maximum peak output voltage | V | Voltage setting +10%
217 |  | Ripple voltage with battery connected | % | ≤ 2%
218 |  | Ripple voltage without battery connected | % | ≤ 5%
219 |  | Efficiency | _ | *
220 |  | Protection
221 |  | Circuit breaker on AC input | _ | Yes
222 |  | High DC voltage shut-down | _ | Yes
223 |  | AC power failure | _ | Yes
224 |  | Reverse polarity protection on the output to the battery | _ | Yes
225 |  | DC undervoltage alarm (low battery voltage) | _ | Yes
226 |  | DC undervoltage disconnection (end of battery discharge) | _ | Yes
227 |  | DC undervoltage disconnection (end of battery discharge) | _ | Yes
228
229 | INDICATION AND MEASUREMENT | Status Indication
230 |  | Load on Inverter supply
231 |  | Load on Static Bypass supply.
232 |  | Normal AC input supply available
233 |  | Inverter on Battery supply
234 |  | MBS in UPS position
235 |  | MBS in Test position (where applicable)
236 |  | MBS in Bypass position
237 |  | Battery charger output failure
238
239
240 |  | Measurements (UPS digital display)
241 |  | Normal input AC voltage / current (per phase) | _ | Yes
242 |  | Bypass input AC voltage / current (per phase) | _ | Yes
243 |  | DC battery voltage / current | _ | Yes
244 |  | Inverter output AC voltage / current | _ | Yes
245 |  | System output frequency | _ | Yes
246 |  | Active and apparent power | _ | Yes
247 |  | Power factor of the load | _ | Yes
248 |  | Battery capacity remaining | _ | Yes
249 |  | Battery enclosure temperature | _ | Yes
250
251 | ALARMS | Alarms - Hardwired (volt free contacts wired to marshalling terminals)
252 |  | AC power failure
253 |  | UPS fault
254 |  | UPS on bypass
255 |  | Battery discharging
256 |  | Battery disconnected
257 |  | Rectifier/charger fault
258 |  | Inverter fault
259 |  | UPS common alarm (grouped)
260 |  | Alarms - links to SCADA
261 |  | Normal input AC power supply failure | _
262 |  | Bypass input AC power supply failure | _
263 |  | Rectifier / charger failure | _
264 |  | DC overvoltage / undervoltage | _
265 |  | Battery disconnected | _
266 |  | Battery charge failure | _
267 |  | Rectifier / charger current-limit mode operating | _
268 |  | Inverter failure | _
269 |  | AC output overvoltage / undervoltage | _
270 |  | Inverter overcurrent | _
271 |  | Inverter output frequency out-of-limits | _
272 |  | Synchronisation loss | _
273 |  | Control circuit fault | _
274 |  | AC output supplies lost | _
275 |  | High cabinet temperature | _
276
277 | STATUS | Status - Hardwired (volt free contacts wired to marshalling terminals)
278 |  | UPS operation healthy | _
279 |  | Modbus TCP/IP communication link to SCADA | _
280 |  | AC input voltage | _
281 |  | AC input current | _
282 |  | Charge voltage | _
283 |  | Charge current | _
284 |  | AC load voltage | _
285 |  | AC load current | _
286 |  | Battery charge/discharge | _
287 |  | Inverter output voltage | _
288 |  | Inverter input voltage | _
289 |  | Switched to bypass operation | _
290
291 | BATTERY MONITORING SYSTEM | BMS device | [8 empty] | Yes
292 |  | Make | _ | [7 empty] | Yes
293 |  | Model | _ | [7 empty] | Yes
294 |  | Communications connection | _
295 |  | Installation location | _
296 |  | Conformal coating | _
297 |  | BMS signals - Modbus TCP/IP communication link to SCADA
298 |  | Cell Temperature | _
299 |  | Cell Impedance (Av, Min, Max) | _
300 |  | Depth of Discharge (Av, Min, Max) | _
301 |  | Estimated Battery Capacity Remaining | _
302 |  | Time Left to Low Voltage | _
303 |  | Discharge Current (Average, Maximum) | _
304 |  | Charge Current (Average, Maximum) | _
305 |  | Deepest Discharge Level | _
306 |  | Counter of Deep Discharge Events | _
307 |  | Average Time Spent in Deep Discharge | _
308 |  | Maximum Time Spent in a Deep Discharge | _
309
310 | CONTROLS | Local controls at UPS
311 |  | Rectifier on/off control switch | _
312 |  | Inverter on/off control switch | _
313 |  | Manual load transfer control switch | _
314 |  | Rectifier input isolation switch | _
315 |  | Battery isolation switch/Circuit Breaker | _
316 |  | Alarm reset local | _
317 |  | Shutdown | _
318 |  | Alarm acknowledge local and at SCADA | _
319 |  | DC float voltage adjustment AC output voltage adjustment Battery isolation circuit breakers Alarm acknowledge Alarm reset Shutdown | _
320 |  | DC current limit adjustment | _
321 |  | AC output voltage adjustment | _
322
323 | PACKAGING AND TRANSPORT | Shock Impact Indicators | Yes/No
324 |  | Shock Impact Indicator Quantity | _
325 |  | Shock Impact Indicator Rating | _
326 |  | Packaging guidelines | _
327 |  | Lifting Plan Required | Yes/No
328 | NOTES | 1. Pre-filled data is for guidance/example only. The project design RPEQ is responsible for populating the preferred data column in accordance with statutory requirements, Seqwater standard specifications and project requirements.
329 |  | 2. Item denoted by * to be supplied by Vendor.
330 |  | 3. Vendor to provide General Arrangement Drawings, Single Line Diagram, Schematic Diagrams, Termination Diagrams, Label Schedule Drawings for approval prior to manufacture.
331 |  | 4. Vendor shall provide a list of departures from Seqwater specification E-SPE-STD-004 AC Uninterruptable Power Supply (UPS) for acceptance with bid proposal.
332 |  | 5. Vendor shall provide battery sizing calculation, ventilation calculation and maximum demand calculations.

## Asset Location List (hidden)
Area | Asset Type | Asset Name
Central | Store | Atkinson Dam
Central | Store | Bill Gunn Dam
Central | Store | Gold Creek Dam
Central | Store | Lake Manchester Dam
Central | Store | Somerset Dam
Central | Store | Wivenhoe Dam
Central | Treat | Banksia Beach WTP
Central | Treat | Esk WTP
Central | Treat | Kirkleagh (Recreation) WTP
Central | Treat | Lowood WTP
Central | Treat | Mount Crosby East Bank WTP
Central | Treat | Mount Crosby West Bank WTP
Central | Other | Camerons Hill Reservoir (Site Type: WTP)
Central | Other | Cormorant Bay SPS (Site Type: WTP)
Central | Other | Lumley Hill Reservoir (Site Type: WTP)
North | Store | Baroon Pocket Dam
North | Store | Borumba Dam
North | Store | Cedar Pocket Dam
North | Store | Cooloolabin Dam
North | Store | Enoggera Dam
North | Store | Ewen Maddock Dam
North | Store | North Pine Dam
North | Store | Poona Dam
North | Store | Sideling Creek Dam
North | Store | Wappa Dam
North | Treat | Borumba Dam WTP
North | Treat | Dayboro WTP
North | Treat | Enoggera WTP
North | Treat | Ewen Maddock WTP
North | Treat | Image Flat WTP
North | Treat | Jimna WTP
North | Treat | Kenilworth WTP
North | Treat | Kilcoy WTP
North | Treat | Landers Shute WTP
North | Treat | Linville WTP
North | Treat | Noosa WTP
North | Treat | North Pine WTP
North | Treat | Petrie WTP
North | Other | Linville Reservoir (Site Type: WTP)
South | Store | Hinze Dam
South | Store | Leslie Harrison Dam
South | Store | Little Nerang Dam
South | Store | Maroon Dam
South | Store | Moogerah Dam
South | Store | Nindooinbah Dam
South | Store | Wyaralong Dam
South | Treat | Amity Point WTP
South | Treat | Beaudesert WTP
South | Treat | Boonah-Kalbar WTP
South | Treat | Canungra WTP
South | Treat | Capalaba WTP
South | Treat | Dunwich WTP
South | Treat | Hinze Dam WTP
South | Treat | Kooralbyn WTP
South | Treat | Maroon Dam WTP
South | Treat | Molendinar WTP
South | Treat | Moogerah Dam WTP
South | Treat | Mudgeeraba WTP
South | Treat | North Stradbroke Island WTP
South | Treat | Point Lookout WTP
South | Treat | Rathdowney WTP