## Template Cover Page
Template
E-TMP-STD-007
Arc Flash Hazard Label Template
Document Number: TEM-00371
This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.
Rev no. | Description | Process Owner |  | Approved for issue
|  | Position | Name | Position | Name | Date
1 | Issued for Use | Lead Electrical Engineer | Refer Supporting info in REX | Principal Engineering Standards and Assurance | Refer Supporting Info in REX | 2024-12-11
Subject Matter Expert Authorisation
Rev no. | Name |  | Date |  | RPEQ #
1 | Refer Document Properties in REX |  | 2024-12-03 |  | Refer Doc Properties in REX
DOCUMENT SENSITIVITY: OFFICIAL (Public)

## Cover Page
Facility Code - Facility Name
Project Number - Project Name
Arc Flash Hazard Labels
Document Number: XXXXXXX
This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.
Rev no. | Description | Prepared by: | Checked by: | Approved by:
|  | Name | Name | Name | RPEQ No. | Company | Date

## Type 1 - DANGER
ARC FLASH AND SHOCK HAZARD
DANGER

## Type 2 - PPE REQUIRED
ARC FLASH AND SHOCK HAZARD
Equipment ID: | TRH-E-9SWB002 |  |  |  | Report Date: |  | 2024-12-28
Position: | NON-INCOMER CIRCUITS |  |  |  | Report No: |  | ESRGA-99-REP- TRH-002
Voltage: | 400 |  |  |  | Incident Energy (cal/cm²): |  | 18
ACTIVITY |  |  | DOORS CLOSED |  |  | DOORS OPEN
VISUAL INSPECTION |  |  | CAT 0 |  |  | CAT 4
OPERATING CONTROLS |  |  | CAT 2 |  |  | CAT 4
ROUTINE SWITCHING |  |  | CAT 4 |  |  | CAT 4
RACKING |  |  | N/A |  |  | N/A
ELECTRICAL TESTING |  |  | CAT 4 |  |  | CAT 4
ARC FLASH BOUNDARY ONLY APPLICABLE WHEN EQUIPMENT ENERGISED
CATEGORY: |  | 4 |  | BOUNDARY: |  |  |  | 3
COMMENTS
Switchboard condition:
Arc Flash Containment Tests:
PPE REQUIRED
DANGER

## Type 3 - EXTREME
ARC FLASH AND SHOCK HAZARD
Equipment ID: | TRH-E-9SWB003 |  | Report Date: | 2024-12-28
Position: | ALL |  | Report No: | ESRGA-99-REP- TRH-002
Voltage: | 400 |  | Incident Energy (cal/cm²): | 50
RISK ASSESSMENT AUTHORISED BY ELECTRICAL SUPERVISOR IS REQUIRED FOR ANY INTERACTION WITH THIS EQUIPMENT WHILE ENERGISED
ARC FLASH BOUNDARY ONLY APPLICABLE WHEN EQUIPMENT ENERGISED
EXTREME INCIDENT ENERGY EXCEEDS CAT 4 PPE LIMIT |  | BOUNDARY: |  |  | 3.9
COMMENTS
Switchboard condition:
Arc Flash Containment Tests:
EXTREME ARC FLASH INCIDENT ENERGY
DANGER

## Type 4 - COMPACT CAT 0
ARC FLASH AND SHOCK HAZARD
Equipment ID: |  | TRH-E-9SWB001
Position: |  | CONTROL TIER ONLY
Voltage: |  | 230 V
Report Date: |  | 2024-12-28
Report No: |  | ESRGA-99-REP-TRH-002
Incident Energy: |  | LESS THAN 1.2 cal/cm²
COMMENTS
PPE: CAT 0
BOUNDARY: <0.5m

## Type 5 - PPE CATEGORIES
APPLY PPE LEVELS LISTED BELOW AS SPECIFIED ON INDIVIDUAL EQUIPMENT SIGNS
CAT 0 | CAT 2 | CAT 4
INCIDENT ENERGY UP TO 1.2 cal/cm² | INCIDENT ENERGY UP TO 7.9 cal/cm² | INCIDENT ENERGY UP TO 40 Cal/cm²
• UNTREATED NATURAL FIBRE LONG SLEEVE SHIRT AND PANTS OR COVERALLS • SAFETY HELMET (AS REQUIRED) • LEATHER WORKWEAR GLOVES (AS REQUIRED) • SAFETY GLASSES OR SAFETY GOGGLES • FACE SHIELD (AS REQUIRED) • HEARING PROTECTION (AS REQUIRED) • SAFETY BOOTS | • ARC-RATED PPE WITH MINIMUM RATING 7.9 cal/cm² • ARC-RATED LONG SLEEVE SHIRT & PANTS OR COVERALLS • ARC-RATED SAFETY HELMET WITH FACE SHIELD, CHIN RETURN & BALACLAVA - OR ARC-RATED HOOD WITH HELMET • ARC-RATED GLOVES OR VOLTAGE-RATED GLOVES WITH LEATHER PROTECTORS • SAFETY GLASSES • HEARING PROTECTION • SAFETY BOOTS | • ARC-RATED PPE WITH MINIMUM RATING 40 cal/cm² • ARC-RATED SUIT AND HOOD WITH HELMET • ARC-RATED GLOVES OR VOLTAGE RATED GLOVES WITH LEATHER PROTECTORS • SAFETY GLASSES • HEARING PROTECTION • SAFETY BOOTS
ADDITIONAL MINIMUM PPE APPLIES TO ELECTRICAL WORK ON OR NEAR ENERGISED ELECTRICAL EQUIPMENT (INCLUDING FAULT FINDING, TESTING AND PROVING ISOLATION); AND HV OPERATION. ADD THE FOLLOWING REQUIREMENTS TO THE CAT 0/2/4 PPE LISTED ABOVE: • FULL LENGTH ARC RATED CLOTHING • VOLTAGE-RATED GLOVES WITH LEATHER PROTECTORS • ELECTRICAL NON-CONDUCTIVE SAFETY BOOTS • ELECTRICAL INSULATED MAT (AS REQUIRED) • LOW VOLTAGE RESCUE KIT (AS REQUIRED) REFER TO PRO-00006 ELECTRICAL SAFETY PROCEDURE FOR DETAILS
ARC FLASH PPE CATEGORIES
TEM-00371 Type 5
Rev 1 - 3/12/2024
HOLD 1
TYPE 5 LABEL TO BE CONFIRMED, PENDING ONGOING REVIEW OF PRO-00006 ELECTRICAL SAFETY PROCEDURE.
CONTACT SEQWATER ENGINEERING BEFORE PRINTING THIS LABEL.

## Print Details
Label | Size |  | Material
| Width (mm) | Height (mm)
Type 1 - DANGER | 125 | 70 | UV Resistant Laminated Vinyl
Type 2 - PPE REQUIRED | 125 | 95 | UV Resistant Laminated Vinyl
Type 3 - EXTREME | 125 | 95 | UV Resistant Laminated Vinyl
Type 4 - COMPACT CAT 0 | 80 | 60 | UV Resistant Laminated Vinyl
Type 5 - PPE CATEGORIES | 170 | 150 | UV Resistant Laminated Vinyl