## TEMPLATE COVER PAGE
Template
I-TMP-STD-003
Document number: TEM-00210
LOCATION: e.g. EAST BANK WTP
Document Number: I-LST-AAA-XXX (Contact engineering@seqwater.com.au for document number)
REX ID: Contact engineering@seqwater.com.au
This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.
|  |  | Author |  |  | Approved for issue
Rev No | Date | Document Status | Position | Name | Signature | Position | Name | Signature
1 | 14/11/2017 | Original Version | Senior Engineer, Process | Refer Supporting info in REX |  | Principal Engineer Standards & Specifications | Refer Supporting Info in REX
2 | 24/11/2020 | Review cycle 2020 | OT Engineer | Refer Supporting info in REX |  | Team Leader Process & Analysis | Refer Supporting Info in REX
3 | 2022-11-29 | Review Cycle 2022 | OT Engineer | Refer Supporting info in REX |  | Team Leader Process & Analysis | Refer Supporting Info in REX
4 | 2025-11-11 | Review Cycle 2025 | OT Engineer | Refer Supporting info in REX |  | Team Leader Process & Analysis | Refer Supporting Info in REX
DOCUMENT SENSITIVITY: OFFICIAL (Public)
Delete This page before submitting to Process Control Systems Folders

## Title Block
REVISION (As Constructed ) |  |  |  |  | CONTRACTOR LOGO | LOCATION: eg. EAST BANK WTP |  |  | AS CONSTRUCTED
NO. | DESCRIPTION | DATE | PREPARED BY | CHECKED BY |  |  |  |  | APPROVER
[6 empty] | SUBLOCATION: eg. RAW WATER PUMP STATION |  |  | DATE
SIGNATURE
WORK DESCRIPTION: eg. WELL G PUMP REFURBISHMENT
RPEQ No.
FOR CONSTRUCTION
[6 empty] | DOCUMENT NUMBER : eg. I-LST-AAA-YYY |  |  | APPROVER
DATE
[5 empty] | PROJECT NO: | PLC NNN I/O SCHEDULE | REX ID: ANN/NNNNNN | I-LST-XXX-00X | SIGNATURE
RPEQ No.
Notes:
The format provided in the IO list for Schnider ControlExpert tags is mandatory and needs to be followed within termination dwgs aswell.
The IO List is a maintained process control systems (PCS) document and the process control document coordinator (as per X-PRO-STD-019 Process Control Systems Information Maintenance) shall be contacted via engineering@seqwater.com.au for access to this document.
Document Number and REX ID - To be requested from PCS document coordinator through engineering@seqwater.com.au
Template cover page shall be replaced with project revision number and Author and approval details
PLC Number - Replace NNN with the actual PLC Number as per equipment tagging philosophy. Each PLC shall have it's own IO list document
The "Rack Layout" shall detail the cards installed. Any new card added shall be coloured Green for that revision.
All columns on IO List are mandatory to filled. New IOs added shall be marked as green and the revision number column shall be updated.
Information within body of template is for example only.
When project is completed, the "As Constructed " Revision shall be submitted to PCS document coordinator through email engineering@seqwater.com.au
The main cover page shall only show the revision number for "AS CONSTRUCTED", in between revisions shall have alphabetical suffix and shall be save as project
This text box shall be deleted when the template is populated
Information within body of template is for example only.
Update the Cover Page table related to project details.
Note on K2: Clear the text LOCATION: eg. Insert only the Location.
Note on I3: Peer Review
Note on K4: Remove the text SUBLOCATION: eg. Insert only sublocation name.
Note on K6: Remove the text WORK DESCRIPTION: eg. Insert only name of work description
Note on K9: Clear and remove text DOCUMENT NUMBER: eg. Insert only document number & start with I-LST-
Note on K11: Refer to note 5
Note on L11: Refer to note 3
Note on M11: Refer note 3, The document number shall be as given by PCS documentation
Note on I13: PLEASE NOTE: Once the notes are understood hide them by Right-clicking somewhere on the cell and select hide the comment.

## RACK LAYOUT
NOTES
1. Abbreviations: Programmable Logic Controller (PLC), Digital Input (DI), Digital Output (DO), Analogue Input (AI), Analogue Output (AO), Communications (COMMS).
2. Following are examples of a Schneider and a Siemens PLC and IO layout
3. The following arrangement is only for M580 and S7-15xx PLC. This can be modified as per project requirement
Revision
Schnider PLC and IO Layout example
Main Rack - RACK 00
| Slot 00 | Slot 01 | Slot 02 | Slot 03
| Part | Part |  | Part
| Number | Number | BMENOC0321 | Number
| Firmware Ver. # | Firmware Ver. # | SV1.08 | Firmware Ver. #
| PLC | PLC | Network | Description
|  |  | Interface Card | Description
Remote Rack - RACK 01
| Slot 00 | Slot 01 | Slot 02 | Slot 03 | Slot 04 | Slot 05 | Slot 06 | Slot 07 | Slot 08 | Slot 09 | Slot 10 | Slot 11 | Slot 12
|  | Part | Part | Part |  |  |  |  | Part | Part | Part | Part | Part
| BMECRA31210 | Number | Number | Number | BMXDDI3202K | BMXDDO3202K | BMXAMI0810 | BMXAMO0802 | Number | Number | Number | Number | Number
| SV2.70 | Firmware Ver. # | Firmware Ver. # | Firmware Ver. # | NA | NA | SV1.70 | SV1.20 | Firmware Ver. # | Firmware Ver. # | Firmware Ver. # | Firmware Ver. # | Firmware Ver. #
| Network | Description | Description | Description | 32 Point | 32 Point | 8 Channel | 8 Channel | Description | Description | Description | Description | Description
| Interface Card | Description | Description | Description | Digital Input | Digital Output | Analog Input | Analog Output | Description | Description | Description | Description | Description
Siemens PLC and IO Layout example
Main Node - Node 00
Firmware Ver. #
S7-15XX
PLC
Remote Node - Node 01
| Slot 00 | Slot 01 | Slot 02 | Slot 03 | Slot 04
| 6ES7155-6AU01-0CN0 | 6ES7131-6BH01-0BA0 | 6ES7132-6BF61-0AA0 | 6ES7134-6GD01-0BA1 | 6ES7135-6HD00-0BA1
| V4.2.0 | NA | NA | V2.0.1 | V1.1.3
| ET200 SP | ET200 SP | ET200 SP | ET200 SP | ET200 SP
| PROFINET | 16 Point | 08 Point | 4 Channel | 4 Channel
| Interface mod. | Digital Input | Digital Output | Analog Input | Analog Output
Note on B8: Revision for the change in IO hardware. This revision needs to be changed in Rows as well as Columns. Latest revision details to stay. Old revision details should be removed
Note on J11: PLEASE NOTE: Once the notes are understood hide them by Right-clicking somewhere on the cell and select hide the comment.
Note on K32: Suggestion - To add PLC software verion detials for Control Expert and TIA

## IO LIST
IO Types | Total | Used | Spares | Spares%
DI | 3 | 3 | 0 | 0%
DO | 3 | 3 | 0 | 0%
AI | 3 | 3 | 0 | 0%
AO | 3 | 3 | 0 | 0%
NOTES
1. Abbreviations: Programmable Logic Controller (PLC), Digital Input (DI), Digital Output (DO), Analog Input (AI), Analog Output (AO), Communications (COMMS), PB_XX (Profibus IO type), PN_XX (Profinet_IO Type), MB_XX(Modbus_IO Type).
ADDRESS | RACK | EXTENSION | SLOT | CHANNEL | TYPE | PLC TAG | DESCRIPTION | OFF STATE / 4mA | ON STATE / 20mA | Raw Value | Comment | Rev.
Control Expert
MR00E00S04C00 | 0 | 0 | 4 | 0 | DI | TIF_8XVxx0101_iOPEN | Filter 1 Inlet Valve - Fully Opened | - | Open |  | Example tag for Schneider
RR01E01S03C01 | 1 | 1 | 3 | 1 | DO | TIF_8XVxx0101_qCLOSE | Filter 1 Inlet Valve - Close | - | Closed |  | Example tag for Schneider
MR00E00S06C01 | 0 | 0 | 6 | 1 | AI | TCP_4AITx0101_iTUR | Treated Water Turbidity Field input | 0 NTU | 400 NTU |  | Example tag for Schneider
MR00E00S07C00 | 0 | 0 | 7 | 0 | AO | TCP_1PMPx0201_qSPDSP | Lime dose PUMP 1 Speed Setpoint | 0% | 100% |  | Example tag for Schneider
TIA Portal
%I0.0 | 0 | 0 | 1 | 0 | DI | TIF_8XVxx0101_iOPEN | Filter 1 Inlet Valve - Fully Opened | - | Open |  | Example tag for TIA Portal
%Q10.0 | 0 | 0 | 7 | 0 | DO | TIF_8XVxx0101_qCLOSE | Filter 1 Inlet Valve - Close | - | Closed |  | Example tag for TIA Portal
%IW20 | 0 | 0 | 10 | 0 | AI | TCP_4AITx0101_iTUR | Treated Water Turbidity Field input | 0 NTU | 400 NTU |  | Example tag for TIA Portal
%QW50 | 0 | 0 | 14 | 0 | AO | TCP_1PMPx0201_qSPDSP | Lime dose PUMP 1 Speed Setpoint | 0% | 100% |  | Example tag for TIA Portal
Simatic S7
I0.0 | 0 | 0 | 1 | 0 | DI | TIF_8XVxx0101_iOPEN | Filter 1 Inlet Valve - Fully Opened | - | Open |  | Example tag for Simatic Manager
Q10.0 | 0 | 0 | 7 | 0 | DO | TIF_8XVxx0101_qCLOSE | Filter 1 Inlet Valve - Close | - | Closed |  | Example tag for Simatic Manager
IW20 | 0 | 0 | 10 | 0 | AI | TCP_4AITx0101_iTUR | Treated Water Turbidity Field input | 0 NTU | 400 NTU |  | Example tag for Simatic Manager
QW50 | 0 | 0 | 14 | 0 | AO | TCP_1PMPx0201_qSPDSP | Lime dose PUMP 1 Speed Setpoint | 0% | 100% |  | Example tag for Simatic Manager
Once the notes are understood hide the comments for ease of use. Use Monospace font for contents of the table
Do not to change font also
Do not to direct copy and paste, but paste values only to retain the destination format.
Note on H5: PLEASE NOTE: Once the notes are understood hide them by Right-clicking somewhere on the cell and select hide the comment.
Note on C13: This can be either Main Rack or Remote rack. Main rack will always have value '0 Remote rack can be 1,2,3… depending upon number of racks added
Note on D13: Extension of Main or Remote Rack
Note on G13: DI - Digital Input DO - Digital Output AI - Analog input AO - Analog Output
Note on H13: Tag naming should be as per I-SPE-STD-010, Control system Tag Naming
Note on J13: OFF STATE / 4mA with min- Limit & Eng. Unit for Analogs
Note on K13: ON STATE / 20mA with min- Limit & Eng. Unit for Analogs
Note on L13: Typically for an analog input or output this will display the channel's configured resolution (not the default/factory set resolution) Examples of reconfigured resolution; 0-10000 0-27648 0-32768
Note on M13: Informaiton about Instrument calibration and any functionality tips for the instrument can be added in Comments column here
Note on N13: Revision for the individual IOs added/updated. Latest revision details to stay. Old revision details should be removed
Note on B14: Use Monospace font for contents of the table Do not to change font also Do not to direct copy and paste, but paste values only to retain the destination format.
Note on B15: Default format, Example use MR00E00S04C00, Main PLC Rack_0 - Extension_0 -Slot 4 - Channel 0 RR01E00S03C00, Remote Rack_1 - Extension_0 - Slot_3 - Channel 1
Note on N15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The format of the excel sheet can not be locked and hence to maintain the as suggested(and agreed upon) comment to use Monospace font for PLC tag, a comment needs to be added to the sheet “not to change font also not to direct copy and paste, but to paste values only to retain the destination format.”