I-TMP-STD-005 Functional Description Part B

Document number: TEM-00222

This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.

| Ver No. | Description | Document Owner |  | Document Approver |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Position | Approval | Position | Approval | Approval Date |
| 5 | Amended Version | Lead Engineer - Operational Technology | Refer to supporting Info in Rex | Team Leader Process & Analysis | Refer to supporting Info in Rex | 24/01/2024 |
| This Engineering Standard was endorsed by an RPEQ on behalf of Seqwater. |  |  |  |  |  |  |

This page shall be deleted by the contractor.

# Approval Process

Where noted in this Template that Seqwater approval, attention or input shall or should be sought, the Seqwater Team Leader DTI Service Delivery - PAT (or their delegate) shall be responsible for reviewing or generating the technical response. A request for approval, attention or input shall made via the Seqwater Project Representative (for external parties) or via Seqwater’s Engineering mailbox (engineering@seqwater.com.au) (for internal parties).

# Changes from Previous Version

This Template will be regularly reviewed and updated, including the consideration of requested alterations, in accordance with Seqwater Procedure X-PRO-STD-004 Development and Review of Asset Standards.

Table 1 Changes from previous version

| Section Number | Change |
| --- | --- |
| Cover page | Cover page for the template and actual FD B document separated |
| All | Format changed to be more site specific than project specific |
| All sections | Major revision (rev 1 to 2) |

# Verification

Compliance with this document may be verified by internal audit.

# Further Information

Consult Seqwater’s Engineering mailbox Engineering@seqwater.com.au for following points prior to beginning work on FD B for any sites

Document type: Plantwide FD B or site specific

Document number

REX ID

Delete the first two Template cover page of this document for the actual FD B document.

For further information please contact the owner of this document.

This page shall be deleted by the contractor.

Insert name of site/area/project

Functional Description Part B

  - Date: DD/MM/YYYY

**please contact corporate communications for alternative cover options**

Doc. No.: Request from Seqwater as per X-PRO-STD-019

REX ID: XX/XXXX Request from Seqwater as per X-PRO-STD-019

Template Document number: TEM-00222

Revision History

| Date | Rev | Description of Comments or Changes | Author | Checked By | Approved By |
| --- | --- | --- | --- | --- | --- |
| dd/mm/year | 0 | ‘Add project details If updated as part of project’ | Full name - Position Company | Full name - Position Company | Full name – RPEQ # Position Company |

The extent of changes to this document is highlight in green.

Review History

| Date | Rev | Reviewer | Position | Comments Received | Comments Incorporated |
| --- | --- | --- | --- | --- | --- |

Contents

1.	Purpose	7

2.	Audience	7

3.	Abbreviations	8

4.	References & Associated Documents	9

5.	Holds List	10

6.	Scope	11

7.	Overall Plant Control Philosophy	11

8.	Plant Control System	13

8.1.	PLC	13

8.2.	Application Program Architecture	13

8.3.	Program Block Usage	14

8.3.1.	Seqwater Standard PLC Blocks	14

8.3.2.	Site Specific Software PLC Blocks	14

8.4.	Sequential Start-Up of the Entire Plant	14

8.5.	Normal Sequential Shutdown of the entire plant	16

8.6.	Abnormal Shutdown Plant of the entire plant	16

8.7.	Control Reliability	16

8.7.1.	Control System Architecture Reliability	16

8.8.	Common Alarms	17

9.	SCADA Configuration Details	17

9.1.	SCADA System	17

9.2.	Software Objects Library	17

9.3.	Site Specific SCADA Objects	18

9.4.	Graphic display list	18

9.5.	Trending	18

9.6.	SCADA Hierarchy Structure and Menu Structure	18

9.6.1.	Displays/Screen Graphics	19

9.6.2.	Indication Signals	19

9.7.	SCADA Database Configuration Details	19

9.8.	Reporting	19

9.8.1.	HL pump Reporting (e.g., only)	19

9.9.	User roles and Privileges Levels	20

10.	Communication Details	20

10.1.	Networks	20

10.2.	Communication Hardware	20

10.3.	IP Address Schema	20

10.4.	Seqwater WAN Connection	20

10.5.	Network Diagnostic	20

11.	Name of Process Group e.g. Raw Water Pump Station	21

11.1.	Process Overview	21

11.2.	Control System Hierarchy (Can be an Appendices)	21

11.3.	Calculations	21

11.4.	Equipment and Instrumentation	22

11.5.	Equipment or Instrument Scaling	23

11.6.	Control	23

11.7.	Control Loops	24

11.7.1.	Settled Water Channel Level Primary Controller (E.G. Only)	24

11.8.	Hardware Interlocks and Permissive	25

11.9.	Sequence Control	26

11.10.	Alarms	27

11.11.	Events & Indications	27

11.12.	Setpoints and Parameters	28

12.	PLC Signal Processing Requirements	28

Appendix A	29

Purpose

How to use this standard/template:

This template is used to produce a Functional Description Part B. Further details on the development of Functional Descriptions are contained in B-SPE-STD-005 Functional Description Documentation.

All table & figure captions, cross references, table of contents etc. are automatically updated by pressing ‘Ctrl + A’ or right clicking over any greyed-out captions and selecting ‘update field’.

All items in grey highlighting are for reference and guidance. These should be changed or deleted as required.

For facility code of the asset refer to X-PRO-STD-002 Engineering Drawing Number Procedure, Appendix A.

The objective of this Functional Description Part B is to describe the site / area / project functionality. It explains and details the equipment hierarchy, redundancy, pre-start, start-up, operation, shutdown and isolation conditions, constraints, interlock & fault conditions, abnormal operation, safety features and ancillary information. It is intended to provide all the necessary details essential for developing application software and configuration of control system for the plant.

In addition to this Functional Description Part B is Part A. The inter-relationship between Part A and B are described in B-SPE-STD-005 Functional Description Documentation.

This Functional Description is a ‘dynamic document’ and should be updated with changes to the asset design and operational control intent.

This Functional Description is to be read in conjunction with the site / area / project P&IDs, PFDs and FD Part A as specified in Section 4.

This document does not include operational procedures. This is to be defined within Operations Manuals for site / area / project.

The Functional Description is a document that should be created by the designer. It is intended to provide all the necessary detail to describe the processes, the control, and all information necessary to develop and implement the control system for the plant. It is not an Operations and Maintenance Manual.

Audience

This document has been developed specifically for, but not limited to, the following:

Control System Engineers

Control System Programmers

Process Engineers

Abbreviations

| Abbreviation | Description |
| --- | --- |
| CCP | Critical Control Points |
| FB | Function Blocks |
| FC | Functions |
| FD | Functional Description |
| HACCP | Hazard Analysis and Critical Control Points |
| I/O | Input / Output |
| MAOP | Maximum Allowance Operating Pressure |
| MCC | Motor Control Centre |
| NAS | Network attached storage |
| OHS | Occupational, Health and Safety |
| P&ID | Piping and Instrumentation Diagram |
| PFD | Process Flow Diagram |
| PLC | Programmable Logic Controller |
| RIO | Remote Input Output |
| SCADA | Supervisory Control and Data Acquisition |
| SFC | Sequential function chart |
| UC Number | Supervisory Control Number |
| UPS | Uninterruptable Power Supply |
| WTP | Water Treatment Plant |

References & Associated Documents

Table 4.1 Site Specific Referenced Documents

| Description | Status | Location | Rev |
| --- | --- | --- | --- |
| Functional Description Part A | [Active or draft] | [REX ID] |  |
| Cause & Effect Matrix | [Active or draft] | [REX ID] |  |
| O&M manual | [Active or draft] | [REX ID] |  |
| Vendor Process description & Vendor Process drawings | [Active or draft] | [REX ID] |  |
| Alarm Register | [Active or draft] | [REX ID] |  |
| SCADA Setpoint Register | [Active or draft] | [REX ID] |  |
| Control Network Drawings | [Active or draft] | [REX ID] |  |
| I/O List | [Active or draft] | [REX ID] |  |
| IP Register | [Active or draft] | [REX ID] |  |

Table 4.2 P&IDs

| Drawing Number | Description | Rev |
| --- | --- | --- |
| Add P&ID related to projects |  |  |

Table 4.3 Generic Referenced Documents

| Description | Status | Location | Rev |
| --- | --- | --- | --- |
| SPE-00361 Control System Design and Construction (I-SPE-STD-013) | Active | REX/Waternet |  |
| PLN-00388 Monitoring and Control System Alarm Strategy (I-SPE-STD-006) | Active | REX/Waternet |  |
| SPE-00356 High Priority Alarms and Interlocks management (I-SPE-STD-005) | Active | REX/Waternet |  |
| SPE-00360 Control Systems Testing (I-SPE- STD-11) | Active | REX/Waternet |  |
| SPE-00359 Control System Tag Naming (I-SPE-STD-010) | Active | REX/Waternet |  |
| SPE-00358 I-SPE-STD-009 Control Systems Architecture | Active | REX/Waternet |  |
| SPE-00349 Functional Description Documentation (B-SPE-STD-005) | Active | REX/Waternet |  |
| PRO-02329 Process Control Systems Information Maintenance Procedure (X-PRO-STD-019) | Active | REX/Waternet |  |
| Reference 1 | [Active or draft] | [REX ID] |  |

Holds List

The following HOLDs are noted throughout this document. These are highlighted yellow and noted as TBC for ease of finding.

Table 5 List of HOLDs

| HOLD No. | Section | Description of HOLD | Status |
| --- | --- | --- | --- |
|  |  |  | Open/Closed |

Part B

Scope

The scope of this document relates to the ‘site name’ plant control system programming functionality. It mainly gives following details:

Process overview in brief (details in the plant FD A ‘FD A Document number’).

Details for PLC configuring and developing the application program as per process requirements including interlocking or sequence step actions and conditions.

Details for SCADA configuration and graphics design as per operator interface requirements.

Associated risks and plant safety.

This section shall also list’ the boundaries of the plant control covered.

Overall Plant Control Philosophy

This section shall cover the process overview briefly which can be used for programming the control system. Some points below can be covered briefly keeping the description as process related.

Start up

Shut down

Form of logic implemented (regulatory / sequence / interlock)

Group or plant sequences with details as below (add table below where applicable):

Table 7.1 Group or plant sequence table (examples in grey below)

| Top Level Controller | TLI_9UCxx0001 | Main Supervisory Controller |
| --- | --- | --- |
| Subordinate Controllers | TLI_9UCxx0002 | Production Supervisory Controller |
|  | TLI_1UCxx0001 | Raw Water Supervisory Controller |
|  | TLI_2UCxx0001 | Membrane 1 Supervisory Controller |

Interfaces to other plants/ systems

Interlocks for plant supervisory controllers such as crash interlock, shutdown interlocks, service permissive interlocks and device monitoring interlock (Add table if applicable, refer to I-SPE-STD-013 for further details)

Control Modes (reference to I-SPE-STD-013 (and revision number if different to the current version) and only site-specific details in this document). Generic block diagrams as seen in the e.g., below can also be added:

- Schematic is an example only to be deleted.

Figure 7-1 Overview of PID Mode Selections and Setpoint Handling Example

Plant Control System

This section gives the overview of the control systems and software being used for plant.

The plant is controlled by PLCs as detailed in the following sections.

PLC

Table 8.1 PLC  being used for control of site/equipment

| Equipment Tag | Equipment Description | Equipment Type | Location |
| --- | --- | --- | --- |

Application Program Architecture

Describe the controller hierarchy in application program (preferably in block diagram) giving references to respective Process group section. Wherever possible the controller’s names as per tag naming philosophy also to be added.

Schematic is an example only, to be deleted.

Figure 8-2 Controller Hierarchy Example

Refer to FD A for the overall process hierarchical table, representing a model of the physical assets under control.

Further details of group process control are detailed in the individual process group sections.

Program Block Usage

Seqwater Standard PLC Blocks

Table 8.3.1 Standard PLC Blocks

| Name | Description | Datasheet No. | Rev |
| --- | --- | --- | --- |

Site Specific Software PLC Blocks

Site specific Functions (FC) and Function Blocks (FBs) or User Defined Data Types developed for the plant application program are as below.

Table 8.3.2 Site Specific Software PLC Blocks

| Name | Description | Datasheet No. | REX ID | Rev |
| --- | --- | --- | --- | --- |

Sequential Start-Up of the Entire Plant

This section briefly describes the process start up. Refer to FD A document for details.

Preference is to have Process start-up to be represented in a graphical flowchart format by analysing the data from FD A.

Schematic is an example only, to be deleted.

Figure 8-4 Sequential Start-Up Diagram Example

Representation of process in flow chart does not necessarily means that it has to be a sequential logic written in sequential functional chart (SFC) or other sequencing PLC languages.

Option of brief description (as per example below) shall be acceptable, but not preferred:

If the plant permissive conditions are met, the plant will start as below (see links to individual start-up sequences):

Wait for the Clear Water Reservoir level to drop below the (operator adjustable) start-up set point.

Delay for 30 seconds.

Ramp up Raw Water flow: begin ramp up of summated RW flow at operator adjustable rate.

Enable filter flow control.

Wait until Raw Water flow reaches plant start-up flow.

Start Service Water system and enable pre-filter chemical dosing systems.

Wait until Filtered Water flow reaches plant start-up flow.

Start post-filter chemical dosing systems.

Wait until Raw Water flow reaches final set point.

Enable Raw Water flow control.

Set plant status to ‘Online’.

Normal Sequential Shutdown of the entire plant

Refer to FD A document for details.

Preference is to have a flow chart representation to describe sequence steps and transition condition for normal shutdown. Otherwise, a brief description of the shutdown sequence is expected.

Abnormal Shutdown Plant of the entire plant

An emergency shutdown is initiated by operator input or failure of the on-site power generator or any site major fault.

Flow Chart representation is desired also some points to consider in this section as below:

Abnormal shut down conditions e.g., Power failure, communication failure, process group unavailability etc.

How the overall plant control responds to the above conditions.

Auto restart of the plant shall be disabled in case of Abnormal shutdown.

Avoid duplication by referring to other sections of the process group in the documents.

Control Reliability

Control System Architecture Reliability

This section shall describe how the control system design addresses the failure modes which can affect the reliability of the control systems. Some guidewords for failure modes are as below:

Power supply - Redundant Power Supply, UPS backup, PLC Rack and RIO Rack separate Power Supply;

Instrumentation - Use of redundant instrument/channels for critical parameters or use of instrumentation with higher reliability;

Architecture - Class I, II or III depending on the reliability requirements;

Hardware failure - Fail Safe wiring and logic;

Common cause failures - Distribution of equipment / IOs;

Communication failures - Fail safe actions; or

Any Specific conditions that will ensure the plant control brings the process to a safe state, in case of any of the above failures.

Common Alarms

Refer to Alarm list I-LST-XXX-XXX for details on plant common alarms.

Some common examples of alarms to be considered as common alarms are as below:

Overall plant safety alarms / HACCP

PLC Diagnostic alarms

Communication failure alarms

Electrical instrumentation alarms

Fire Safety Alarms

Safety Showers

It is not expected to describe the third-party equipment alarms (lights and beacon) which are not connected to the control system in the FD Part B.

SCADA Configuration Details

SCADA System

‘Product name of SCADA system’ system provides an operator interface to the plant control system. Refer to System architecture drawing ‘Number and REX ID ‘for further details.

SCADA System design and configuration shall follow the requirements of I-SPE-STD-013 Control Systems Design and Construction.

Site specific SCADA system details are as below:

Table 9.1 Site Specific SCADA system details

| Equipment Tag | Equipment Type | Equipment Name | Location |
| --- | --- | --- | --- |
|  | SCADA Server | As per tag naming philosophy |  |
|  | SCADA Client |  |  |
|  | SCADA Thin Clients |  |  |
|  | Historian |  |  |

Refer to ‘Architecture drawing number’ for further details.

Software Objects Library

All devices and graphics on SCADA use the ‘Seqwater standard library’ or ‘use the current site name’ specific object library.

In case of site-specific library details needs to be filled in in the below table:

Table 9.2 Software Objects Library

| Object Name | Description | Datasheet No. | REX ID | Rev |
| --- | --- | --- | --- | --- |

Site Specific SCADA Objects

Site specific SCADA objects or SCADA objects developed for the plant application are as below.

Table 9.3 Site Specific Software PLC Blocks

| Name | Description | Datasheet No. | REX ID | Rev |
| --- | --- | --- | --- | --- |

Graphic display list

The following table below gives the list of graphics for plant control of ‘Site Name’

Mark the new graphics in green, and the deleted graphics in Blue.

Table 9.4 Graphics Display List

| Graphics Name | Description |
| --- | --- |
|  | Plant Process Overview |
|  | Network Overview |
|  | PLC and Communication diagnostic |
|  | Power System Overview |
|  | Water Quality |
|  | Treated Water Reservoir Overview |

Trending

Trending, trend sampling, events and logging periods have been configured as per the Trends section in I-SPE-STD-013 Control System Design and Construction.

SCADA Hierarchy Structure and Menu Structure

Plant wide hierarchy of SCADA displays and menu structure has been developed as per I- SPE-STD-013 Control System Design and Construction standard. In case of site-specific library being used, the details shall be referred in datasheet listed in Table 9.3 Site Specific Software PLC Blocks.

Some key points to cover are as below:

Layout of popup menus and faceplates

Button functions

Nested menu layers

Displays/Screen Graphics

Insert all details/redline mark-ups /print screens of displays and screens for the programmer to build new screen or modify existing screens. This shall stay in the ‘For Construction’ FD Part B.

In the ‘As constructed ‘ FD Part B these details shall be deleted and referred to Section 4.3

Indication Signals

Refer to standard I-SPE-STD-013 for further details.

Plant specific details/graphics of default indication signals on SCADA such as below shall be mentioned here:

Alarm, Warning and Signal Events

Operational Mode

Simulation and Bypass Events

Along with the default indications some Device Block icons have additional information such as process variable readouts, device status indicators and graphical animations. These shall be referred to the respective datasheets.

SCADA Database Configuration Details

For further information on SCADA database refer section SCADA Software, subsection SCADA Database in I-SPE-STD-013 Control Systems Design and Construction standard.

This section is to describe how the SCADA Database is configured. Include information such as data capture frequency, rapid trend data retention periods, archiving frequency, manual/automatic backup configuration, hardware setup (Network attached storage (NAS) drive, dedicated historian server, etc.).

Reporting

For standard report configuration requirements refer to the Reporting section in I-SPE-STD-013 Control Systems Design and Construction standard.

Table 9.8 Site Name Generated Reports

| Report Number | Title | Type |
| --- | --- | --- |
| 1 | Water Treatment Plant Data | Free Format |
| 2 | Pump Status Report | Microsoft Excel |
| 4 | Hourly Report | Free Format |
| 5 | Daily Report | Free Format |
| 6 | HL Pumps Running | Alarm and Event |
| 7 | Alarm Disabled Report | Point Attribute |

The site-specific reports developed are as per following sections.

HL pump Reporting (e.g., only)

Configuration details of any site-specific reports to be developed need to be detailed as sub sections in FD part B revision ‘For Construction’.

In the FD part B revision ‘As Constructed ‘ only the report name is to be listed in Table 9.8 and all configuration details removed from this section.

User roles and Privileges Levels

Refer to the user roles and privileges in I-SPE-STD-013 and I-SPE-STD-005 for more details.

Additionally, this section describes if any site-specific levels and specific privileges are required. (e.g., for interlocks bypass, alarm acknowledge, etc.).

Communication Details

Networks

The site communication network is designed as per I-SPE-STD-009 Control Systems Architecture.

This section provides details of communication network as mentioned in the following sections:

SCADA LAN, PLC LAN and RIO Lan.

PLC to PLC communication (intra site / external Seqwater site).

Radio communication.

Digital communication details (Ethernet TCP/IP, Fieldbus, profibus, profinet etc.).

Interfaces to 3rd party equipment.

Interfaces to external parties such as Unity water etc.

Communication Hardware

Details of communication cabinet for the plant are listed in the table below:

Table 10.2 Communication Hardware

| Cabinet Equipment No | Description | Location |
| --- | --- | --- |

For other hardware details refer to the Site-specific Architecture Drawing REX ID.

IP Address Schema

Refer to the Site-specific IP Register / Schema ‘Document Number’ and ‘REX ID’.

Seqwater WAN Connection

The Remote access requirements for the process group are as below:

Network Diagnostic

Diagnostic details are configured as per ‘Communication and Diagnostic’ section in I-SPE-STD-013. Additionally, this section specifies the site-specific network diagnostic signals.

Name of Process Group e.g. Raw Water Pump Station

Process Overview

Provide a brief overview of how this Process Group operation/functional unit is controlled in form of a block diagram. It shall be helpful to add in the ‘UC’ numbers on each of these controllers seen in Figure 11-1 Control System Hierarchy Example. Avoid repeat of copying word details from FD A.

Control System Hierarchy (Can be an Appendices)

This section shall display key objects that make up the control system hierarchy. A flow chart representation as below shall be a desired option (with supervisory block names as per PLC logic included).

Figure 11-1 Control System Hierarchy Example

Calculations

Details on any calculations used for process control such as dosing calculations etc. and its purpose shall be described in this section.

Tie up calcs in FD A and Vendor Datasheet here with some explanation to link both, wherever possible tag number to be provided in the equation.

sVREQ = mFPROC × mDRREQ × 0.36cSG × cCONC

Where  sVREQ = Calculated dose rate in L/hr

mDRREQ=  Flow Paced SP in mg/L from SCADA

mFPROC = 100-FIT-001 flow rate in L/s

cCONC = Solution concentration SP in % w/w from SCADA

cSG = Specific Gravity SP from SCADA

Equation X: Dosing Rate Calculation Example

The desired flowrate in flowpaced dosing mode is to be calculated using the Seqwater library block “Dose_Calc” (see datasheet I-DSH-STD-062).

Wherever possible tag number to be provided in the equation.

Equipment and Instrumentation

List the equipment and instrumentation that is under control from this Process Group. Items that are under control from subordinate Plant Units should be listed in that section, not as part of this section.

Table 11.4.1 Process Unit Equipment List

| Equipment Identifier | Description |
| --- | --- |
| TMG-3PMD001 (800-PMP-005)* | Alum Dosing Pump |
| TWB-M-1FAN001 | Raw Water Pump Station Vent Fan 1 |
| TWB-V-1XV400 | Raw Water Pump 4 Delivery Valve |

*Note: For new instruments the equipment identifier needs to match with new tagging philosophy, in case of existing equipment enter new as well as old equipment identifier if not updated on P&ID.

Table 11.4.2 Process Unit Instrument List

| Instrument Identifier | Description1 |
| --- | --- |
| TMG-3FIT001 | Alum Dosing Flowmeter |
| TWB-V-1XV100 | Raw Water Pump 1 Delivery Valve |

Refer to the IO List for details on range and units

Equipment or Instrument Scaling

This section shall refer to the site standard IO List (not a project specific document).

Only any special scaling requirements for any equipment if required.

Table 11.5 Equipment with special scaling requirements

| Equipment Identifier | Raw Min | Raw Max | Engineering Unit | Engg Min | Engg Max |
| --- | --- | --- | --- | --- | --- |

Control

The control system application software for this process group is configured in the ‘PLC name’.

For management of ‘Name of Process Group’ system the ‘name of supervisory control ‘ is the highest level of the supervisory control. The control system hierarchy between the process is as seen in figure XXX below: Process Units is also listed here.

List the equipment that is under control from this Process Group preferably in form of block diagram, example below:

Figure 11-2 Control System Hierarchy for ‘Name of Process group’

Or alternatively it can be shown in a table format as below:

Table 11.6 Control System Hierarchy for ‘Name of Process Group’

| Process Group | PLC Name | Process Unit Supervisory Controller | Process Equipment |
| --- | --- | --- | --- |
| Raw Water Pump Station 1UC-XXX |  | 1UC-001 Raw Water Pump Set 1 | Raw Water Pump 1 |
|  |  |  | Raw Water Pump 1 Delivery Valve |
|  |  | 1UC-002 Raw Water Pump Set 2 | Raw Water Pump 2 |
|  |  |  | Raw Water Pump 2 Delivery Valve |
|  |  |  | Raw Water Pump 2 Cooling Water Valve |
|  |  |  | Raw Water Vent Fan 1 |
|  |  | 1UC-003 Raw Water Pump Set 3 | Raw Water Pump 3 |
|  |  |  | Raw Water Pump 3 Delivery Valve |
|  |  | 1UC-004 Raw Water Pump Set 4 | Raw Water Pump 4 |
|  |  |  | Raw Water Pump 4 Delivery Valve |
|  |  |  | Raw Water Pump 4 Cooling Water Valve |
|  |  |  | Raw Water Vent Fan 2 |
|  |  | 1UC-005 Raw Water Pump Set 5 | Raw Water Pump 5 |
|  |  |  | Raw Water Pump 5 Delivery Valve |

Describe any control system functionality that is not captured in other parts of this section.

Control Loops

Specify how many control loops are existing in the process i.e. how many analog loops and digital control loops. For analog control loops, further specify whether it is PID based, or the output of the analog loops is based on calculations.

Table 11.7 Process Group ‘Name’ Control Loops

| Tag | Type | Short Description/ Function |
| --- | --- | --- |
| TEB_2LICx0021 | PID | Settled water channel level Primary controller |
| TWB_FICx0001 | PID | Raw Water Pump Flow Slave Controller |
| TWB_2LICx0800 | PID | Dosed Filtered Water Wet Well Level Controller |
| TMG_3FICx0001 | PID | Alum pump Flow control |

Settled Water Channel Level Primary Controller (E.G. Only)

The Settled Water Channel Level Controller (TEB_2LICx0021) uses the measured levels of the water flowing from the sedimentation basins into the filters to determine a common Filter Velocity Setpoint to balance the load across all the online filters. The PID serves as a cascade master controller providing the common setpoint value for the secondary PID flow control loops on the individual filters.

The output of the Settled Water Channel Level Controller (TEB_2LICx0021.sOUT) is the common Filter Velocity Setpoint in meters per hour.

Figure 11-3 Block diagram representation of logic Example

Add subsection for additional details such as mode selection, setpoint selection etc.

Hardware Interlocks and Permissive

For trip interlock and safety interlocks conditions, please refer to site ‘I-REGG-AAA-NNN Cause & Effect Matrix.

The below table details hardware interlocks and permissive for units and devices under the control of this process group. Only hardware interlocks are in all modes all other interlocks and permissive are in Remote Auto mode only.

Repeat the below table as many times as necessary to capture the relevant Process Units and Devices

Table 11.8 Interlocks and Permissive

| Identifier | Tag Number – Could be a Device or Process Unit supervisor |  |
| --- | --- | --- |
| Description |  |  |
| Hardware Interlocks | Description (FD A reference section) |  |
| Process Permissive | Description (FD A reference section) | Delay |
| Tag Number, include logic for combining tags if required. E.g. [LIT0801] < Auto-Stop level Set Point AND [LIT0802] < Auto-Stop level Set Point | Click here to enter text. | Click here to enter text. |
| Start Permissives | Description (FD A reference where applicable) | Delay |
| P1 | e.g. Blower thermal overload fault, inlet valve closed | None |
| P2 | inlet valve closed | None |
| Duty/Standby/Assist | Details on any duty arrangements |  |
| Operating Modes | List any details on the modes of operation that exist. Refer to I-SPE-STD-013 for list of Equipment Modes and Control Modes. e.g. Process critical equipment in disable mode; Maintenance function for specified equipment; Maximum time allowed for forcing for process critical equipment |  |
| Group Control Shutdown | Description (FD A reference where applicable) | Delay |

Note: combine different causes for a trip under one number

Sequence Control

This section describes sequence control for running of equipment in ‘Process Unit Name’.

The preferential method is to show it in sequence chart as in Figure 7 below.

While describing the sequence following key points needs to be identified:

Use tag identifiers to describe equipment and reference setpoints.

Describe normal operation and abnormal operation during the sequence controls.

The logic needs to identify step being ‘Complete’, ‘Executed’ or ‘Stopped’.

It shall also show the parallel branching of the sequence path.

Ability to monitor sequence crash stop.

Note: Representation of control in sequence chart does not imply that the SFC or Sequencer is to be used for developing the logic. The guidelines in I-SPE-STD-013 shall be followed for any sequential logic to be developed and needs Principal’s approval.

Schematic is an example only.

Figure 11-4 Sequence Control

Alarms

Refer to Alarms and section in Control System Diagnostics in I-SPE-STD -013 Control Systems Design and Construction Standard for further information on configuration of alarms.

Detail alarm list can be found in I-LST-XXX-00X ‘Site Name’ Alarm Register.

Events & Indications

Refer to Events section in I-SPE-STD-013 Control Systems Design and Construction standard for further information on events and indications.

Add any project relevant information about events and indications here.

Setpoints and Parameters

Detail setpoints and parameters used for controlling this process group here. This is not an alarm list. Alarms are listed separately. Include Process Setpoints that can be adjusted by the operator from SCADA and PLC parameters.

Table 11.12 Setpoint and Parameter Table

| Tag | Parameter Description | Unit | Min | Max | Default | SCADA Privilege level * |
| --- | --- | --- | --- | --- | --- | --- |
|  | Raw Water Flow Setpoint | L/S | 0 | 278 | 200 | Operator |
|  | Raw Water Pump No-Flow Delay | secs | 0 | 999 | 10 | Manager |

*Note SCADA Adjustable field should indicate authority level for change. A blank field indicates a PLC parameter that cannot be adjusted from the SCADA screen.

PLC Signal Processing Requirements

Some points to consider for this section are and can be added:

XXXX msec is the maximum Scan time of CPUXXX

XXXX is the memory of the CPU XXX

Maximum time between PLC-PLC Communication

SOE (Sequence of event recording requirements

External Barriers / Isolators installed for I/Os

Use of external power source (DO or 4 wire transmitters)

Special calibration requirements (gas detectors, analyzers)

Digital inputs inversion requirements (ideally it needs to be wired in FS state) if not logic needs to take care of it.

Safety loops present?

Any Hazardous area installations

Appendix A

Intentionally left blank for project use