## Cover sheet
Template
I-TMP-STD-007
Inspection Certificates for Control Systems Template
Document Number: TEM-00212
This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.
Rev no. | Description | Process Owner |  | Approved for issue
|  | Position | Name | Position | Name | Date
2 | Amended Version | Principal OTE Delivery | Refer Supporting info in REX | Principal OTE Assurance & Performance | Refer Supporting info in REX | 2020-03-03
3 | Amended Version | Lead OT | Refer Supporting info in REX | Principal Process & Analysis | Refer Supporting info in REX | 2023-06-20
3 | Review No Change | Lead OT Engineer | Refer Supporting info in REX | Team Leader Process & Analysis | Refer Supporting info in REX | 2026-07-20
CONTENTS
Network Diagnostics
PLC & RIO Diagnostics
Valve or Motorised Valve
PID
Motor
Analog
HACCP
Totaliser
Advanced Duty
Supervisory Controller
DOCUMENT SENSITIVITY: OFFICIAL (Public)

## Network Diagnostics
SUBJECT |  | SHEET |  |  |  |  | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service Network Diagnostics |  |  |  |  | XXX
Rev - XX
Project Name: | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  | Date:
[7 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  | NA | = Not Applicable
SCADA Page Name |  | e.g. |  |  |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P (J.B.) 21/5
[7 empty] | Ensure all unused ports have been disabled |  |  |  |  | Pass / Fail: | e.g. P (J.B.) 21/5
Network Connections Testing
Device #1 Interface | Device #1 Address/ mask | Device #2 Interface | Device #2 Address | Protocol | Procedure to Trigger Fault |  |  | Alarm Description |  | Alarm Category (Priority) | Delays (On/Off/Hold) | Recovery Time | Pass/Fail
e.g. Chemical Dosing PLC Device Network ports | e.g. 10.101.189.40 /255.255.255.0 | e.g. Power Meter | e.g.10.101.189.110 | e.g. Modbus TCP | e.g. Confirm power meter shown as healthy on SCADA network diagnostics page and no alarms exist. Pull ethernet patch cable at power meter and confirm SCADA icon shows unhealthy state and alarm appears.Plug cable back in and confirm SCADA icon returns to healthy and alarm clears. |  |  | e.g. Communications fault with Power Meter |  | e.g. Warning (3) | 0 s On 10s Off 10s Hold | e.g.11s | e.g. F (J.B.) 21/5
e.g. SCADA Server | e.g.10.96.189.45 | e.g. Chemical Dosing PLC NOC (Rack 0 Slot 3) | e.g. 10.96.189.45 /255.255.255.0 | e.g. Modbus TCP | e.g. Confirm PLC shown as healthy on SCADA network diagnostics page and no alarms exist. Pull ethernet patch cable at PLC and confirm SCADA icon shows unhealthy state and alarm appears.Plug cable back in and confirm SCADA icon returns to healthy and alarm clears. |  |  | e.g. Communications fault with Chemical Dosing PLC |  | e.g. Crticial (1) | 0 s On 10s Off Hold N/A | e.g. 15s | e.g. P (J.B.) 21/5
e.g. Filters PLC Profibus Port | e.g. Node 1 | e.g. Mixer #1 VSD | e.g. Node 21 | e.g. Profibus DP | e.g. Confirm VSD shown as healthy on SCADA network diagnostics page and no alarms exist. Turn off VSD acircuit breaker nd confirm SCADA icon shows unhealthy state and alarm appears. Turn circuit breaker on and confirm SCADA icon returns to healthy and alarm clears. |  |  | e.g. Communications fault with Mixer #1 VSD |  | e.g. Crticial (1) | 0 s On 10s Off 10s Hold | e.g. 5s | e.g. P (J.B.) 21/5
e.g. Filters PLC Profinet port | e.g. 10.30.25.2 / 255.255.254.0 | e.g. Reservoir PLC Profinet port | e.g. 10.30.26.1 /255.255.254.0 | e.g. ISO-on-TCP | e.g. Confirm VReservoir PLC shown as healthy on SCADA network diagnostics page and no alarms exist. Remove Profibus connector at VSD and confirm SCADA icon shows unhealthy state and alarm appears.Plug cable back in and confirm SCADA icon returns to healthy and alarm clears. |  |  | e.g. Communications fault with Reservoir PLC |  | e.g. Crticial (1) | 0 s On 10s Off | e.g. 20s | e.g.F (J.B.) 21/5
Network Bandwidth Statistics Recording | Interface | Test Method |  |  | Value (FAT) | Value (SAT) |  | Device Interface |  | Part Number |  | Software/Firmware Version
Availability | e.g. SCADA Server PLC network NIC | e.g. Setup ping request to PLC 's IP for 1hr. Record total percentage of successful packets. |  |  | e.g. 100% | Refer Supporting info in REX |  | e.g. Chemical Dosing PLC |  | e.g. BME H58 4040 |  | e.g. SV02.20
Usage | e.g. SCADA Server PLC network NIC | e.g. Open Task Manager -> Performance -> Network Details. Monitor NIC throughput for 1 minute and record highest observed value. |  |  | e.g. 2% | Refer Supporting info in REX |  | e.g. Chemical Dosing PLC Network Interface Card (Rack 0 Slot 2) |  | e.g. BME NOC 0301.2 |  | e.g. SV02.04
Availability | e.g. Chemical Dosing PLC internal NIC | e.g. In Unity Pro , right cllick on module in DTM Browser and select Device Menu -> Diagnostics -> Ethernet diagnostics. Record total number of errors. |  |  | e.g. 0 | Refer Supporting info in REX |  | e.g. Chemical Dosing PLC X80 Drop 1 EIO Adapter |  | e.g. BME CRA 31210 |  | e.g SV02.30
Usage | e.g. Chemical Dosing PLC internal NIC | e.g. In Unity Pro , right cllick on module in DTM Browser and select Device Menu ->Diagnostics -> Bandwidth.Record "Processor Utilisation" value. |  |  | e.g. 21% | e.g. 23%
Availability
Usage
Network Diagnostics Tests
Test Description |  | Procedure to Trigger Fault |  |  |  | Alarm Description |  |  | Alarm Category (Priority) | Recovery Time | Pass/Fail
e.g. Remote I/O LAN fault |  | e.g. Power off RIO Switch. Confirm alarm appears. Power on RIO Switch and confirm alarm disappears |  |  |  | e.g. Remote I/O LAN Fault |  |  | e.g. Warning (3) | e.g.5s | e.g. F
e.g. PLC LAN Fault |  | e.g. Power off PLC LAN switch. Confirm alarm appears. Power off PLC LAN switch and confirm alarm disappears. |  |  |  | e.g. PLC LAN Fault |  |  | e.g. Warning (3) | e.g. 7s | e.g. P
e.g. SCADA LAN Fault |  | e.g. Power off SCADA LAN switch. Confirm alarm appears. Power off SCADA Lan switch and confirm alarm disappears. |  |  |  | e.g. SCADA LAN Fault |  |  | e.g. Information (4) | e.g. 23s | e.g. P
e.g. Individual port diagnostic alarm from switch(es) |  | e.g. Unplug ethernet cable from RIO Switch port 2. Confirm alarm appears. Restore cable to port 2 and confirm alarm disappears. |  |  |  | e.g. RIO Switch #1 Port Fault |  |  | e.g. Information (4) | e.g. 18s | e.g. P
e.g. Communications module fault alarm |  | e.g. Turn off supply power to radio modem. Confirm alarm appears. Power on modem and confirm alarm disappears. |  |  |  | e.g. Reservoir Radio Communications fault |  |  | e.g. Information (4) | e.g. 18s | e.g. P
Defect Number | Defect Description | [10 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: |  |  |  |  | Seqwater Witness: |  |  |  |  | Completed / Passed:
Signature: |  |  |  |  | Signature: |  |  |  |  | Date:
X-XXX-XXX-XXX PLC Network and Rack Diagnostic REX no. XXX/XXXXX
Note on B41: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on O41: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## PLC & RIO Diagnostics
SUBJECT |  | SHEET |  |  |  |  | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service PLC and Remote I/O Rack Diagnostic |  |  |  |  | XXX
Rev - XX
Project Name: | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  | Date:
[7 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  | NA | = Not Applicable
SCADA Page Name |  | e.g. |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  | Pass / Fail: | e.g. P |  | Rack identification | e.g. RIO Rack 1
Slot Number | Parameter | Type | Description |  | Test Action |  | Expected Result |  |  | Pass / Fail
[7 empty] | Hardware | PLC | SCADA
0 | aRACKFLT | BOOL | e.g. Fault with RIO Rack 1 |  | 1. Remove ethernet cable, confirm ethernet module light turns yellow. |  | Fault Light | Alarm Triggered | Alarm Displayed | e.g. P
[5 empty] | 2. Restore ethernet connection and verify fault clears. |  | Fault Clears | Alarm Clears | Alarm Clears
1 | aSLOT1FLT | BOOL | e.g. Card Fault in Rack 1 Slot 1 |  | 1. Remove I/O card in slot 1, verify slot n fault alarm activated. |  | Fault Light | Alarm Triggered | Alarm Displayed | e.g. P
[5 empty] | 2. Confirm card fault triggers rack fault (aRACKFLT). |  | Fault Light | Alarm Triggered | Alarm Displayed
[5 empty] | 3. Restore I/O card in slot 1, verify fault clears. |  | Fault Clears | Alarm Clears | Alarm Clears
2 | aSLOT2FLT | BOOL | e.g. Card Fault in Rack 1 Slot 2 |  | 1. Remove I/O card in slot 2, verify slot n fault alarm activated. |  | Fault Light | Alarm Triggered | Alarm Displayed | e.g. P |  | NOTE: Please duplicate the 'Card Fault' rows to suit the number of slots in the rack being tested.
[5 empty] | 2. Confirm card fault triggers rack fault (aRACKFLT). |  | Fault Light | Alarm Triggered | Alarm Displayed
[5 empty] | 3. Restore I/O card in slot 2, verify fault clears. |  | Fault Clears | Alarm Clears | Alarm Clears
3 | aSLOT3FLT | BOOL | e.g. Card Fault in Rack 1 Slot 3 |  | 1. Remove I/O card in slot 2, verify slot n fault alarm activated. |  | Fault Light | Alarm Triggered | Alarm Displayed | e.g. P
[5 empty] | 2. Confirm card fault triggers rack fault (aRACKFLT). |  | Fault Light | Alarm Triggered | Alarm Displayed
[5 empty] | 3. Restore I/O card in slot 2, verify fault clears. |  | Fault Clears | Alarm Clears | Alarm Clears
(Copy this row for number of slots) n | aSLOTnFLT | BOOL | e.g. Card Fault in Rack 1 Slot n |  | 1. Remove I/O card in slot n, verify slot n fault alarm activated. |  | Fault Light | Alarm Triggered | Alarm Displayed | e.g. P
[5 empty] | 2. Confirm card fault triggers rack fault (aRACKFLT). |  | Fault Light | Alarm Triggered | Alarm Displayed
[5 empty] | 3. Restore I/O card in slot n, verify fault clears. |  | Fault Clears | Alarm Clears | Alarm Clears
Defect Number | Defect Description | [10 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: |  |  |  |  | Seqwater Witness: |  |  |  |  | Completed / Passed:
Signature: |  |  |  |  | Signature: |  |  |  |  | Date:
X-XXX-XXX-XXX PLC and Remote I/O Rack Diagnostic REX no. XXX/XXXXX
DOCUMENT SENSITIVITY: OFFICIAL (Public)
Note on B30: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on O30: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## Valve or Motorised Valve
SUBJECT |  | SHEET | [5 empty] | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service Valve/Motorised Valve | [5 empty] | XXX
Rev - XX
Project Name: |  | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  |  |  | Date:
[8 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  |  | NA | = Not Applicable
SCADA Page Name |  |  |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P |  |  | Equipment ID
P&ID Tag |  | PLC Symbol |  | SCADA Tag |  |  | Description
e.g. NAS_V_BL228 |  | e.g. NAS_V_BL228 |  | e.g. NAS_V_BL228 |  |  | e.g. Aspley South Hypo Dosing Line 1 Discharge Valve
Testing and Results
Statuses and Outputs
Test Action/s |  | Expected Results |  | Tag | Status Description | PLC Symbol | IO address | SCADA Tag | PLC Value | SCADA Value | SCADA Connection | Verify Trend | Trend Units | Trend Range | Notes | Pass/Fail
e.g. Open Valve |  | SCADA status updated and "Valve Opened" observed |  | sOPEND | Valve Opened | [5 empty] | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. Close Valve |  | SCADA status updated and "Valve Closed" observed |  | sCLOSD | Valve Closed | [5 empty] | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. Open Valve |  | While the Valve is opening and open switch not active yet, observe SCADA status of "Valve Opening" |  | sOPENG | Valve Opening | [5 empty] | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. Close Valve |  | While the Valve is closing and close switch not active yet, observe SCADA status of "Valve Closing" |  | sCLOSG | Valve Closing | [5 empty] | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. Simulate/trigger Power OK signal if applicable |  | "Power OK" Status Observed in SCADA |  | sPWROK | Power OK | [5 empty] | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. Change Value Manually if applicable |  | Output Reset in SCADA |  | qRSET | Reset Output | [5 empty] | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g.Open or Close Valve (Not Applicable to Non-Motorised Valves) |  | Observe "Valve Current Postion" changing values in SCADA |  | sPOSPV | Valve Current Postion | [5 empty] | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. Change Value Manually (Not Applicable to Non-Motorised Valves) |  | Observe Value is SCADA |  | Refer Supporting info in REX | Deadbancd around cPOSSP where acceptable to stop valve open/close operation (% of PV range) | Refer Supporting info in REX |  |  |  |  | eg. √ | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Alarms
Test Action/s |  | Expected Results |  | Refer Supporting info in REX | Alarm Description | Refer Supporting info in REX | Alarm Privilege | Setpoint | Setpoint Range | Delay | Masked | Verify Trend | Trend Units | Trend Range | Notes | Pass/Fail
Activate the "Fault Alarm" e.g. by forcing one of the many tripping conditions (e.g Valve Power Not OK [mPWROK = 0] OR Valve Available Input is OFF [iAVL = 0] etc..) |  | Scada graphic indicates "Fault" |  | aFL | Fault Alarm | e.g. Warning (3) | e.g. Operator |  |  | e.g. 2s | e.g. Y | e.g. P |  |  |  | e.g. F (J.B.) 21/5
Activate the "Not Available" Alarm e.g. by forcing the specific condtions of (Valve Not Available [iAVL = 0] AND Power OK [mPWROK = 1] AND Not Disabled [sDSABLD = 0]) |  | Scada graphic indicates "Not Available" |  | aNAVL | Not Available | e.g. Warning (3) | e.g. Operator |  |  | e.g. 2s | e.g. N | e.g. P |  |  |  | e.g. F (J.B.) 21/5
Activate the "Failed to Open" Alarm. e.g. The “Fail to Open” (aOPENFL = 1) alarm is set if the output qOPEN is set and the valve position feedback mPOSPV has not changed value in the last time defined by “Fail to Open Delay” (mOPENFLTTMR) |  | Scada graphic indicates "Failed to Open" |  | aOPENFL | Failed to Open | e.g. Warning (3) | e.g. Operator |  |  | e.g. 1m | e.g. N | e.g. P |  |  |  | e.g. F (J.B.) 21/5
Activate the "Failed to Close" Alarm. e.g. The “Fail to Close" (aCLOSFL = 1) alarm is set if the output qCLOS is set and the valve position feedback mPOSPV has not changed value in the last time defined by “Fail to Close Delay” (mCLOSFLTTMR) |  | Scada graphic indicates "Failed to Close" |  | aCLOSFL | Failed to Close | e.g. Warning (3) | e.g. Operator |  |  | e.g. 1m | e.g. N | e.g. P |  |  |  | e.g. F (J.B.) 21/5
Activate the "Not Ready" Alarm e.g. by forcing condtions (e.g. Valve Power NOT OK [mPWROK = 0] OR Not Available [iAVL = 0] etc..) |  | Scada graphic indicates "Not Ready" |  | aNRDY | Not Ready | e.g. Warning (3) | e.g.Supervisor |  |  | e.g. 2s | e.g. N | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Activated the "Feedback Error" Alarm e.g. by setting the conditions of (Both Limit Switches are on [iOPEND = 1 AND iCLOSD = 1] AND Valve Not Disabled [sDSABLD = 0] AND Timer Elapsed [mFBKFLTMR]) |  | Scada graphic indicates "Limit Switch Feedback" |  | aFBKFL | Limit Switch Feedback Fault | e.g. Warning (3) | e.g. Operrator |  |  | e.g. 1m | e.g. N | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Activate the " Setpoint out of range" Alarm e.g. with the conditons (Valve Position Setpoint [mPOSMAX] < [cPOSSP] < [mPOSMIN] AND Valve Not Disabled [sDSABLD = 0]) |  | Scada graphic indicates "Setpoint out of range" |  | aSPFL | Setpoint out of range | e.g. Warning (3) | e.g. Operator |  |  | e.g. 2s | e.g. Y | e.g. P | e.g. % | e.g. 0-120% |  | e.g. P (J.B.) 21/5
Interlocks
Test Action/s |  | Expected Results |  | Tag | Description | Condition 1 | Condition 2 | Condition 3 | Condition 4 | Condition 5 | Condition 6 | Condition 7 | Condition 8 | Condition 9 | Notes | Pass/Fail
e.g. Activate Interlock (Remote Auto or Remote Manual Mode) |  | Depending on type, Valve returns to default safe mode Type 1 - Fail Close Type 2 - Fail Open Type 3 - Fail Last |  | sTILOCKS_OK | Trip Interlocks OK | e.g PLC Condition 1 | e.g PLC Condition 2 | e.g PLC Condition 3 | e.g PLC Condition 4 | e.g PLC Condition 5 | e.g PLC Condition 6 | e.g PLC Condition 7 | e.g PLC Condition 8 | e.g PLC Condition 8 |  | e.g. P (J.B.) 21/5
e.g. Activate Interlock (Remote Auto Mode) |  | Depending on type, Valve returns to default safe mode Type 1 - Fail Close Type 2 - Fail Open Type 3 - Fail Last |  | sPILOCKS_OK | Process Interlocks OK | e.g PLC Condition 1 | e.g PLC Condition 2 | e.g PLC Condition 3 | e.g PLC Condition 4 | e.g PLC Condition 5 | e.g PLC Condition 6 | e.g PLC Condition 7 | e.g PLC Condition 8 | e.g PLC Condition 8 |  | e.g. P (J.B.) 21/5
Special Operating Modes
Test Action/s |  | Expected Results |  | Alarm Tag | Alarm Description | Category (Priority) |  | Alarm Privilege |  |  |  | Verify Trend |  |  | Notes | Pass/Fail
From SCADA, place device in disabled mode. |  | All alarms masked, graphic in disabled mode and valve disable alarm generated. |  | aDSABLD | Device Disabled | e.g. Warning (3) |  | e.g. Operator |  |  |  | e.g. P |  |  |  | e.g. P (J.B.) 21/5
From SCADA, place device in maintenance mode. |  | Graphic in maintenance mode and valve in maint alarm generated |  | sMAINT | In Maintenance Mode | e.g. Warning (3) |  | e.g. Operator |  |  |  | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Operating Modes
Test Action/s |  | Expected Results |  | Tag | Description | PLC Symbol | IO address | SCADA Tag | PLC Value |  | SCADA Value |  | Verify Trend |  | Notes | Pass/Fail
From SCADA, place device in manual mode |  | Graphic in manual mode |  | sAUTO [0] | In Manual Mode | [7 empty] | e.g. P |  |  | e.g. P (J.B.) 21/5
From SCADA, place device in local mode |  | Graphic in local mode |  | sLOCAL | In Local Mode | [7 empty] | e.g. P |  |  | e.g. P (J.B.) 21/5
From SCADA, place device in auto mode |  | Graphic in auto mode |  | sAUTO [1] | In Auto Mode | [7 empty] | e.g. P |  |  | e.g. P (J.B.) 21/5
Additional Tests
Test Action/s |  |  |  |  | Expected Results |  |  |  | Values / Comments | [6 empty] | Pass/Fail
e.g. P (J.B.) 21/5
e.g. P (J.B.) 21/5
Defect Number | Defect Description | [13 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: | [5 empty] | Seqwater Witness: | [7 empty] | Completed / Passed:
Signature: | [5 empty] | Signature: | [7 empty] | Date:
X-XXX-XXX-XXX Valve Testing REX no. XXX/XXXXX
Note on B56: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on R56: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## PID
SUBJECT |  | SHEET | [5 empty] | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service PID | [5 empty] | XXX
Rev - XX
Project Name: |  | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  |  |  | Date:
[8 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  |  | NA | = Not Applicable
SCADA Page Name |  |  |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P |  |  | Equipment ID
P&ID Tag |  | I/O Address |  | SCADA Tag |  |  | Description
e.g. NAS_PIDx1002 |  |  |  | e.g. NAS_PIDx1002 |  |  | e.g. Aspley North Hypo Dosing Pump 1 PID Control
Testing and Results
Statuses and Outputs
Test Action/s |  | Expected Results |  | Tag | Status Description | PLC Symbol |  |  | PLC Value | SCADA Value |  | Verify Trend | Trend Units | Trend Range | Notes | Pass/Fail
e.g. Activate Ouput |  | PID Output correctly displayed in SCADA |  | qOUT | Output starts at correct value and responds accodingly | [10 empty] | e.g. P (J.B.) 21/5
e.g. Change the setpoint manually |  | Setpoint value should be correctly observed in SCADA |  | cSP | SP using correct value | [6 empty] | e.g. P | e.g. L/hr | e.g. 0 - 100 |  | e.g. P (J.B.) 21/5
e.g. Change the process value manually |  | Process Value should be correctly observed in SCADA |  | sPV | PV using correct value | [6 empty] | e.g. P | e.g. L/hr | e.g. 0 - 100 |  | e.g. P (J.B.) 21/5
e.g. Turn Tracking mode on/off |  | SCADA correctly presents the current Tracking mode Status |  | sTR_S | Tracking Switch/Override Status | [6 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. Alter Feedforward Status on/off |  | Feedforward Status observed in SCADA |  | sFF | Feedforward Status | [6 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. From Scada, command the change of PID Gain term |  | Observe Correct Gain Term in SCADA and PLC |  | cKP | PID Gain Component | [6 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. From Scada, command the change of PID Integral term |  | Observe Correct Integral Term in SCADA and PLC |  | cTi | PID Integral Component | [6 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. From Scada, command the change of PID Derivative term |  | Observe Correct Derivative Term in SCADA and PLC |  | Refer Supporting info in REX | PID Derivative Component | Refer Supporting info in REX | [5 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
e.g. From Scada, command the change of the Upper limit |  | Observe Maximum Ouput Graphic Change in SCADA and PLC |  | Refer Supporting info in REX | Upper limit of the output in Auto mode | Refer Supporting info in REX | [5 empty] | e.g. P | e.g. % | e.g. 0 - 100 |  | e.g. P (J.B.) 21/5
e.g. From Scada, command the change of the Lower limit |  | Observe Minimum Output Graphic Change in SCADA and PLC |  | Refer Supporting info in REX | Lower limit of the output in Auto mode | Refer Supporting info in REX | [5 empty] | e.g. P | e.g. % | e.g. 0 - 101 |  | e.g. P (J.B.) 21/5
Desired Behaviour
Test Action/s |  | Expected Results 1 |  | Expected Results 2 |  | Expected Results 3 | Expected Results 4 | Expected Results 5 | Tags | Notes/Comments | [5 empty] | Pass/Fail
e.g. Place the PID in Auto Mode and inject an Analogue Input |  | sAUTO ( =ON), In Auto Mode |  | e.g. PID Ramps Up or Down the Input to Desired Setpoint. |  | e.g. PID Parameters are correctly shown in SCADA. | e.g. Correct behaviour observed when input stops |  | e.g. qOUT etc | [6 empty] | e.g. P (J.B.) 21/5
e.g. Place the PID in Tracking / Override Mode from PLC (mTR_S = ON, e.g. Uisng associated dosing pump not running as input to mTR_S; 0 as tracking value : mTR_I = 0 ) |  | sTR_S ( =ON), In Override Mode |  | e.g. PID is in override mode and PID output is locked at mTR_I |  | e.g. Correctly activates Tracking Mode when there is no Input. |  |  | e.g. qOUT etc | [6 empty] | e.g. P (J.B.) 21/5
e.g. Place the PID in Manual Mode. Enter Proportial, Integral and Derivative terms manually from SCADA |  | sAUTO ( =OFF), In Manual Mode |  | e.g. Observe the correct PID parameters in the PLC and SCADA. |  | e.g. Observe the correct response from the output: PID output = manual SP. |  |  | e.g. cMAN and qOUT etc | [6 empty] | e.g. P (J.B.) 21/5
Alarms
Test Action/s |  | Expected Results |  | Alarm Tag | Alarm Description | Category (Priority) | Alarm Privilege | Setpoint | Setpoint Range | Delay | Masked | Verify Trend | Trend Units | Trend Range | Notes | Pass/Fail
(Setpoint - PV) > 5% of setpoint for 60 seconds |  | "Deviation Alarm" Activated in SCADA |  | User Defined | Deviation Alarm | e.g. Warning (3) | e.g. Operator | e.g. 80% | e.g. 80-100% | e.g. 2s | e.g. Y | e.g. P | e.g. % | e.g. 0-120% |  | e.g. P (J.B.) 21/5
Output High > 90% |  | "Output High Alarm" Activated in SCADA |  | User Defined | Output High Alarm | e.g. Warning (3) | e.g. Operator | e.g. 60% | e.g. 0-100% | e.g. 2s | e.g. N | e.g. P | e.g. % | e.g. 0-120% |  | e.g. P (J.B.) 21/5
If PID is in remote manual mode, then the alarm shall be generatedc after 5 minutes in this mode |  | "PID Controller Mode Alarm" Activated in SCADA |  | User Defined | PID Controller Mode Alarm | e.g. Warning (3) | e.g. Operator | e.g. 30% | e.g. 0-100% | e.g. 1m | e.g. N | e.g. P | e.g. % | e.g. 0-120% |  | e.g. P (J.B.) 21/5
Special Operating Modes
Test Action/s |  | Expected Results |  | Tag | Alarm Description | Category (Priority) |  | Alarm Privilege |  |  |  | Verify Trend |  | Notes |  | Pass/Fail
From SCADA, place device in disabled mode. |  | All alarms masked, graphic in disabled mode and alarm generated. |  | sDSABLD | Device Disabled | e.g. Warning (3) |  | e.g. Operator |  |  |  | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Operating Modes
Test Action/s |  | Expected Results |  | Tag | Description | PLC Symbol | IO address | SCADA Tag | PLC Value | SCADA Value |  | Verify Trend |  | Notes |  | Pass/Fail
From SCADA, place device in manual mode |  | Graphic in Manual Mode |  | DOCUMENT SENSITIVITY: OFFICIAL (Public) | Manual Mode | [6 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
From SCADA, place device in auto mode |  | Graphic in Auto Mode |  | sAUTO [1] | Auto Mode | [6 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Additional Tests
Test Action/s |  |  |  |  | Expected Results |  |  |  | Values / Comments | [6 empty] | Pass/Fail
e.g. From SCADA, place device in autotuning mode |  |  |  |  | e.g. auto tuning PID active, sAutoTune = ON, auto tuning works as expected | [10 empty] | e.g. P (J.B.) 21/5
e.g. cascade PID used (cSP is using calculated value or other PID loop's output) | [15 empty] | e.g. P (J.B.) 21/5
Defect Number | Defect Description | [13 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: | [5 empty] | Seqwater Witness: | [7 empty] | Completed / Passed:
Signature: | [5 empty] | Signature: | [7 empty] | Date:
X-XXX-XXX-XXX PID Testing REX no. XXX/XXXXX
Note on B53: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on R53: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## Motor
SUBJECT |  | SHEET | [5 empty] | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service Motor | [5 empty] | XXX
Rev - XX
Project Name: |  | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  |  |  | Date:
[8 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  |  | NA | = Not Applicable
SCADA Page Name |  |  |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P |  |  | Equipment ID | e.g. NAS_M_PMP001
P&ID Tag |  |  |  | Motor ID |  |  | Description
e.g. NAS_M_PMP001 |  |  |  | e.g. NAS_M_PMP001 |  |  | e.g. AspWQMF Hypo Waste Transfer Pmp
Testing and Results
Outputs
Test Action/s |  | Expected Results |  |  |  | PLC Symbol | IO address |  | PLC Value | SCADA Value | Verify Trend | Trend Units | Trend Range | Notes |  | Pass/Fail
e.g. Activate Run Output |  | Updates the SCADA status |  |  |  | XXXXXX_qRun | [9 empty] | e.g. P (J.B.) 21/5
e.g. Activate Reset |  | Resets module after a fault |  |  |  | XXXXXX_qRSET | [9 empty] | e.g. P (J.B.) 21/5
e.g. Activate Run Reverse |  | Updates the SCADA status |  |  |  | XXXXXX_qRUNREV | [9 empty] | e.g. P (J.B.) 21/5
e.g. Activate Speed Reference in Auto (mAUTOSPD) and Manual (cMANUALSPD) |  | Reference Speed raw output from the scaled value (sSPD) |  |  | Auto | XXXXXX_qSPD | [9 empty] | e.g. P (J.B.) 21/5
Manual
Alarms
Test Action/s |  | Expected Results |  |  | Alarm Tag | Alarm Description Active Alarm Window | Alarm Banner | Summary Alarm Window (for Logging) | Category (Priority) | Alarm Privilege | Delay | Masked | Verify Trend | Notes |  | Pass/Fail
• Drive “Power OK” is set (mPWROK = 1) • Drive Available Input is OFF (iAVL = 0) • Drive Hardwired Interlocks OK is OFF (iHWILOK = 0) • The drive has not been disabled (sDSABLD = 0). |  | Not available |  |  | aNAVL | Refer Supporting info in REX | e.g. Y | e.g. Y | e.g. Information (4) | e.g. Operator | e.g. 2s | e.g. N | e.g. P |  |  | e.g. P (J.B.) 21/5
• Run request is set (qRUN = 1); • Drive running feedback is not received (iRUN =0); |  | Fail to Start |  |  | aSTRTFL | Refer Supporting info in REX | e.g. Y | e.g. Y | e.g. Information (4) | e.g. Operator | e.g. 1m | e.g. N | e.g. P |  |  | e.g. P (J.B.) 21/5
• Run request is reset (qRUN = 0); • Drive running feedback is received (iRUN = 1); |  | Fail to Stop |  |  | aSTPFL | Refer Supporting info in REX | e.g. Y | e.g. Y | e.g. Warning (3) | e.g. Operator | e.g. 1m | e.g. N | e.g. P |  |  | e.g. P (J.B.) 21/5
Run request is set (qRUN = 1); • Drive running feedback is not received (iRUNREV =0); • SCADA command start in Reverse (cSTRTREV =1); |  | Fail to Start in Reverse |  |  | aREVSTRTFL | AspWQMF Sth Jet Mix Pmp 1-Fail to Start Reverse | e.g. Y | e.g. Y | e.g. Action (2) | e.g.Supervisor | e.g. 2s | e.g. N | e.g. P |  |  | e.g. P (J.B.) 21/5
Drive Hours Run exceeds the alarm setpoint (cServiceSP) |  | Service Due |  |  | aServiceDue | AspWQMF Sth Jet Mix Pmp 1-Service Due Alm | e.g. Y | e.g. Y | e.g. Information (4) | e.g. Operator | e.g. 2s | e.g. N | e.g. P |  |  | e.g. P (J.B.) 21/5
Any of the above |  | Fault alarm triggered |  |  | aFL | AspWQMF Sth Jet Mix Pmp 1-General Fault | e.g. Y | e.g. Y | e.g. Action (2) | e.g.Supervisor | e.g. 2s | e.g. Y | e.g. P |  |  | e.g. P (J.B.) 21/5
Interlocks
Test Action/s |  | Expected Results |  |  | Tag | Condition 1 | Condition 2 | Condition 3 | Condition 4 | Condition 5 | Condition 6 | Condition 7 | Condition 8 | Notes |  | Pass/Fail
Simulate/Trigger Drive Trip Interlocks |  | Change in device Status and alarm triggering |  |  | mTILOCKS_OK | e.g. chemical tank high high level | e.g. discharge line no flow | [8 empty] | e.g. P (J.B.) 21/5
Simulate/Trigger Start Permissive Interlocks |  | Change in device Status and alarm triggering |  |  | mSILOCKS_OK | e.g. at least one doing pump available | [9 empty] | e.g. P (J.B.) 21/5
Simulate/Trigger Process Interlocks |  | Change in device Status |  |  | mPILOCKS_OK | e.g. chemical tank level operational high | [9 empty] | e.g. P (J.B.) 21/5
Simulate/Trigger Hardwired Interlock OK |  | Change in device Status and alarm triggering |  |  | iHWILOCK | e.g. motor cicuit break not closed | [9 empty] | e.g. P (J.B.) 21/5
Special Operating Modes
Test Action/s |  | Expected Results |  |  | Alarm Tag | Alarm Description | Category (Priority) |  | Alarm Privilege |  |  | Verify Trend |  |  | Notes | Pass/Fail
From SCADA, place device in disabled mode. |  | All alarms masked, graphic in Disabled mode and disable alarm generated. |  |  | aDSABLD | Device Disabled | e.g. Warning (3) |  | e.g. Operator |  |  | e.g. P |  |  |  | e.g. P (J.B.) 21/5
From SCADA, place device in maintenance/service mode. |  | Graphic shows device in Maintenance mode and device in Maintenance mode alarm generated. |  |  | aMAINT | In Maintenance Mode | e.g. Warning (3) |  | e.g. Operator |  |  | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Operating Modes
Test Action/s |  | Expected Results |  |  | Tag | Description | PLC Value |  | SCADA Value |  |  | Verify Trend |  |  | Notes | Pass/Fail
From SCADA, place device in manual mode (iAVL=1) |  | Graphic shows device in Manual mode and operator can Start or Stop device from SCADA |  |  | sAUTO =0 | In Manual Mode | [5 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
From SCADA, place device in auto mode (iAVL=1) |  | Graphic shows device in Auto mode and operator cannot start device from SCADA; Device can be started by PLC/RTU program |  |  | sAUTO =1 | In Auto Mode | [5 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Place device in local mode (iAVL=0, iHWILOK=1) |  | Graphic shows device in Local mode and device can only be start or stopped in local filed; Neither PLC/RTU or SCADA program can start or stop it |  |  | sLOCAL=1 | In Local Mode | [5 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Calculations
Test Action/s |  | Expected Results |  |  | Tag | Description |  |  |  | PLC Value | SCADA Value | Verify Trend | Trend Units | Trend Range | Notes | Pass/Fail
Start and Stop Motor many times |  | Number of starts increases |  |  | sNSTRTS | eg. AspWQMF Hypo Waste Transfer Pmp-Num of Starts | [5 empty] | e.g. P |  |  |  | e.g. P (J.B.) 21/5
Leave Motor running |  | Run - Hours - Lifetime and Run Hours - Daily increase |  |  | sHRSRUN sHRSDAILY | eg. AspWQMF Hypo Waste Transfer Pmp-Running daily hours and total running hours | [5 empty] | e.g. P | Hours |  |  | e.g. P (J.B.) 21/5
Trigger mHRSRSET (mHRSRSET=1) |  | Run Hours - Daily is reset |  |  | mHRSRSET | eg. AspWQMF Hypo Waste Transfer Pmp-Run Hrs Daily- reset at midnight | [5 empty] | e.g. P | Hours |  |  | e.g. P (J.B.) 21/5
Additional Tests
Test Action/s |  |  |  |  | Expected Results |  |  |  | Values / Comments | [6 empty] | Pass/Fail
e.g. Toggle Reverse Flow input |  |  |  |  | e.g. SCADA mimic shows reverse flow |  |  |  | e.g. Performed as expected. | [6 empty] | e.g. P (J.B.) 21/5
e.g. Simulate dosing pump reaches maximum/minimum capacity and alarm is generated correctly |  |  |  |  | e.g. Alarm can only be active and trigger proper actions |  |  |  | e.g. Performed as expected. | [6 empty] | e.g. P (J.B.) 21/5
e.g. motor associated setpoints can be configued properly from SCADA |  |  |  |  | e.g. setpoints can be changeable from SCAD to PLC and functional working in program |  |  |  | e.g. Performed as expected. | [6 empty] | e.g. P (J.B.) 21/6
Defect Number | Defect Description | [13 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: | [5 empty] | Seqwater Witness: | [7 empty] | Completed / Passed:
Signature: | [5 empty] | Signature: | [7 empty] | Date:
X-XXX-XXX-XXX Motor Testing REX no. XXX/XXXXX
Note on B59: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on R59: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## Analog
SUBJECT |  | SHEET | [5 empty] | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service Analog and Transmitters Alarms | [5 empty] | XXX
Rev - XX
Project Name: |  | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  |  |  | Date:
[8 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  |  | NA | = Not Applicable
SCADA Page Name |  |  |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P |  |  | Equipment ID | e.g. NAS-I-FIT010
P&ID Tag |  | I/O Address |  | SCADA Tag |  |  | Description
e.g. NAS_I_FIT010_iFLOWPV |  | e.g. EIO2_d2_r0_s9_AMI0810.ANA_CH_IN[2].ANA.VALUE |  | e.g. NAS_I_FIT010_sFLOWPV |  |  | e.g. Aspley South Ammonia Dosing Line 1 Flow Meter
Testing and Results
Inputs
Test Action/s |  | Expected Results |  |  | Range | Units | Full Span Instrument Test / Multipoint Calibration Results |  | PLC Value | SCADA Value | Verify Trend | Trend Units | Trend Range |  |  | Pass/Fail
e.g. Inject current into analog input module, from 4-20mA. |  | Appropriately scaled result in PLC and SCADA. |  | Instrument | e.g. 4-20 | e.g. mA | 0% | e.g. 4mA | e.g. 0.2% | e.g. 0.2% | e.g. P | e.g. % | e.g. 0-120% |  |  | e.g. P (J.B.) 21/5
[7 empty] | 25% | e.g. 8mA | e.g. 24.5% | e.g. 2.45%
|  |  |  | Engineering | e.g. 0.0-100 | e.g. % | 50% | e.g. 12mA | e.g. 51% | e.g. 51%
[7 empty] | 75% | e.g. 16mA | e.g. 76% | e.g. 76%
[7 empty] | 100% | e.g. 20mA | e.g. 99% | e.g. 99%
Alarms
Test Action/s |  | Expected Results |  |  | Alarm Tag | Alarm Description | Category (Priority) |  | Alarm Privilege | Setpoint | Setpoint Range | Delay | Masked | Alarm Hold Time | Deadband | Pass/Fail
e.g. Inject current into analog input module, appropriate to test each alarm setpoint. |  | Alarm triggered when PV above corresponding setpoint. Alarm stays on until Hold Time has elapsed and PV has fallen below alarm setpoint minus alarm deadband setpoint. |  |  | aHH | Refer Supporting info in REX | e.g. Action (2) |  | e.g.Supervisor | e.g. 80% | e.g. 80-100% | e.g. 2s | e.g. Y | e.g. 5s | e.g. 2% | e.g. F (J.B.) 21/5
[5 empty] | aHI | Refer Supporting info in REX | e.g. Information (4) |  | e.g. Operrator | e.g. 60% | e.g. 0-100% | e.g. 2s | e.g. N
|  | Alarm triggered when PV below corresponding setpoint. Alarm stays on until Hold Time has elapsed and PV rises above alarm setpoint plus alarm deadband setpoint. |  |  | aLO | Refer Supporting info in REX | e.g. Information (4) |  | e.g. Operator | e.g. 30% | e.g. 0-100% | e.g. 1m | e.g. N
[5 empty] | aLL | Low Low | e.g. Warning (3) |  | e.g. Operator | e.g. 10% | e.g. 0-100% | e.g. 1m | e.g. N
e.g. Inject current into analog input module which is outside deadband limits . Force signal on iFL input (if applicable) |  | Alarm triggered. When fault trigger turns off, alarm stays on until Hold Time elapses. |  |  | aFL | Sensor Fault | e.g. Warning (3) |  | e.g. Operator | [5 empty] | e.g. +- 51.19 = +- 0.2mA | e.g. P (J.B.) 21/5
Special Operating Modes
Test Action/s |  | Expected Results |  |  | Alarm/Event Tag | Alarm Description | Category (Priority) |  | Alarm Privilege | Verify Setpoint | Verify Force Time | Verify Trend |  |  |  | Pass/Fail
From SCADA, place device in disabled mode. |  | All alarms masked, graphic in disabled mode and alarm generated. |  |  | aDSABLD | Device Disabled | e.g. Warning (3) |  | e.g.Supervisor | [6 empty] | e.g. P (J.B.) 21/5
From SCADA, place device in maintenance mode. |  | Graphic in maintenance mode and alarm generated. |  |  | sMAINT | In Maintenance Mode | e.g. Warning (3) |  | e.g. Operrator | [6 empty] | e.g. P (J.B.) 21/5
From SCADA, when in maintenance mode, press force button. |  | Check force value and time displayed on popup. Enter a valid forced PV value and confirm forced PV value is able to change. Enter a valid force time and confirm foce time is able to change. After Force Time elapsed, confirm that force is deselected automatically. |  |  | sFRCE | Is Forced | e.g. Warning (3) |  | e.g. Operator | e.g. P | e.g. P | e.g. P |  |  |  | e.g. P (J.B.) 21/5
From SCADA press force period reset button. |  | Resets the Force period timer |  |  | cFRCETIME | Timer Period Reset | [9 empty] | e.g. P (J.B.) 21/5
Additional Tests
Test Action/s |  |  |  |  | Expected Results |  |  |  | Values / Comments | [6 empty] | Pass/Fail
e.g. Toggle Reverse Flow input |  |  |  |  | e.g. SCADA mimic shows reverse flow |  |  |  | e.g. Performed as expected. | [6 empty] | e.g. P (J.B.) 21/5
e.g. Confirm High-High alarm is masked correctly |  |  |  |  | e.g. Alarm can only be active when pump 6PMP001 has been running for 5 seconds |  |  |  | e.g. Performed as expected. | [6 empty] | e.g. P (J.B.) 21/5
Defect Number | Defect Description | [13 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: | [5 empty] | Seqwater Witness: | [7 empty] | Completed / Passed:
Signature: | [5 empty] | Signature: | [7 empty] | Date:
X-XXX-XXX-XXX Analog Transmitters Testing REX no. XXX/XXXXX
Note on B44: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on R44: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## HACCP
SUBJECT |  | SHEET | [5 empty] | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service HACCP | [5 empty] | XXX
Rev - XX
Project Name: |  | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  |  |  |  | Date:
[8 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  |  | NA |  | = Not Applicable
SCADA Page Name |  |  |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P |  |  |  | Equipment ID | e.g. NAS_I_AIT003
P&ID Tag |  | I/O Address |  | SCADA Tag |  |  | Description
e.g. NAS_I_AIT003_TC |  | e.g. EIO2_d2_r0_s9_AMI0810.ANA_CH_IN[2].ANA.VALUE |  | e.g. NAS_I_AIT003_TC_sPV |  |  | e.g. Aspley WQMF - SW TotalChlorine Analyser
Testing and Results
Alarms
Test Action/s |  | Expected Results |  |  | Alarm Tag | Alarm Description | Category (Priority) | Setpoint Range | Enable/Disable | Masked | Dial Out Enable | Alarm Delay (ON/OFF) |  | Alarm Hold Time | Deadband | Notes | Pass/Fail
1- Change Process Value to a value between Action High and Critical High SP 2- Toggle cCRTHDSABL 3- Toggle mCRTHMASK 4- Toggle cCRTHDLEN |  | 1- Confirm aCRTH and sCRTHDL turn to ON after elapsed time 2- Confirm: sCRTHDSABLD = ON, aCRTH = OFF, sCRTHDL = OFF 3- Confirm: sCRTHMASKED = ON, aCRTH = OFF, sCRTHDL = OFF 4- Confirm aCRTH = ON, sCRTHDL = OFF |  |  | aCRTH | eg. AspWQMF SW Ttl Chlr. HACCP CritHi ALM | e.g. Critical |  |  | e.g. Y | e.g. Y | e.g. 1m | e.g. 1m |  |  |  | e.g. P (J.B.) 21/5
1- Change Process Value to a value between Action High and Critical High SP 2- Toggle cCRTLDSABL 3- Toggle mCRTLMASK 4- Toggle cCRTLDLEN |  | 1- Confirm aCRTL and sCRTLDL turn to ON after elapsed time 2- Confirm: sCRTLDSABLD = ON, aCRTL = OFF, sCRTLDL = OFF 3- Confirm: sCRTLMASKED = ON, aCRTL = OFF, sCRTLDL = OFF 4- Confirm aCRTL = ON, sCRTLDL = OFF |  |  | aCRTL | eg. AspWQMF SW Ttl Chlr. HACCP CritLo ALM | e.g. Critical |  |  | e.g. N | e.g. Y | e.g. 1m | e.g. 1m |  |  |  | e.g. P (J.B.) 21/5
1- Change Process Value to a value between Action High and Critical High SP 2- Toggle cACTHDSABL 3- Toggle mACTHMASK 4- Toggle cACTHDLEN |  | 1- Confirm aACTH and sACTHDL turn to ON after elapsed time 2- Confirm: sACTHDSABLD = ON, aACTH = OFF, sACTHDL = OFF 3- Confirm: sACTHMASKED = ON, aACTH = OFF, sACTHDL = OFF 4- Confirm aACTH = ON, sACTHDL = OFF |  |  | aACTH | eg. AspWQMF SW Ttl Chlr. HACCP ActHi ALM | e.g. Action |  |  | e.g. Y | e.g. Y | e.g. 1m | e.g. 1m |  |  |  | e.g. P (J.B.) 21/5
1- Change Process Value to a value between Action High and Critical High SP 2- Toggle cACTLDSABL 3- Toggle mACTLMASK 4- Toggle cACTLDLEN |  | 1- Confirm aACTL and sACTLDL turn to ON after elapsed time 2- Confirm: sACTLDSABLD = ON, aACTL = OFF, sACTLDL = OFF 3- Confirm: sACTLMASKED = ON, aACTL = OFF, sACTLDL = OFF 4- Confirm aACTL = ON, sACTLDL = OFF |  |  | aACTL | eg. AspWQMF SW Ttl Chlr. HACCP ActLo ALM | e.g. Action |  |  | e.g. N | e.g. Y | e.g. 1m | e.g. 1m |  |  |  | e.g. P (J.B.) 21/5
Additional Tests
Test Action/s |  |  |  |  | Expected Results |  |  |  | Values / Comments | [7 empty] | Pass/Fail
Simulate/Trigger Aspley South West Total Chlorine Critical High Alarm while sequnece's in auto mode |  |  |  |  | Sequenctial shudtdown of Aspley South Dosing Facility |  |  |  | e.g. Performed as expected. | [7 empty] | e.g. P (J.B.) 21/5
e.g. P (J.B.) 21/5
Defect Number | Defect Description | [14 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: | [5 empty] | Seqwater Witness: | [8 empty] | Completed / Passed:
Signature: | [5 empty] | Signature: | [8 empty] | Date:
X-XXX-XXX-XXX HACCP Testing REX no. XXX/XXXXX
DOCUMENT SENSITIVITY: OFFICIAL (Public)
Note on B30: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on S30: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## Totaliser
SUBJECT |  | SHEET | [5 empty] | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service Totalisers | [5 empty] | XXX
Rev - XX
Project Name: |  | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  |  |  | Date:
[8 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  |  | NA | = Not Applicable
SCADA Page Name |  |  |  |  | Ensure all devices accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P |  |  | Equipment ID | e.g. NAS_I_FQI001
P&ID Tag |  | I/O Address |  | SCADA Tag |  |  | Description
e.g. NAS_I_FIT001_iPULSE |  | e.g. EIO2_d1_r0_s3_DDI1602.DIS_CH_IN[4].VALUE |  | e.g. NAS_FQI001 |  |  | e.g. Aspley North Hypo Dosing Line 1 Flow Meter Pulse
Test Description | Test Action |  |  | Expected Results |  | Flow/pulse (digital) or Flow rate (analogue) | Test pulses (digital) or Test length (analogue) | Value Expected | PLC Values | SCADA Values | Verify Trend | Trend Units | Trend Range | Notes |  | Pass/Fail
Total accumulation | e.g. Start with period total and accumulated total values at zero. Toggle state of input from low to high and back to low for the chosen number of cycles. Review results in PLC and SCADA. |  |  | Recorded total matches calculated total |  | e.g. 1L / pulse | e.g. 20 pulses | e.g. 20L Total Flow 20L Period Flow | e.g. 20L Total Flow 20L Period Flow | e.g. 20L Total Flow 20L Period Flow | e.g. P (J.B.) 21/5 | e.g. kL |  |  |  | e.g. P (J.B.) 21/5
Total reset | e.g. Manipulate total reset input logic to change input state from low to high. Toggle the state of the pulse input for a few cycles. |  |  | e.g. The Total flow values reset to zero. The Period Flow value is unaffected and accumulation continues. (Results will vary from digital to analogue totalisers) |  |  |  | e.g. Period Flow accumulates 0L Total Flow | e.g. Period Flow accumulates 0L Total Flow | e.g. Period Flow accumulates 0L Total Flow | [5 empty] | e.g. P (J.B.) 21/5
Period accumulation | e.g. Start with Period Flow at zero and positive values in Previous Period Flow and Total Flow. Toggle state of pulse input from low to high and back to low for the chosen number of cycles. Review results in PLC and SCADA. |  |  | Flow values match calculated totals |  | e.g. 1L / pulse | e.g. 10 pulses | e.g. 10L Period Flow 20L Prev. Prd. Flow 30L Total Flow | e.g. 10L Period Flow 20L Prev. Prd. Flow 30L Total Flow | e.g. 10L Period Flow 20L Prev. Prd. Flow 30L Total Flow | e.g. P (J.B.) 21/6 | e.g. kL |  |  |  | e.g. P (J.B.) 21/5
Period reset | e.g. Start with Total Accumulation value matching Period Total. Set PLC RTC to 11:59:30pm. Wait for RTC to elapse past midnight (setting the mRSET_PRD_TOT input true for one scan). |  |  | e.g. Period Flow value shall be rolled into previous Period Flow value. Period Flow value goes to zero. (Results will vary from digital to analogue totalisers) |  |  |  | e.g. 0L Period Flow 20L Prev. Prd. Flow 20L Total Flow | e.g. 0L Period Flow 20L Prev. Prd. Flow 20L Total Flow | e.g. 0L Period Flow 20L Prev. Prd. Flow 20L Total Flow | [5 empty] | e.g. P (J.B.) 21/5
Hold logic active | e.g. Manipulate hold input logic to change hold input state from low to high. Toggle the state of the pulse input for a few cycles. |  |  | e.g. Period value stays static, Total value continues totalising |  |  |  | e.g. 10L Period Flow 20L Prev. Prd. Flow 20L Total Flow | e.g. 10L Period Flow 20L Prev. Prd. Flow 20L Total Flow | e.g. 10L Period Flow 20L Prev. Prd. Flow 20L Total Flow | e.g. P (J.B.) 21/6 | e.g. kL |  |  |  | e.g. P (J.B.) 21/5
Hold logic inactive | e.g. Manipulate hold input logic to change hold input state from high to low. Toggle the state of the pulse input for a few cycles. |  |  | e.g. Period flow value continues incrementing |  |  |  | e.g. 10L Period Flow 20L Prev. Prd. Flow 20L Total Flow | e.g. 10L Period Flow 20L Prev. Prd. Flow 20L Total Flow | e.g. 10L Period Flow 20L Prev. Prd. Flow 20L Total Flow | [5 empty] | e.g. P (J.B.) 21/5
SCADA Disable command active | e.g. Tick device disable check box on SCADA popup. Trigger pulses on the digital input. |  |  | SCADA popup shows device disabled and disable alarm appears. The Period and Total flow values stay static. | [6 empty] | e.g. P (J.B.) 21/6 | e.g. N/A |  |  |  | e.g. P (J.B.) 21/5
SCADA Disable command inactive | e.g. Uncheck device disable check box on SCADA popup. Trigger pulses on the digital input. |  |  | SCADA popup disabled notification disappears. The Period and Total flow values resume totalising | [6 empty] | e.g. P (J.B.) 21/6 |  |  |  |  | e.g. P (J.B.) 21/5
Additional Tests
Test Action/s |  |  |  |  | Expected Results |  |  |  | Values / Comments | [6 empty] | Pass/Fail
Defect Number | Defect Description | [13 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: | [5 empty] | Seqwater Witness: | [7 empty] | Completed / Passed:
Signature: | [5 empty] | Signature: | [7 empty] | Date:
X-XXX-XXX-XXX Totalisers Testing REX no. XXX/XXXXX
DOCUMENT SENSITIVITY: OFFICIAL (Public)
Note on B34: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on R34: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## Advanced Duty
SUBJECT |  | SHEET | [5 empty] | REFERENCE
TEST SHEETS |  | Control Systems FAT / SAT / Out of Service Advanced Duty Control | [5 empty] | XXX
Rev - XX
Project Name: |  | XXXXXX | [5 empty] | Project Number : |  |  | Testing Officer: |  |  |  | Date:
[8 empty] | Version of Library Blocks: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  |  | F | = Unacceptable |  |  |  | NA | = Not Applicable
SCADA Page Name |  |  |  |  | Ensure advanced duty Control object accurately displayed on SCADA page(s). |  |  |  |  | Pass / Fail: | e.g. P | Equipment ID/s | e.g. NAS_M_XYxxx
Duy/Standy Pair 1 |  | PLC Symbol |  | SCADA Tag |  |  | Description |  |  |  |  | Operation List |  |  | Duty Cycle
|  | e.g. NAS_M_PMD001 |  | e.g. NAS_M_PMD001 |  |  | e.g. Aspley South Ammonia Dosing Line 1 Pump |  |  |  |  | e.g. Operation List : [0] = 5, NAS_M_PMD006, highest priority |  |  | e.g. accordingly, NAS_M_PMD006 will run first. This is then followed by NAS_M_PMD001, NAS_M_PMD002, NAS_M_PMD003, NAS_M_PMD005 and NAS_M_PMP004 will be the last to run.
|  | e.g. NAS_M_PMD002 |  | e.g. NAS_M_PMD002 |  |  | e.g. Aspley South Ammonia Dosing Line 2 Pump |  |  |  |  | e.g. Operation List : [1] = 0 NAS_M_PMD001, 2nd priority
|  | e.g. NAS_M_PMD003 |  | e.g. NAS_M_PMD003 |  |  | e.g. Aspley South Ammonia Dosing Line 3 Pump |  |  |  |  | e.g. Operation List : [2] = 1 NAS_M_PMD002, 3rd priority
|  | e.g. NAS_M_PMD004 |  | e.g. NAS_M_PMD004 |  |  | e.g. Aspley South Ammonia Dosing Line 4 Pump |  |  |  |  | e.g. Operation List : [3] = 2NAS_M_PMD003, 4th priority
|  | e.g. NAS_M_PMD005 |  | e.g. NAS_M_PMD005 |  |  | e.g. Aspley South Ammonia Dosing Line 5 Pump |  |  |  |  | e.g. Operation List : [4] = 4 NAS_M_PMD005, 5th priority
|  | e.g. NAS_M_PMD006 |  | e.g. NAS_M_PMD006 |  |  | e.g. Aspley South Ammonia Dosing Line 6 Pump |  |  |  |  | e.g. Operation List : [5] = 3 NAS_M_PMD004, lowest priority
Duy/Standy Pair 2 |  | e.g. NAS_M_TNK002 |  | e.g. NAS_M_TNK002 |  |  | e.g. Aspley Hypo Dosing Tank 2 |  |  |  |  | e.g. Operation List : [0] = 0, NAS_M_TNK002, highest priorty |  |  | e.g. accordingly, Aspley Hypo Dosing Tank 2 will be selected first to provide chemical. This is then follwed by Tank 3, Tank 4, Tank 5, Tank 6, Tank 7, Tank8, Tank 9, Tank 10, and Tank 11 will the last to be selected.
|  | e.g. NAS_M_TNK003 |  | e.g. NAS_M_TNK003 |  |  | e.g. Aspley Hypo Dosing Tank 3 |  |  |  |  | e.g. Operation List : [1] = 1, NAS_M_TNK003, 2nd priorty
|  | e.g. NAS_M_TNK004 |  | e.g. NAS_M_TNK004 |  |  | e.g. Aspley Hypo Dosing Tank 4 |  |  |  |  | e.g. Operation List : [2] = 2, NAS_M_TNK004, 3rd priorty
|  | e.g. NAS_M_TNK005 |  | e.g. NAS_M_TNK005 |  |  | e.g. Aspley Hypo Dosing Tank 5 |  |  |  |  | e.g. Operation List : [3] = 3, NAS_M_TNK005, 4th priorty
|  | e.g. NAS_M_TNK006 |  | e.g. NAS_M_TNK006 |  |  | e.g. Aspley Hypo Dosing Tank 6 |  |  |  |  | e.g. Operation List : [4] = 4, NAS_M_TNK006, 5th priorty
|  | e.g. NAS_M_TNK007 |  | e.g. NAS_M_TNK007 |  |  | e.g. Aspley Hypo Dosing Tank 7 |  |  |  |  | e.g. Operation List : [5] = 5, NAS_M_TNK007, 6th priorty
|  | e.g. NAS_M_TNK008 |  | Refer Supporting info in REX |  |  | e.g. Aspley Hypo Dosing Tank 8 |  |  |  |  | e.g. Operation List : [6] = 6, NAS_M_TNK008, 7th priorty
|  | e.g. NAS_M_TNK009 |  | Refer Supporting info in REX |  |  | e.g. Aspley Hypo Dosing Tank 9 |  |  |  |  | e.g. Operation List : [7] = 7, NAS_M_TNK009, 8th priorty
|  | e.g. NAS_M_TNK010 |  | Refer Supporting info in REX |  |  | e.g. Aspley Hypo Dosing Tank 10 |  |  |  |  | e.g. Operation List : [8] = 8, NAS_M_TNK0010, 9th priorty
|  | e.g. NAS_M_TNK011 |  | e.g. NAS_M_TNK011 |  |  | e.g. Aspley Hypo Dosing Tank 11 |  |  |  |  | e.g. Operation List : [9] = 9, NAS_M_TNK0011, Lowest priorty
Alarms
Test Action/s |  |  | Expected Results |  | Tag |  | Description |  | Category (Priority) | Alarm Privlege | Delay | Masked | Verify Trend | Values / Comments |  | Pass/Fail
e.g. Set p_M (Number of Connected Duty Devices) greater than 16 e.g. set p_m less than 1 e.g. set p_N greater then p_M |  |  | Duty Block Fault Active |  | A_fault |  | Fault |  | e.g. Action (2) | e.g. Operator | e.g. 2s | e.g. N | e.g. P | e.g. Performed as expected. |  | e.g. P (J.B.) 21/5
Operating Modes
Test Action/s |  |  | Expected Results |  | Tag |  | Description |  | Verify Trend | Values / Comments | [5 empty] | Pass/Fail
Place in Auto Duty Mode |  |  | The duty rotation happens each time the process unit goes offline |  |  |  | Auto Duty |  | e.g. P | e.g. Performed as expected. | [5 empty] | e.g. P (J.B.) 21/5
Place in Fixed Duty Mode |  |  | The equipment selected for duty will operate (as Duty) if available |  |  |  | Fixed Duty |  | e.g. P | e.g. Performed as expected. | [5 empty] | e.g. P (J.B.) 21/5
Place in Time Based Duty Mode |  |  | The online equipment automatically rotates to the standby equipment, if available after an elapsed time |  |  |  | Time Based |  | e.g. P | e.g. Performed as expected. | [5 empty] | e.g. P (J.B.) 21/5
Additional Functions
Test Action/s |  |  | Expected Results |  | Tag |  | Description |  | Verify Trend | Values / Comments | [5 empty] | Pass/Fail
Test Disable Duty cycle from SCADA |  |  | Mask alarm a_Fault No duty device available |  | cDSABL |  | SCADA Command - Disable |  | e.g. P | e.g. Performed as expected. | [5 empty] | e.g. P (J.B.) 21/5
Manually select the devices priority to change device's duty priority in list from SCADA |  |  | Manully change the Setup of Operator-Set drive list |  | c_Operator_list |  | Conrol Variabel - The operator-set list |  | e.g. P | e.g. Performed as expected.
Load a new list from SCADA |  |  | Load new Operator cycling sequence |  | c_Load |  | Load the operator-set drive list |  | e.g. P | e.g. Performed as expected. | [5 empty] | e.g. P (J.B.) 21/5
Manually select to cycle through the list from SCADA |  |  | Cycle through the cycling sequence |  | c_CycleNow |  | Manually Cycle the list now |  | e.g. P | e.g. Performed as expected. | [5 empty] | e.g. P (J.B.) 21/5
Defect Number | Defect Description | [13 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: | [5 empty] | Seqwater Witness: | [7 empty] | Completed / Passed:
Signature: | [5 empty] | Signature: | [7 empty] | Date:
X-XXX-XXX-XXX Duty Testing REX no. XXX/XXXXX
Note on B47: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on R47: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.

## Supervisory Control
SUBJECT |  | SHEET |  |  |  |  | REFERENCE
TEST SHEET |  | Control Systems FAT / SAT / Out of Service Supervisory Controller |  |  |  |  | XXX
Rev - XX
Project Name: |  | XXXXXX |  |  |  |  | Project Number : |  |  | Testing Officer: |  |  |  |  | Date:
[7 empty] | Library Block Version: |  |  | Version of Code Tested:
Check Results : |  | P | = Acceptable |  | F | = Unacceptable |  |  |  | NA |  | = Not Applicable
SCADA Page Name |  |  | Ensure all devices accurately displayed on SCADA page(s). |  | Pass / Fail: | e.g. P |  | Description | e.g. Treated Water Supervisory Controller |  |  |  |  | Equipment ID | e.g. TLI_6UC001
Alarms
Input Tag | Test Description | Test Action |  |  | Expected Results | [6 empty] | Alarm Tag | Alarm Description | Category (Priority) | Priviledges | Pass/Fail
cDSABL | Disable from SCADA | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Select Disable command from SCADA. |  |  | e.g. SCADA status changes to state "Disabled" and alarm appears. qSERV output turns Off. When Disable command is deselected from SCADA, SCADA status changes to state "In Service" and alarm turns Off. qSERV output tuns On. | [6 empty] | sDSABLD | e.g. Disabled | e.g. Warning (3) | e.g. Supervisor (alarm ack, command) | e.g. P (J.B.) 21/5
cGRPDSABL | Group Disable from SCADA | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Select Group Disable command from SCADA. |  |  | e.g. SCADA status changes to state "Disabled" and alarm appears. qSERV output turns Off. Pump TLI_6PMP001 also enters "Disabled" state. When Group Disable is deselected, SCADA status changes to state "In Service" and alarm turns Off. qSERV output tuns On. Pump TLI_6PMP001 stays in a Disabled state until it is reset from its SCADA popup. | [9 empty] | e.g. Supervisor (alarm ack, command) | e.g. P (J.B.) 21/5
mGRPDSABL | Group Disable from higher level Supervisory Controller | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Select Group Disable command from higher level supervisory controller SCADA popup. |  |  | e.g. SCADA status changes to state "Disabled" and alarm appears. qSERV output turns Off. Pump TLI_6PMP001 also enters "Disabled" state. | [9 empty] | e.g. Supervisor (alarm ack) | e.g. P (J.B.) 21/5
mDEVFL | Device Fault | e.g. Generate a fault on a critical device within the process group |  |  | e.g. SCADA popup shows state "../Faulted" and the "Device Fault" indication is highlighted. | [6 empty] | aDEVFL | e.g. Device Fault | e.g. Warning (3) | e.g. Supervisor (alarm ack) | e.g. P (J.B.) 21/5
cRSET | Fault Reset | e.g. Start with aDEVFL active due to a device fault and command a reset of alarms |  |  | e.g. After resetting device fault, supervisory conroller alarms stay active until reset button on supervisory controller popup is pressed. | [6 empty] | aFL | e.g. Fault | e.g. Warning (3) | e.g. Supervisor (alarm ack, command) | e.g. P (J.B.) 21/5
mCRSH | Crash Stop from higher level supervisory controller | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Place the higher level supervisory controller in Manual and select "Crash Stop" |  |  | e.g. SCADA popup shows status "Crash Stop", the qSERV output turns off and the general fault alarm turns on | [10 empty] | e.g. P (J.B.) 21/5
Interlocks
Input Tag | Test Description | Test Action |  | Expected Results |  |  |  | Interlock 1 | Interlock 2 | Interlock 3 | Interlock 4 | Interlock 5 | Interlock 6 | Interlock 7 | Interlock 8 | Pass/Fail
mSHILOCKS_OK | Shutdown Interlocks | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Set each interlock in turn to an Unhealthy state and monitor the response. |  | e.g. Interlock's associated alarm turns on. Sup controller Alarms section shows "Shutdown Interlocks" in yellow and individual interlock display text is correct. And qSERV and sSERV turns to OFF. When interlock returns to Healthy state, alarm is reset automatically. |  |  |  | e.g. MCC Mains Power Not Healthy | e.g. Control Power Not Healthy | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. P (J.B.) 21/5
mSILOCKS_OK | Service Permissive Interlocks | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Set each interlock in turn to an Unhealthy state and monitor the response. |  | e.g. Interlock's associated alarm turns on, sSILOCKS_OK truns off. Sup controller Alarms section shows "Start Interlocks" in yellow and individual interlock display text is correct. When interlock returns to Healthy state, alarm is reset automatically. And loss of sSILCOKS_OK shall have no effect on the control of the block while the Supervisory Control in service |  |  |  | e.g. No Hypo Duty Pump Available | e.g. South Chemical Dosing Sequence Unhealthy | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. P (J.B.) 21/5
mCRILOCKS_OK | Crash Stop Interlocks (Latched) | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Set each interlock in turn to an Unhealthy state and monitor the response. |  | e.g. Interlocks associated alarm turns on and sCRILOCKS_OK turns off. Sup controller Alarms section shows "Crash Interlocks" in yellow and individual interlock display text is correct and qSERV (for one scan) and sSERV turn to Off, qCRSH (one scan) turns On . When interlock returns to Healthy state, alarm stays on until Reset on Supervisory Controller popup pressed. |  |  |  | e.g. Reservoir Low Level | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. N/A | e.g. P (J.B.) 21/5
Operating Modes | [14 empty] | Trends
Input Tag | Test Description | Test Action |  |  |  | Expected Results | [5 empty] | Priviledges | Pass/Fail |  | Output | Pass/Fail
cSHTDOWN | Manual Shutdown from SCADA | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Select "Manual" from SCADA and press "Shutdown" button. |  |  |  | e.g. SCADA status shows state "Shutdown" and qSERV output is Off. | [5 empty] | e.g. Supervisor | e.g. P (J.B.) 21/5 |  | sAUTO | e.g. P (J.B.) 21/5
cSERV | Manual Service from SCADA | e.g. Press "Service" button on SCADA |  |  |  | e.g. SCADA status changes to state "In Service" and qSERV output is On. | [5 empty] | e.g. Supervisor | e.g. P (J.B.) 21/5 |  | sDSABLD | e.g. P (J.B.) 21/6
cCRSH | Manual Crash Stop from SCADA | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Manual, the qSERV output is On and the status is "In Service" or "Running". Press "Crash Stop" button on SCADA. |  |  |  | e.g. SCADA status shows state "Crash Stop" and qSERV output is Off. | [5 empty] | e.g. Supervisor | e.g. P (J.B.) 21/5 |  | sSERV | e.g. P (J.B.) 21/7
cGRPAUTO | Set Group Auto from SCADA | e.g. Start with supervisory controller and all process group devices in Manual. Press the "Group Auto" button from the supervisory controller popup on SCADA. |  |  |  | e.g. All supervisory controller and all process group devices change to "Auto" state | [5 empty] | e.g. Supervisor | e.g. P (J.B.) 21/5
mGRPAUTO | Set Group Auto from higher level Supervisory Controller | e.g. Start with supervisory controller and all process group devices in Manual. Press the "Group Auto" button from the higher-level supervisory controller popup on SCADA. |  |  |  | e.g. All supervisory controller and all process group devices change to "Auto" state | [6 empty] | e.g. P (J.B.) 21/5
mDEVAVL | Devices Available/Not Available | e.g. Set a critical device to manual |  |  |  | e.g. SCADA popup shows status "Devices Not Available". On setting critical device back to auto, supervisory controller popup shows "Devices Available" | [6 empty] | e.g. P (J.B.) 21/5
mDEVRUN | Devices Running/Not Running | e.g. Ensure at least one process group device has stopped |  |  |  | e.g. SCADA popup shows status "Devices Off". When all devices are running, SCADA popup shows "Devices Running" | [6 empty] | e.g. P (J.B.) 21/5
mSHTDOWN | Shutdown from higher level controller | e.g. Start with inputs manipulated in the required state so that the Supervisory Controller is in Auto, the qSERV output is On and the status is "In Service" or "Running". Place the higher level supervisory controller in Manual and select "Shutdown" |  |  |  | e.g. SCADA popup shows status "Shutdown" and the qSERV output turns off | [6 empty] | e.g. P (J.B.) 21/5
mSERV | Higher level return to service | e.g. Press the "Service" button higher level supervisory controller |  |  |  | e.g. SCADA popup for this supervisory controller show status "In Service" and the qSERV output turns on | [6 empty] | e.g. P (J.B.) 21/5
Additional Tests
Test Action/s |  |  |  | Expected Results |  |  |  | Values / Comments | [7 empty] | Pass/Fail
Defect Number | Defect Description | [13 empty] | Defect Corrected (Initials) | Defect Corrected (Date) | Defect Rating (H,M,L)
Testing Officer: |  |  |  |  | Seqwater Witness: | [8 empty] | Completed / Passed:
Signature: |  |  |  |  | Signature: | [8 empty] | Date:
X-XXX-XXX-XXX Supervisory Controller Testing REX no. XXX/XXXXX
Note on B43: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.
Note on T43: Note: All high priority (H) defects should be rectified before progressing further and that medium priority (M) and low priority (L) can progress based on Seqwater approval.