## Template Cover Page
Template
I-TMP-STD-008
Master Alarms Database
Document Number: TEM-00254
This document is the property of Seqwater. It must not be copied or reproduced in any way whatsoever without the authority of Seqwater. This document is uncontrolled when printed. An electronic database manages and stores the controlled version.
Rev no. | Description | Process Owner |  | Approved for issue
|  | Position | Name | Position | Name | Date
4 | • 'Instructions' worksheet added and 'Instructions' section moved from 'Worksheet' to 'Instructions' sheet • Columns for 'Rev.' and 'P&ID Number' added in Worksheet • Notes added to 'Alarm Priority' and 'Notes' columns. • Column for 'Ack. Authority' and 'Corrective action' removed. • More information added to 'Instructions' section. • A3 Ttille block added in. | Lead Automation and Process Control Engineer | Refere Supporting Information in REX | Team Leader Process ＆ Analysis | Refer Supporting Information in REX | 2023-09-22
Subject Matter Expert Authorisation
Rev no. | Name |  | Date |  | RPEQ #
4 | Refer Document Properties in REX |  | 2023-09-22 |  | Refer Doc Properties in REX
DOCUMENT SENSITIVITY: OFFICIAL (Public)
Delete This page before submitting to Process Control Systems Folders

## Title Block
A4 Title block - Populate only this block. A3 Block will populate automatically
| REVISION (As Constructed ) |  |  |  |  | CONTRACTOR LOGO | LOCATION: e.g. EAST BANK WTP |  | AS CONSTRUCTED
| NO. | DESCRIPTION | DATE | PREPARED BY | CHECKED BY |  |  |  | APPROVER
[7 empty] | SUBLOCATION: e.g. RAW WATER PUMP STATION |  | DATE
SIGNATURE
PROJECT NUMBER: e.g. PID123
RPEQ No.
FOR CONSTRUCTION
[7 empty] | DOCUMENT DESCRIPTION : e.g. WELL G PUMP REFURBISHMENT |  | APPROVER
DATE
[7 empty] | REX ID: ANN/NNNNNN | I-LST-XXX-00X | SIGNATURE
RPEQ No.
A3 title block, this will populate automatically when above A4 title block is populated
| REVISION (As Constructed ) | [10 empty] | CONTRACTOR LOGO | LOCATION: e.g. EAST BANK WTP |  | AS CONSTRUCTED
| NO. | DESCRIPTION | [6 empty] | DATE | PREPARED BY | CHECKED BY |  |  |  | APPROVER
[13 empty] | SUBLOCATION: e.g. RAW WATER PUMP STATION |  | DATE
SIGNATURE
PROJECT NUMBER: e.g. PID123
RPEQ No.
FOR CONSTRUCTION
[13 empty] | DOCUMENT DESCRIPTION : e.g. WELL G PUMP REFURBISHMENT |  | APPROVER
DATE
[13 empty] | REX ID: ANN/NNNNNN | I-LST-XXX-00X | SIGNATURE
RPEQ No.
Notes:
The Master Alarms Database Template is a maintained process control systems (PCS) document and the process control document coordinator (as per X-PRO-STD-019 Process Control Systems Information Maintenance) shall be contacted via engineering@seqwater.com.au for access to this document.
Document Number and REX ID - To be requested from PCS document coordinator through engineering@seqwater.com.au.
Delete Tempalte Cover Page Tab. Before submitting to engineering@seqwater.com.au.
Information within body of template is for example only.
The main cover page shall only show the revision number for "AS CONSTRUCTED", in between revisions shall have alphabetical suffix and shall be saved in the project directory.
This text box shall be deleted when the template is populated.
Note on K2: Clear the text LOCATION: e.g. Insert only the Location.
Note on I3: Peer Review
Note on K4: Remove the text SUBLOCATION: e.g. Insert only sublocation name.
Note on K6: Remove the text WORK DESCRIPTION: e.g. Insert only name of work description
Note on M11: Document Number and REX ID - To be requested from PCS document coordinator through engineering@seqwater.com.au.
Note on I13: PLEASE NOTE: Once the notes are understood hide them by Right-clicking somewhere on the cell and select hide the comment.
Note on R14: Clear the text LOCATION: e.g. Insert only the Location.
Note on P15: Peer Review
Note on R16: Remove the text SUBLOCATION: e.g. Insert only sublocation name.
Note on R18: Remove the text WORK DESCRIPTION: e.g. Insert only name of work description
Note on R21: Clear and remove text DOCUMENT NUMBER: e.g. Insert only document number & start with I-LST-
Note on T23: Document Number and REX ID - To be requested from PCS document coordinator through engineering@seqwater.com.au.

## Instructions
Master Alarms Database - Alarms Prioritisation and Classification Worksheet
Instructions
Step 1 | For guidance on how to populate this sheet refer I-SPE-STD-005 High Priority Alarms & Interlocks Management (SPE-00356) and I-SPE-STD-006 Monitoring and Control System Alarm and Event Management (SPE-00357).
Step 2 | Fill out details in all blue columns where required. Grey columns are automatically calculated and do not need data entry.
Process engineers to populate the majority of the table with an exception fo Alarm tag, this is to be filled in by a Control System engineer.
Step 3 | Against each alarm, assign a consequence (per the Seqwater Risk Matrix) in the appropriate Loss Type as per the Consequence Table
Step 4 | Select the appropriate Operator Response Time. Not assigning a response time, defaults the alarm to Priority 5 (an Event). The Priority column will then determine the appropriate Alarm Priority level for the given
Consequence and Response Time.
Step 5 | Complete remaining alarm details section.
Step 6 | Review the alarm breakdown Summary and adjust or request exemption if required.
Step 7 | Assign the correct operator Alarm Dial Out Category from the drop down.
Assigning Alarm Dialler Categories. Alarms generated by
| 1 -Power Outage | Phase Failure Relay Alarm or other power outage indications.
| 2- Process Critical | HACCP Action/Critical alarms or water quality alarms
| 3- Fluoride | All Fluoride alarms higher than priority 5 OR operator requested alarms
| 4- Plant Shutdown | Any alarm that unexpectedly causes a plant shutdown. (not including planned shutdowns)
| 5- Fire or Security | Fire Alarm or Security System alarm
| 6- Dialer Fault | Test alarm to test Alarm Dialler. This test is generated from SCADA
Step 8 | Review the alarm priority guidelines in I-SPE-STD-006 for alarm priority ranges.
Note | The spreadsheet assumes the alarms are acknowledged by an operator.
Add new rows before the end of the table or extend the table downwards to keep formulas.

## Worksheet
Master Alarms Database - Alarms Prioritisation and Classification Worksheet
[8 empty] | Consequence | [9 empty] | Total
[8 empty] | 0 | Event | [8 empty] | 36
[8 empty] | 1 | Insignificant | [7 empty] | 36 | Allowed | Priority
[8 empty] | 2 | Minor | [7 empty] | 1 | 1 | Critical
[8 empty] | 3 | Moderate | [7 empty] | 1 | 2 | Action
[8 empty] | 4 | Major | [7 empty] | 6 | 6 | Warning
[17 empty] | 13 | 29 | Information
[8 empty] | 5 | Catastrophic | [7 empty] | 15 | No Limit | Event
Rev | P&ID Number | Equipment Number | Alarm tag | Alarm Type | Alarm Area | Alarm Description | Type | Health and Safety | Environment | Legal and Regulatory | Reputation, Social and Community | Financial | Water Quality and Supply | Highest Consequence Rating | Consequence | Required Response Time | Calc | Alarm Priority | Dial Out Assignment | Alarm Owner | CCP Type | Instrument Parameter | Engineering Units | Default Setpoint | Analogue Limits | Alarm On Delay | Alarm Off Delay | Dead band | Alarm Hold Time | Alarm Masking | Alarm Causes | Consequence of Alarm | Notes
|  | W08-I-1AIT563 | W08_1AIT563_aHI | Analogue | Caloundra Street | Caloundra Street WQMF Free Chlorine High | Alarm | 2 | 1 | 3 | 2 | 1 | 2 | 3 | Moderate | Within 15 Minutes | 78 | 3 | 2-Process Critical | Water Quality | Action | Chlorine | mg/L | 3 | 3-5 | Instant |  | NA |  |  |  | Chlorine Dosing Shutdown
|  | W08-I-1AIT563 | W08_1AIT563_aLO | Analogue | Caloundra Street | Caloundra Street WQMF Free Chlorine Low | Alarm | 2 | 1 | 3 | 2 | 1 | 2 | 3 | Moderate |  | 3 | 5 | 2-Process Critical | Water Quality | Critical | Chlorine | mg/L | 1 | 0-1 | Instant |  | NA |  |  |  | Chlorine Dosing Shutdown
|  | TNP-I-1AIT032 | TNP_1AIT032_aHH | Analogue | Raw Water | North Pine WTP Raw Water Turbidity High High | Alarm | 5 | 4 |  |  |  |  | 5 | Catastrophic | Within 1 Minute | 250 | 1 | No Dial | Electrical | Not CCP | Turbidity | NTU | 18 | 0-350 | 90s |  | 5%
|  | TNP-I-1AIT032 | TNP_1AIT032_aHI | Analogue | Raw Water | North Pine WTP Raw Water Turbidity High | Alarm | [5 empty] | 2 | 2 | Minor | Within Hours | 36 | 4 | No Dial | Electrical | Not CCP | Turbidity | NTU | 15 | 0-350 | 90s |  | 5%
|  | TNP-I-1AIT032 | TNP_1AIT032_aLO | Analogue | Raw Water | North Pine WTP Raw Water Turbidity Low | Alarm | [5 empty] | 1 | 1 | Insignificant | Within Hours | 18 | 4 | No Dial | Electrical | Not CCP | Turbidity | NTU | 4 | 0-350 | 90s |  | 5%
|  | TNP-I-1AIT032 | TNP_1AIT032_aLL | Analogue | Raw Water | North Pine WTP Raw Water Turbidity Low Low | Alarm | [5 empty] | 2 | 2 | Minor | Within 5 Minutes | 80 | 3 | No Dial | Electrical | Not CCP | Turbidity | NTU | 1 | 0-350 | 90s |  | 5%
|  | TNP-I-1AIT032 | TNP_1AIT032_aFL | Digital | Raw Water | North Pine WTP Raw Water Turbidity Instrument Fault | Alarm | [5 empty] | 2 | 2 | Minor | Within Hours | 36 | 4 | No Dial | Electrical | Not CCP |  |  |  |  | 5s
|  | TLO-I-2AIT502 | TLO_2AIT502_aACTHI | Analogue | Stabilised Water | HACCP Critical Lowood WTP Stabilised Water pH High | Alarm | 4 | 2 | 4 | 1 | 1 | 4 | 4 | Major | Within 15 Minutes | 104 | 2 | 4-Plant Shutdown | Water Quality | Critical | pH | pH | 8.2 | 4-9 | Instant |  | NA |  | Not Masked |  | Plant Shutdown
|  | TLO-I-2AIT502 | TLO_2AIT502_aCRTHI | Analogue | Stabilised Water | HACCP Action Lowood WTP Stabilised Water pH High | Alarm | 2 |  | 3 |  |  | 4 | 4 | Major | Within Hours | 72 | 3 | 2-Process Critical | Water Quality | Action | pH | pH | 7.8 | 4-9 | 30s |  | 0.2 |  | Not Masked |  | Clear Water pumps shutdown
|  | TLO-I-2AIT502 | TLO_2AIT502_aHH | Analogue | Stabilised Water | Lowood WTP Stabilised Water pH High High | Alarm | [5 empty] | 2 | 2 | Minor | Within 15 Minutes | 52 | 3 | No Dial | Water Quality | Not CCP | pH | pH | 7.7 | 4-9 | 90s |  | 5%
|  | TLO-I-2AIT502 | TLO_2AIT502_aHI | Analogue | Stabilised Water | Lowood WTP Stabilised Water pH High | Alarm | [5 empty] | 2 | 2 | Minor | Within Hours | 36 | 4 | 1-Power Outage | Operations | Not CCP | pH | pH | 7.6 | 4-9 | 120s |  | 5%
|  | TLO-I-2AIT502 | TLO_2AIT502_aLO | Analogue | Stabilised Water | Lowood WTP Stabilised Water pH Low | Alarm | [5 empty] | 2 | 2 | Minor | Within Hours | 36 | 4 | No Dial | Operations | Not CCP | pH | pH | 6.4 | 4-9 | 120s |  | 5%
|  | TLO-I-2AIT502 | TLO_2AIT502_aLL | Analogue | Stabilised Water | Lowood WTP Stabilised Water pH Low Low | Alarm | [5 empty] | 2 | 2 | Minor | Within 15 Minutes | 52 | 3 | No Dial | Water Quality | Not CCP | pH | pH | 6 | 4-9 | 90s |  | 5%
|  | TLO-I-2AIT502 | TLO_2AIT502_aFL | Digital | Stabilised Water | Lowood WTP Stabilised Water pH Instrument Fault | Alarm | 2 |  |  |  |  | 2 | 2 | Minor | Within 15 Minutes | 52 | 3 | No Dial | Water Quality | Not CCP |  |  |  |  | 5s
|  | TWB-M-2PMP032 | TWB_2PMP032_AMP_aHH | Analogue | Settled Water | West Bank WTP Settled Water Pump 2 Current High High | Alarm | [5 empty] | 2 | 2 | Minor | Within Hours | 36 | 4 | No Dial | Electrical | Not CCP | Current | A | 48 | 0-50 | 5s |  | NA
|  | TWB-M-2PMP032 | TWB_2PMP032_AMP_aHI | Analogue | Settled Water | West Bank WTP Settled Water Pump 2 Current High | Alarm |  |  |  |  | 1 |  | 1 | Insignificant | Within Hours | 18 | 4 | No Dial | Electrical | Not CCP | Current | A | 44 | 0-50 | 5s |  | 10%
|  | TWB-M-2PMP032 | TWB_2PMP032_AMP_aLO | Analogue | Settled Water | West Bank WTP Settled Water Pump 2 Current Low | Alarm |  |  |  |  | 1 |  | 1 | Insignificant | Within Hours | 18 | 4 | No Dial | Operations | Not CCP | Current | A | 38 | 0-50 | 5s |  | 10%
|  | TWB-M-2PMP032 | TWB_2PMP032_AMP_aLL | Analogue | Settled Water | West Bank WTP Settled Water Pump 2 Current Low Low | Alarm | [5 empty] | 2 | 2 | Minor | Within Hours | 36 | 4 | No Dial | Operations | Not CCP | Current | A | 5 | 0-50 | 5s |  | NA
|  | TWB-M-2PMP032 | TWB_2PMP032_AMP_aFL | Digital | Settled Water | West Bank WTP Settled Water Pump 2 Current Fault | Alarm | 1 | 1 |  |  |  | 1 | 1 | Insignificant | Within Hours | 18 | 4 | No Dial | Electrical | Not CCP |  |  |  |  | 5s
|  | TWB-M-2PMP032 | TWB_2PMP032_sRUN | Digital | Settled Water | West Bank WTP Settled Water Pump 2 Start | Event | [6 empty] | 0 | Event |  | 0 | 5 | No Dial | Electrical | Not CCP |  |  |  |  | 5s
|  | TWB-M-2PMP032 | TWB_2PMP032_sRUN | Digital | Settled Water | West Bank WTP Settled Water Pump 2 Stop | Event | [6 empty] | 0 | Event |  | 0 | 5 | No Dial | Electrical | Not CCP |  |  |  |  | 5s
|  | TWB-M-2PMP032 | TWB_2PMP032_aTOL | Digital | Settled Water | West Bank WTP Settled Water Pump 2 Overload Tripped | Alarm |  |  |  |  | 1 | 2 | 2 | Minor | Within Hours | 36 | 4 | No Dial | Electrical | Not CCP |  |  |  |  | 5s
|  | TWB-M-2PMP032 | TWB_2PMP032_sCBOPEND | Digital | Settled Water | West Bank WTP Settled Water Pump 2 Circuit Breaker Open | Event | [6 empty] | 0 | Event |  | 0 | 5 | No Dial | Electrical | Not CCP |  |  |  |  | 5s
|  | TWB-M-2PMP032 | TWB_2PMP032_aESTOP | Digital | Settled Water | West Bank WTP Settled Water Pump 2 Emergency Stop | Alarm |  |  | 2 |  | 1 | 2 | 2 | Minor | Within Hours | 36 | 4 | No Dial | Electrical | Not CCP |  |  |  |  | 5s
|  | BLI-M-1SBP101 | BLI_1SBP101_CTRLPWRFL.aALM | Digital | Settled Water | Raw Water Pump Control Power Failure | Alarm | [5 empty] | 1 | 1 | Insignificant | Within 15 Minutes | 26 | 4 | No Dial | Electrical | Not CCP |  |  |  |  | 0s | 5s |  | 5s | cDSABLD OR BLI_1SBP101.aDSABLD | NOT BLI_1SBP101_iCTRLPWROK | Interlock pump (triggers 1SBP101.aFL)
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
[14 empty] | 0 | Event |  | 0 | 5 | No Dial
Note on S12: Total Alarms and Events
Note on S13: Number of alarms allowed for each alarm category.
Note on C23: As per X-PRO-STD-06 Equipment Naming. Minus the facility code and equipment designation
Note on D23: Control System engineer to populate this field Descriptor structure as per I-SPE-STD-010 Tag Naming
Note on F23: Free text field used to help filter and search for alarms.
Note on S23: For categorisation refer I-SPE-STD-006 and I-SPE-STD-005
Note on T23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Refer to 'Instructions' tab for details.
Note on U23: Department responsible for managing alarm setpoint and delay.
Note on V23: Water Quality CCP Type Critical High / Low Action High / Low
Note on AA23: Delay in seconds before the alarm activates.
Note on AB23: Delay in seconds after the alarm de-activates.
Note on AC23: For self-resetting alarms, what is the % or absolute value, the instrument signal must retrace for the alarm to reset.
Note on AD23: Minimum HOLD time to latch the output Alarms for minimum hold time
Note on AE23: Mask this alarm when the listed alarms are also active
Note on AG23: Automatic Action to be taken when this alarm triggers or other plant effects. Typically Plant Shutdown.
Note on AH23: Alarm masking information to be added here along with any known corrective actions

## Seqwater Risk Matrix
Seqwater Risk Matrix |  |  | Hazard Effect / Consequence | [13 empty] | 1
|  |  | (Where an event has more than one ‘Loss Type’, choose the ‘Consequence’ with the highest rating) | [13 empty] | 1
Loss Type |  |  | Insignificant | Minor | Moderate | Major | Catastrophic | [9 empty] | 1
(Additional ‘Loss Types’ may exist for an event; identify & rate accordingly) | [9 empty] | Consequence | [6 empty] | 1
Health and Safety |  |  | Symptoms requiring no treatment or first aid treatment only. | Minor temporary injury or illness requiring medical treatment. | Moderate injury or temporary impairment. | Permanent injury or impairment. | ≥1 Fatalities. | Response Time | Likelihood | Insignificant | Minor | Moderate | Major | Catastrophic |  |  | 1
|  |  | Returned to full duties. | Inability to complete rest of shift or modified duties. | One or more entire shift missed as a result. |  |  | Within 1 minute | Almost Certain | Medium | High | High | Extreme | Extreme |  |  | 1
Environment |  |  | Localised, on site, actual or potential nuisance. Routine short term remediation. | Localised on/off site environmental nuisance. Routine short term remediation (<1 month). | Localised on/off site actual or potential environmental harm/impact to the ecosystem, flora, fauna (excluding declared and rare threatened and vulnerable species) requiring limited resources to mitigate (>1 - <3 months). | Localised on/off site actual or potential serious harm/Impacts to the ecosystem, flora, fauna (including declared and rare threatened and vulnerable species) requiring substantial resources to mitigate (>3 - <6 months). | Actual or potential widespread environmental harm/Impacts to the ecosystem, flora, fauna requiring extensive resources to mitigate (>6 months). | Within 5 minutes | Likely | Medium | Medium | High | High | Extreme |  |  | 1
Legal and Regulatory |  |  | Low level legal matter Regulatory reporting not required. | Minor legal issue, non-compliance and/or breach of a regulation. | Serious breach of law; investigation/report to regulatory body, prosecution and/or possible moderate penalty. | Major breach of the law; considerable prosecution and penalties. | Long term legal action, government inquiry, significant penalties, prosecutions. Potential jail terms. | Within 15 minutes | Possible | Low | Medium | Medium | High | High |  |  | 1
Reputation / Social and Community |  |  | Slight impact - public awareness may exist but no public concern. | Limited impact - localised public/media concern. | Considerable impact - regional public/media concern. | National impact - national public/media attention. | International impact - international public/media attention. | Within hours | Unlikely | Low | Low | Medium | Medium | High |  |  | 1
|  |  | Superficial infringement of cultural heritage and no disturbance to heritage sites. | Limited damage to heritage sites. Localised cultural heritage reputational damage. | Moderate damage to regional heritage sites, regional cultural heritage reputational damage. | Significant damage to important QLD heritage site. Major infringement of cultural heritage. | Highly offensive infringement of cultural heritage. | Events only | Rare | Event | Event | Event | Event | Event |  |  | 1
[7 empty] | Total destruction of nationally significant heritage locations. | [9 empty] | 1
Financial |  |  | ≤$250k | >$250k - ≤$1m | >$1m - ≤$2.5m | >$2.5m - ≤$5m | >$5m |  | Alarm priorities Calc | 1 | 2 | 3 | 4 | 5 |  |  | 1
|  |  | ≤10% overspend of project budget and/or realisation in delivery of benefits. | >10% - ≤25% overspend of initiative/project budget and/or realisation in delivery of associated benefits. | >25% - ≤50% overspend of initiative/project budget and/or realisation in delivery of associated benefits. | >50% - ≤75% overspend of initiative/project budget and/or realisation in delivery of associated benefits. | >75% overspend of initiative/project budget and/or realisation in delivery of associated benefits |  | 50 | 50 | 100 | 150 | 200 | 250 |  |  | 1
Water Quality and Supply |  |  | Reservoirs lower than agreed normal operating levels for <4 hours or restricted output from treatment plant. No loss of supply from any bulk water supply point. | Reservoirs approaching agreed communication trigger levels. Treatment plant at restricted output requiring supply reconfiguration. | Reservoir levels below communication trigger levels > 8 hours. Reduced operating volumes due to treatment plant capability for a short duration resulting in retailer network configuration changes. | Unplanned loss of water supply from any bulk water supply point to any non-network or connected customers supply zones for up to 24 hours. | Unplanned loss of water supply from any bulk water supply point to any non-network or network connected supply zones for > 24 hours. |  | 40 | 40 | 80 | 120 | 160 | 200 |  |  | 1
|  |  | Little or no disruption to normal operations. | No loss of supply from any bulk water supply point. | Widespread aesthetic impacts for SEQ Drinking Water Supply System plants. Repeated breach of guideline value / specification in quarterly Water Quality reports for chronic health parameters. | Potential acute health impacts (no declared outbreak expected). | Potential acute health impacts, declared outbreak expected. |  | 26 | 26 | 52 | 78 | 104 | 130 |  |  | 1
|  |  |  | Localised aesthetic impacts for non-SEQ Drinking Water Supply System plants. Isolated sample reports above guideline value / specification for chronic health parameters. |  |  |  |  | 18 | 18 | 36 | 54 | 72 | 90 |  |  | 1
Likelihood |  |  | Risk Rating | [5 empty] | 1 | 1 | 2 | 3 | 4 | 5 |  |  | 1
Almost Certain | The event is expected to occur in most circumstances | >90% | Medium | High | High | Extreme | Extreme | [9 empty] | 1
Likely | The event will probably occur in most circumstances. | >50–90% | Medium | Medium | High | High | Extreme | [9 empty] | 1
Possible | The event might occur, but not expected to occur under normal circumstances. | >10–50% | Low | Medium | Medium | High | High | [9 empty] | 1
Unlikely | The event could occur at some time, but only in unusual circumstances | >2–10% | Low | Low | Medium | Medium | High | [9 empty] | 1
Rare | The event could occur only in exceptional circumstances | <2% | Low | Low | Low | Medium | Medium | [9 empty] | 1
1
No Dial
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1