## Sheet1 (hidden)
1 | Source Protection Planning Unit
2 | Asset Planning
3 | Asset Lifecycle Capability
4 | Project Delivery
5 | Tactical Asset Maintenance
6 | Process Engineering
7 | Process Improvement
8 | Operations - Supply
9 | Operations - Maintenance
10 | Water Quality Unit

## North
Drinking Water Quality Improvement Plan - Northern Region
Site | Improvement # | Process Step | Issue | Description | Origin of Improvement | Significant Risk | Responsibility | Responsibility assignment code | Due for Completion | Completed? Y/N | Risk Treatment Comments
TDY : Dayboro WTP | ALL16 | Bank Filtration | Contamination incident - Intentional contamination - Accidental contamination | An incident involving an elevated risk presented to the wells, such as cattle or ferral animals becoming entrained in the well areas introducing significantly extra faecal load to the surface surrounding the wells occuring and entering the wells via runoff. | Risk Assessment | Medium (8) | Source Protection Planning Unit | 1 | 2020-06-30 | N | Investigate all plant's pathogen reduction requirements (for crypto and viruses) and identify shortcomings with current treatment processes and develop priority list.
TIF : Image Flat WTP | TBA | Raw Water Intake | Intake of contaminated raw water during a wet weather event (seasonal) | Increased contaminant loads due to wash-in from the catchments, resulting in contaminated treated water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Consideration should be given to real-time water quality and flow monitoring of raw water sources. Assessment based on pathogen load during wet weather events overwhelming plant capability as well as causing coagulation and filter issues. Additional protozoa treatment (eg UV)
TIF : Image Flat WTP | TBA | Raw Water Intake | Intake of contaminated raw water due to incorrect source selection | Contaminant load exceeds treatment capacity | Risk Assessment | Medium (9) | Source Protection Planning Unit | 1 | 2020-06-30 | N | SPPU Investigation. There is a risk around feed from Wappa Dam direct to plant due to issues with Mn. Valves are physically locked and require a manual changeover to access the Wappa source. Source selection procedures consider the level of all storages and consideration of depth samples on dams is taken into account to assess WQ in conjunction with catchments, intake weir and dams
TIF : Image Flat WTP | TBA | Raw Water Intake |  | Increased contamination load leading to contamination of treated water | Risk Assessment | Medium (9) | Asset Planning | 2 | 2022-06-30 | N | enhanced taste and odour treatment long term planning
TIF : Image Flat WTP | IMF1 | Supernatant Return | Supernatant return to Poona Dam | Increased contaminant load | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Monitoring of supernatant return for protozoa Additional protozoa treatment Pump volumes return rates > 38 (range to be determined) ls to Poona Dam where it is diluted. This is significantly bigger than the previous pump. Turbidity is typically less than 10 NTU. No volume limit for return to the Dam. Daily water quality testing is carried out on supernatant return. Recycling supernatant to Poona Dam (within 100m of the off-take) presents potential bacterial contamination to the off-take. Recycling supernatant into Poona has the potential to concentrate pathogens in the dam due to the closed nature of the system. The net loss/gain with recycling into poona should be considered with changes in production (ie drawing out of poona faster but returning to poona fast would not necassarily elevate the risk). However, drawing from Wappa into plant 1, supernatant should not be used. To use wappa feed Seqwater would need to do another risk assessment.
TIF : Image Flat WTP | IMF3 | PAC | Under dose PAC | Contamination of treated water | Risk Assessment | Medium (9) | Project Delivery | 4 | 2019-06-30 | N | Upgrade the taste and odour treatment capability (there is a planning project) Additional taste and odour treatment capacity
TIF : Image Flat WTP | TBA | Coagulation | Over dosing alum | Potentially high level of soluble aluminium Post flocculation occurs leading to suspended solids coagulation failure | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Additional protozoa treatment barrier (ie UV) Alum dosing is digital controlled and feeds back to SCADA. Modification has been made to the sample pipe for coagulation pH instruments which has made them much more reliable and accurate. Online pH is interlocked to stop the plant. Settled water turbidity instruments are installed, connected to SCADA and are alarmed which would also pick up the loss of alum. interlocks on the alum dosing pumps
TIF : Image Flat WTP | TBA | Coagulation | Underdose alum | Poor coagulation / flocculation leading to contamination of settled water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Additional protozoa treatment barrier (ie UV) Alum dosing is digital controlled and feeds back to SCADA. Modification has been made to the sample pipe for coagulation pH instruments which has made them much more reliable and accurate. Online pH is interlocked to stop the plant. Settled water turbidity instruments are installed, connected to SCADA and are alarmed which would also pick up the loss of alum. interlocks on the alum dosing pumps
TIF : Image Flat WTP | TBA | Coagulation | Incorrect Lime dose | Incorrect pH | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Additional protozoa treatment barrier (ie UV) improve lime system - Turn down availability of pre-lime New lime clarifier has been installed. There is a lime scale build up between the batching tank and the saturator tank. It doesn’t get an acid clean.
TIF : Image Flat WTP | TBA | Coagulation | Incorrect soda ash dose (Optional Process) | Incorrect pH | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Additional protozoa treatment barrier (ie UV) improve lime system Soda ash is only used as a contingency if there is a failure of the lime system.
TIF : Image Flat WTP | IMF7 | Clarification | Clarifier boil ups | This leads to overloading of the filter and probable filter break through | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Online turbidity analysers on each clarifier. Currently there is only one instrument for each plant. Additonal protozoa treatment barrier (ie UV)
TIF : Image Flat WTP | IMF4 | Filtration | Filter break through | Potential contamination of treated water | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | Filter Master Valve Replacement (done, new one is still a problem- in defects/liability) Additional protozoa treatment barrier (ie UV)
TIF : Image Flat WTP | TBA | Whole of System | Loss of control systems incl SCADA | Loss of control system | Risk Assessment | Medium (8) | Tactical Asset Maintenance | 5 | 2019-06-30 | N | Tactical Asset Maintenance investigation Loss of SCADA increases the risk at all the other processes as all the automated monitoring is lost. water production could not continue until the PLC were replaced.
TIF : Image Flat WTP | TBA | Raw Water Intake - SOUTH MAROOCHY WEIR DIRECT | Intake of contaminated raw water during a wet weather event (seasonal) | Increased contaminant loads due to wash-in from the catchments, resulting in contaminated treated water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Consideration should be given to real-time water quality and flow monitoring of raw water sources. Assessment based on pathogen load during wet weather events overwhelming plant capability as well as causing coagulation and filter issues. Additional protozoa treatment (eg UV)
TJI : Jimna WTP | TBA | Raw Water Intake | Storm events in the catchment | Intake of raw water that exceeds the treatment capacity of the plant affecting treated water quality. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Confirm HBT assessment
TJI : Jimna WTP | TBA | Clarification (Including Coagulation, Flocculation & Clarification) | Over dosing coagulant | Ineffective coagulation affecting treated water quality. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Confirm HBT assessment
TJI : Jimna WTP | TBA | Clarification (Including Coagulation, Flocculation & Clarification) | Under dosing coagulant | Ineffective coagulation affecting treated water quality. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Confirm HBT assessment
TJI : Jimna WTP | TBA | Clarification (Including Coagulation, Flocculation & Clarification) | Under dose soda ash | Ineffective coagulation affecting treated water quality. | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Process assessment
TJI : Jimna WTP | TBA | Clarification (Including Coagulation, Flocculation & Clarification) | Overdose soda ash | Ineffective coagulation affecting treated water quality. | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Process assessment
TJI : Jimna WTP | TBA | Clarification (Including Coagulation, Flocculation & Clarification) | Ineffective flocculation | Ineffective flocculation affecting treated water quality. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Confirm HBT assessment
TJI : Jimna WTP | TBA | Filtration | Filter break- through Turbidities > 0.3 NTU | Filter break-through impacting treated water quality. | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Process assessment
TJI : Jimna WTP | TBA | Whole of system | Unreliable communications | Loss of comms/insufficient alarming | Risk Assessment | Medium (8) | Tactical Asset Maintenance | 5 | 2019-06-30 | N | Tactical Asset Maintenance investigation: SCADA now on site. Operators are now able to run plant remotely. If there is a comms failure, an alarm is generated.
TJI : Jimna WTP | TBA | Whole of system | Raw water contaminant load exceeds treatment capacity | Hazards that are not adequately managed by the barriers in the process | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Confirm HBT assessment The unmitigated risk assessment specified a 4-5 log Crypto removal; the log removal required by this plant needs to be assessed (current project)
TKR : Kirkleagh (Recreation) WTP | TBA | Raw Water Intake (Pumping Pond, Variable Depth Intake and Trash Racks) | Intake of contaminated raw water during a wet weather event (seasonal) | Contaminant load exceeds treatment capacity | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Capital upgrade to incorporate UV into the plant The protozoa (Crypto) hazard will increase when there are inflow events and during periods of high dam release when dirty water run off is significant; Concerns have been raised about the close proximity of the Kirkleagh WWTP to the WTPs raw water intake, and the risk that this may pose in the advent of an overflow event if it were to reach the dam; Releases from the dam may also have some influence on the impact of dirty water events by drawing water past the intake, therefore increasing water movement and reducing the buffering affect. Hope street sewage infrastructure has been upgraded by QUU. Raw water online turbidity instrument will shut down plant if limits are exceeded.
TKR : Kirkleagh (Recreation) WTP | TBA | Clarification (Incorporating Coagulation, Flocculation & Clarification) | Incorrect soda ash dose | Incorrect pH for coagulation | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Capital upgrade to incorporate UV into the plant
TKR : Kirkleagh (Recreation) WTP | TBA | Clarification (Incorporating Coagulation, Flocculation & Clarification) | Under dosing alum | Underdose of alum - Poor coagulation / flocculation leading contamination of settled water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Capital upgrade to incorporate UV into the plant
TKR : Kirkleagh (Recreation) WTP | TBA | Clarification (Incorporating Coagulation, Flocculation & Clarification) | Over dosing alum | Over dose of alum - Post flocculation occurs leading to suspended solids in the treated water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Capital upgrade to incorporate UV into the plant
TKR : Kirkleagh (Recreation) WTP | TBA | Clarification (Incorporating Coagulation, Flocculation & Clarification) | Flocculator failure | Potential filter break through | Risk Assessment | Medium (8) | Tactical Asset Maintenance | 5 | 2020-06-30 | N | Consideration should be given to the installaton of a paddle stirrer failure alarm if one does not already exist. Flocculation occurs via a single stage mixer that continuously operates in the flocculation chamber to provide mixing and floc formation; and No issues have been observed with regards to the flocculator.
TKR : Kirkleagh (Recreation) WTP | TBA | Clarification (Incorporating Coagulation, Flocculation & Clarification) | Carryover of floc, sludge, algae and/or turbidity in clarified water | This leads to overloading of the filter and probable filter break through | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Process assessment
TKR : Kirkleagh (Recreation) WTP | TBA | Filtration | Filter break- through Turbidities > 0.3 NTU | Filter break-through impacting treated water quality. | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | A review of recent filter turbidity data should be undertaken to assess performance and risk in light of the potential protozoa (Crypto) load in the raw water. Capital upgrade - UV
TKR : Kirkleagh (Recreation) WTP | TBA | Whole of System | Raw water contaminant load exceeds treatment capacity | Hazards that are not adequately managed by the barriers in the process | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Determine the log removal required for baseline and event based pathogen loads into this WTP -Tier 1 study complete showing need 5.5 LRV. Tier 2 study is underway.
TIF : Image Flat WTP | TBA | Raw Water Intake - WAPPA DIRECT | No Other Source | Contamination of Poona (eg with MIB) and a lack of capacity on the south maroochy weir | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Consideration should be given to real-time water quality and flow monitoring of raw water sources. Wappa can directly feed Plant 1 only. Due to extremely elevated MIB in Poona, and a lack of capacity in cooloolabin, Wappa is the only potential water source available that can be used effectively. Process optimisation must occur to treat wappa as it is handled differently by the plant to poona water. Additional protozoa treatment (eg UV)
TNP : North Pine WTP | TBA | pH Correction | underdosing caustic | Low pH if not available when additional alum is used affecting coagulation | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Review monitoring and process interlocks - Failure of the coagulation process is the main issue with failure of the caustic system.
TNP : North Pine WTP | TBA | pH Correction | overdosing of caustic | High pH affecting coagulation | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Review monitoring and process interlocks - Failure of the coagulation process is the main issue with failure of the caustic system.
TNP : North Pine WTP | TBA | Supernatant Return (currently offline) | Increased contaminant load on the treatment plant | Increased in contaminant load potentially resulting in non-compliant treated water | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2019-06-30 | N | The onsite wastewater treatment plant is to be decommissioned and connected to sewer an online turbidity analyser on the supernatant return is required to return the supernatant (after the connection has occurred).
TNP : North Pine WTP | TBA | PAC | Under dosing PAC | PAC is not dosed or under dosed when required | Risk Assessment | Medium (9) | Process Engineering | 6 | 2019-06-30 | N | Investigate alternative treatments for T & O
TNP : North Pine WTP | TBA | Coagulation | Over dosing alum | Non-optimal coagulation resulting in filter break-through | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Review alarming and interlocks.
TNP : North Pine WTP | TBA | Coagulation | Under dosing alum | Non-optimal coagulation resulting in filter break-through | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Review alarming and interlocks.
TNP : North Pine WTP | TBA | Filtration | Filter break- through | Turbidities > 0.3 NTU | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | - Review alarming and interlocks.
TNP : North Pine WTP | TBA | Disinfection | Insufficient Ct - Incorrect pH - Under dose chlorine - Insufficient detention time | Failure to eliminate chlorine sensitive contaminants | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Review alarming and interlocks. Real time / dynamic ct
TLS : Landers Shute WTP | TBA | Raw Water Intake | Intake of contaminated raw water during a wet weather event (seasonal) | Contaminant load exceeds treatment capacity | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Confirm HBT assessment
TKE : Kenilworth WTP | TBA | Whole of system | Raw water contaminant load exceeds treatment capacity | Hazards that are not adequately managed by the barriers in the process | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Investigate long term planning options to improve: (1) raw water intake during flood events given the rapid flow of raw water through the shortened sand bed during flood events; (2) ensuring adequate disinfection for the log-removal of pathogens required at this site. - Category 4 source (requires 6, 6, 5.5 LRV)
TNO : Noosa WTP | TBA | Raw Water Intake (Mary River) | Intake of contaminated raw water during a wet weather event (seasonal) | Contaminant load exceeds treatment capacity | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Confirm HBT assessment Once the river rises about 1 metre it is necessary to change to Lake Macdonald - stays offline until water level drops and screen can be cleared - then pump out intake well with sand pumps. Raw water pumps turn off when Mary River rises approx 1 metre so WTP is not drawing water when the turbidity would be the highest.
TNO : Noosa WTP | TBA | Coagulation | Overdose lime | Non-optimised coagulation | Risk Assessment | Medium (8) | Process Engineering | 6 | 2020-06-30 | N | Investigate lime and alum control with focus on start up and lake only water - link to existing Noosa project improvements project Includine reactivator importance in coag pH validation and control
TNO : Noosa WTP | TBA | Coagulation | Underdosing lime | Non-optimised coagulation | Risk Assessment | Medium (8) | Process Engineering | 6 | 2020-06-30 | N | Investigate lime and alum control with focus on start up and lake only water - link to existing Noosa project improvements project Includine reactivator importance in coag pH validation and control
TNO : Noosa WTP | NOO4 | Filtration | Filter break-through >0.3 NTU | Potential contamination of treated water | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Install appropriate instrumentation, monitoring and control systems to enable effective monitoring and control of filtration. Normally backwash filters on time. Have been some issues with filter ripening after a backwash. Filter aid has been off for 2 years. Is only there to stop turbidity breakthrough if carryover from clarifiers.
TNO : Noosa WTP | NOO3 | Disinfection | Low daily production rates leading to a reduction on pathogen removal efficacy |  | Risk Assessment | Medium (8) | Operations - Supply | 8 | 2019-06-30 | N | The effiacy of flocculation time and mixing energy should be assessed, along with what effects intermittent operation may have when running at very low daily production rates.
TNO : Noosa WTP | NOO12 | Disinfection | Vermin proofing of all plant processes | Bird and animal droppings contaminating the treated water. | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Investigate vermin proofing at Noosa WTP and install appropriate vermin control measures. Vermin proof needs to be investigated on other parts of the plant beside the treated water reservoir.
TNO : Noosa WTP | NOO14 | Disinfection | Insufficient pathogen log removal | Insufficient removal of baseline pathogen load across the whole process | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Identify optimal treatment processes to achieve adequate pathogen treatment.
TEM : Ewen Maddock WTP | EWM4 EWM5 | Intermediate Ozone / BAC | Contamination of BAC from external sources | Introduction of pathogens | Risk Assessment | Medium (8) | Operations - Supply | 8 | 2019-06-30 | N | - Erect contamination signage on/at the BAC filters. - Investigate covering the BAC filters. There is a risk of debris from shoes etc entering the BACs due to the overhead walkways. This has the potential to introduce pathogens after the primary barrier.

## Central
Drinking Water Quality Improvement Plan - Central Region
Site | Improvement # | Process Step | Issue | Description | Origin of Improvement | Significant Risk | Responsibility | Responsibility assignment code | Due for completion | Completed? Y/N | Risk Treatment Comments
Supply System | TBA | Treated Water | Elevated conductivity leaving WTP | Treated water with high conductivity leaving the WTPs leading to elevated disinfection Byproducts in the treated water. | Risk Assessment | Medium (9) | Water Quality Unit | 10 | 2019-06-30 | N | Refer to individual WTPs individual risk treatments to reduce this risk.
Supply System | SSM10 | Reservoir | Contamination of reservoirs by ingress | Rainwater, vermin, dust etc entering reservoirs leading to out of specification treated water. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Reservoir Inspection Program is to be rolled out to all Supply System Reservoirs.
Supply System | SSM13 | Disinfection (secondary) | Breakpoint chlorination | Formation of DBP due to naturally occurring precursors leading to out of specification treated water. | Risk Assessment | Medium (9) | Asset Planning | 2 | 2022-06-30 | N | Roll out of the Secondary Disinfection project actions. Implementation planned in stages between 2019 and 2025.
Supply System | SSM12 | Disinfection (secondary) | Release of free ammonia (subsequent conversion to nitrite and/or nitrate) | Caused by systems complexity, water age and temperature leading to out of specification treated water. | Risk Assessment | Medium (9) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Online ammonia instruments to be installed at Nth Pine, Camerons Hill and key Supply System sites.
TEB : Mount Crosby East Bank WTP | 'EBK22 EBK23 | Raw Water Abstraction | Elevated Raw Water Conductivity | Inflows of salty and hard water via creeks downstream of Wivenhoe Dam (problem is exacerbated if a localised storm event occurs in a problem catchment i.e. Lockyer Creek) | Risk Assessment | Medium (9) | Water Quality Unit | 10 | 2019-06-30 | N | - Options to install conductivity meters at the outlets of the Camerons Hill No. 1 & 2 Reservoirs linked back to SCADA should be investigated. - Additional training should be given to Operations Staff with respect to the online visibility now available in regards to the Catchment Groups remote monitoring stations (i.e. at Lockyer and Blacksnake Creeks) and BOM creek and river gauging stations.
TEB : Mount Crosby East Bank WTP | EBK112 EBK113 | Raw Water Abstraction | Dirty water event in the catchment (i.e. storm, flood, gravel extraction, land slide etc.) | Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | '- Undertake HBT Assessment for this site; - Long term planning is underway for this WTP.
TEB : Mount Crosby East Bank WTP | EBK32 EBK33 | Coagulation | Incorrect Sodium Hydroxide dose | Underdosing of Sodium Hydroxide resulting in coagulation process failure. | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | - There is currently a project in place to install new raw water flow meters to service the inlets to Sedimentation Basins No. 1 and 2 which will result in more reliable flow pacing for caustic soda - Basin 1 is complete, and Basin 2 is to be complete by the end of June 16; completed - Project approval is also being sought to install new raw water flow meters to service the inlets to Sedimentation Basins No. 3 and 4 which will result in more reliable flow pacing for caustic soda into these basins as well - Basin 3 and 4 is to be complete by the end of June 16.
TEB : Mount Crosby East Bank WTP | EBK32 EBK33 | Coagulation | Incorrect Sodium Hydroxide dose | Overdosing of Sodium Hydroxide resulting in coagulation process failure. | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | - There is currently a project in place to install new raw water flow meters to service the inlets to Sedimentation Basins No. 1 and 2 which will result in more reliable flow pacing for caustic soda - Basin 1 is complete, and Basin 2 is to be complete by the end of June 16; completed - Project approval is also being sought to install new raw water flow meters to service the inlets to Sedimentation Basins No. 3 and 4 which will result in more reliable flow pacing for caustic soda into these basins as well - Basin 3 and 4 is to be complete by the end of June 16.
TEB : Mount Crosby East Bank WTP | EBK37 EBK38 | Coagulation | Incorrect Alum dose | Overdose of Alum resulting in ineffective coagulation | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | - As per the recommendations of an ICAM report, ie Interlocking ; - Updates to CCP procedures and validation standard as per project
TEB : Mount Crosby East Bank WTP | EBK40 | Coagulation | Flash mixer failure | Ineffective coagulation, flocculation and sedimentation, filter breakthrough and out of specification treated water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | - Installation of jet flash mixers for Sedimentation Basins No. 3 and 4. - Flow meter upgrade for Sed basins 3 and 4.
TEB : Mount Crosby East Bank WTP | EBK45 | Flocculation and Settling | Flocculator Failure | Ineffective flocculation and sedimentation, filter breakthrough and out of specification treated water. | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | - There is currently an options analysis being undertaken looking at what works would be required to improve flocculation associated with Sedimentation Basin No. 1 - Options analysis underway. Currently sitting with planning.
TEB : Mount Crosby East Bank WTP | TBA | Flocculation and Settling | Carryover of floc, sludge, algae and/or turbidity in settled water | Carry over on to the filters and possible filter break through. | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Process assessment
TEB : Mount Crosby East Bank WTP | EBK49 | Flocculation and Settling | Failure or incorrect operation of a bypass valve around sedimetation basins | Leading to out of specification treated water | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | - Identify bypasses and reveiw lockout arrangements so that these bypass valves cannot be accidentally opened, prior to them being blanked off - Plates welded over spindles
TEB : Mount Crosby East Bank WTP | EBK115 | Media Fitration | Incorrect Polymer Dose | Under dose of Polymer resulting in reduced filter performance | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | - Improve monitoring and control of the filter aid dosing system.
TEB : Mount Crosby East Bank WTP | EBK56 | Media Fitration | Filter breakthrough | Potential contamination of treated water | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | - Eastbank filter upgrade project to start in 2019.
TEB : Mount Crosby East Bank WTP | EBK62 EBK114 | Media Fitration | Contamination of filtered water cells by ingress | Introduction of pathogens | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | - The location and integrity of the vermin proofing (i.e. frog flaps) associated with the overflow pipes from these cells should be checked as a matter of priority. - Mesh breathers for the filtered water cells needs to be replaced.
TEB : Mount Crosby East Bank WTP | EBK80 | Disinfection (primary) | Contamination of Camerons Hill Reservoirs by ingress | Out of specification treated water | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Improvement to vermin proofing need to be made to CH1 and CH2
TEB : Mount Crosby East Bank WTP | EBK85 EBK91 | Disinfection (secondary) | Insufficient mixing | Out of specification treated water | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | - There is currently a project to install a mixer to improve mixing. One Monochloramine and free ammonia analyser to be installed 2 sample lines - 1 for CH1 and 1 for CH .- 90% Design.
TLO : Lowood WTP | LOW67 | Raw Water Abstraction | Dirty water event in the catchment (i.e. storm, flood, gravel extraction, land slide etc.) | Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control. Complete Stage 1 and 2 Plant Upgrade works at Lowood WTP. June 2019 for Stage 1. June 2021 for Stage 2.
TLO : Lowood WTP | LOW67 LOW25 | Supernatant Return | Loading exceeds plant capability | Supernatant return volumes exceed treatment capacity leading to out of specification treated water | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control. Complete Stage 1 and 2 Plant Upgrade works at Lowood WTP. June 2019 for Stage 1. June 2021 for Stage 2. Consideration should be given to undertaking a mass balance of acrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for this compound in the treated water. Carried out for stage 2. Completed. study completed inplementation delayed.
TLO : Lowood WTP | LOW67 LOW9 | Coagulation | Incorrect Lime dose | Underdose of Lime resulting in coagulation process failure | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control. Identify improvements for the lime system to make it more reiliable.
TLO : Lowood WTP | LOW67 LOW9 | Coagulation | Incorrect Lime dose | Overdose of Lime resulting in coagulation process failure | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control. Identify improvements for the lime system to make it more reiliable.
TLO : Lowood WTP | LOW67 | Coagulation | Incorrect Alum dose | Underdose of Alum resulting in ineffective coagulation | Risk Assessment | High (12) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control.
TLO : Lowood WTP | LOW67 | Coagulation | Incorrect Alum dose | Overdose of Alum resulting in ineffective coagulation | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control.
TLO : Lowood WTP | LOW10 | Coagulation | Loss of Carrier Water | Ineffective coagulation | Risk Assessment | High (12) | Process Engineering | 6 | 2019-06-30 | N | Identify monitoring options for carrier water.
TLO : Lowood WTP | LOW25 | Flocculation and Settling | Incorrect Polymer Dose | Underdose of Polymer resulting in ineffective coagulation, flocculation and settling, leading to filter breakthrough and out of specification treated water. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Consideration should be given to undertaking a calculation of acrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for this compound in the treated water.
TLO : Lowood WTP | LOW67 | Flocculation and Settling | Flocculator failure | Ineffective flocculation and clarification, filter breakthrough and out of specification treated water. | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control.
TLO : Lowood WTP | LOW67 | Flocculation and Settling | Carryover of floc, sludge, algae and/or turbidity in clarified water | Due to one or more of the following scenarios, leading to out of specification treated water: - Flow rate changes; - Poor flash mixing; - Flocculator failure; - Floc shearing; - Poor sludge management; - Boil up (temp changes); and - Algae bloom in clarifier. | Risk Assessment | High (12) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control.
TLO : Lowood WTP | LOW67 | Media Fitration | Filter breakthrough | Leading to out of specification treated water. | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control.
TLO : Lowood WTP | LOW67 LOW9 | Disinfection (primary) | Incorrect lime dose | Under dosing lime leading to out of specification treated water. | Risk Assessment | Medium (9) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Any upgrade of the control system associated with this WTP should include interlocks that will automatically shutdown the relevant parts of the WTP in the advent of a critical limit being triggered (i.e. raw water turbidity) - 30% of design has been submitted. Switch board upgrade to include alarms if floculator fails and back up power generator or ensure continuity of operations and control. Identify improvements for the lime system to make it more reiliable.
TWB : Mount Crosby West Bank WTP | 'EBK22 EBK23 | Raw Water Abstraction | Elevated Raw Water Conductivity | Inflows of salty and hard water via creeks downstream of Wivenhoe Dam (problem is exacerbated if a localised storm event occurs in a problem catchment i.e. Lockyer Creek) | Risk Assessment | Medium (9) | Process Engineering | 6 | 2020-06-30 | N | - Options to install conductivity meters at the outlets of the Camerons Hill No. 1 & 2 Reservoirs linked back to SCADA should be investigated - extension date to 1/7/2016; and - Y1403 Additional training should be given to Operations Staff with respect to the online visibility now available in regards to the Catchment Groups remote monitoring stations (i.e. at Lockyer and Blacksnake Creeks) and BOM creek and river gauging stations.
TWB : Mount Crosby West Bank WTP | EBK112 EBK113 | Raw Water Abstraction | Dirty water event in the catchment (i.e. storm, flood, gravel extraction, land slide etc.) | Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | '- Undertake HBT Assessment for this site; - Long term planning is underway for this WTP.
TWB : Mount Crosby West Bank WTP | WBK80 | Disinfection (primary) | Contamination of service water distribution system due to main break or backflow incident. | Potential contamination of treated water | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | - Conduct audit of the the service water to ensure that there are adequate measures in place sto stop backflow events.
TWB : Mount Crosby West Bank WTP | WBK63 | Whole of System | Failure or incorrect operation of a bypass valve | Leading to out of specification treated water. | Risk Assessment | Medium (8) | Operations - Supply | 8 | 2019-06-30 | N | Consider reviewing lockout arrangements so that these bypass valves cannot be accidentally opened, prior to them being blanked off - Plates welded over spindles -
TWB : Mount Crosby West Bank WTP | WB110 | Whole of System | Backflow prevention failure | Leading to out of specification treated water. | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Full audit needs to be undertaken on backflow prevention at Westbank.
TWR : Wivenhoe Dam (Recreation) WTP | WIV75 WIV100 | Coagulation | Incorrect Alum dose | Underdose of Alum resulting in ineffective coagulation | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Package plant to replace the existing plant between the raw water tanks and the clear water storage. Expected to be completed Dec 2018. Check to see if coag pH instrument and alum flow meter is included in this package. If not organise installation of these instruments.
TWR : Wivenhoe Dam (Recreation) WTP | WIV75 | Flocculation and Settling | Carryover of floc, sludge, algae and/or turbidity in clarified water | The following leading to out of specification treated water. - Flow rate changes; - Poor flash mixing; static - Poor sludge management; - Boil up (temp changes); and - Algae bloom in clarifier. | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Package plant to replace the existing plant between the raw water tanks and the clear water storage. Expected to be completed Dec 2018.
TWR : Wivenhoe Dam (Recreation) WTP | WIV75 WIV102 WIV103 | Media Filtration | Filter breakthrough | Leading to out of specification treated water. | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Package plant to replace the existing plant between the raw water tanks and the clear water storage. Expected to be completed Dec 2018. Consideration should be given to ascertaining if it would be practical to installed a first filtered water to waste system, and undertake necessary works if this idea was deamed to be advantageous; Any upgrade of the control system associated with this WTP should retain interlocks that will automatically shutdown the relevent parts of the WTP in the advent of a critical limit being triggered (i.e. filtered water turbidity).
TWR : Wivenhoe Dam (Recreation) WTP | WIV75 WIV100 WIV103 WIV104 | Disinfection (primary) | Insufficient C.t | Insufficient C.t resulting from: - Inadequate t10; - Low free chlorine residual; - High pH; and - Low temperature. | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Package plant to replace the existing plant between the raw water tanks and the clear water storage. Also including: Looking at the online analyser requirements for this WTP (i.e. for the primary disinfection step - dosed filtered water free chlorine, pH and temperature, and treated water free chlorine and pH); Ascertain if a standby (or cold standby) sodium hypochlorite dosing pump has been procurred for this WTP and if not, consider purchasing spare; Any upgrade of the control system associated with this WTP should include for primary disinfection, single point of failure alarms (i.e. for free chlorine, temperature, pH, flow rate and reservoir level) and be complemented by an automated real time chlorine C.t calculator with its own operational and HACCP alarm setpoints. Such an upgrade should also incorporate where applicable, interlocks that will shutdown the relevent parts of the WTP in the advent of a critical limit being triggered. Investigate options for increasing C.t at this WTP.
TWR : Wivenhoe Dam (Recreation) WTP | WIV 75 WIV17 | Whole of System | Loss of SCADA and/or communications system | Leading to loss of supply and/or out of specification treated water. | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Package plant to replace the existing plant between the raw water tanks and the clear water storage. Jacobs report (October 2015) recommends that Wivenhoe Dam WTP to proceed to preliminary design in the second phase of this project, including: Upgrading the control system.

## South
Drinking Water Quality Improvement Plan - Southern Region
Site | Improvement # | Process Step | Issue | Description | Origin of Improvement | Significant Risk | Responsibility | Responsibility assignment code | Due for completion | Completed? Y/N | Risk Treatment Comments
THZ : Hinze Dam WTP | TMO-17 | Raw Water Abstraction | Rain event in catchment | Intake of increased treatment load that could potentially result in contaminated treated water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category for Hinze Dam. Treatement capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. Risk Treatment Reference is as per Molendinar WTP Risk Treatment Reference. Acknowledge that BoH tank is not filled when raw water quality at lower intake is undesirable. Assessment carried out for Molendinar WTP should incorporate Hinze Dam WTP. Refer Molendinar WTP Risk Improvement Item
THZ : Hinze Dam WTP | HNZ-5 | Coagulation | Incorrect coagulant dose | Underdose of ACH resulting in contaminated treated water | Risk Assessment | Medium (8) | Process Engineering | 6 | 2020-06-30 | N | HNZ5: Risk Treatment (raised R.A review 2015): Although this is not known to have occurred at Hinze Dam WTP there is occurrences of coag dosing pipe breakages at other WTPs. There is currently a coagulant flow switch interlocked to WTP operation however coag flow monitoring interlocked to WTP operation is required. Update R.A review 2017: Confirmed as viable WTP and will continue operating. Project will be pursued by Process Improvement Specialists based on current understanding that WTP will remain for the foreseeable future. To be included in Minor Works upgrade 17/18. Note Control System is very limited in terms of adding any further alarms or monitoring. Sludge upgrade project would trigger upgrade of PLC.
TKO : Kooralbyn WTP | TKO-14 | Raw Water Abstraction | Cyanobacteria Bloom | In take of algae or toxins that has an impact on plant operations or water quality from Bigfoot Lagoon | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Risk Treatment (raised in Bigfoot Lagoon Risk Assessment workshop Feb 2017): PAC dosing required when using Bigfoot Lagoon if raw water T&O > acceptable levels. Update R.A 2017: Bigfoot Lagoon PAC system being restored to operational however no operational experience at time of R.A. At time of R.A project already in delivery in 17/18 PD Program PID02682 AIC: Mobile Powder Activated Carbon Units. Dosing point location proposed to be at WTP. Effectivess of PAC with short contact time yet to be demonstrated. Operational availability and reliability to be determined.
TKO : Kooralbyn WTP | TKO-15 TKO-16 | Raw Water Abstraction | Rain event in catchment | Intake of contaminated water that could potentially result in contaminated treated water | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Risk Treatment (raised Kooralbyn WTP - pathogen treatment assessment report June 2015 - documented R.A 201): Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19. Risk Treatment (raised in Bigfoot Lagoon Risk Assessment workshop Feb 2017): Future Control Mitigators and Strategies were identified in the workshop in Feb 2017 to reduce risks associated with running on Bigfoot Lagoon water to acceptable levels including installation of CO2. At time of R.A a project was already in delivery in 17/18 PD program PID02682 AIC: Mobile Powder Activated Carbon Units. Dosing point location proposed to be at WTP.
TKO : Kooralbyn WTP | TKO-17 TKO-18 TKO-15 | Coagulation | Incorrect coagulant dose | Underdose of alum resulting in contaminated treated water including incorrect dosed water pH | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Risk Treatment (raised R.A 2017): The primary signal to detect underdose of coagulant is the coagulant flow meter. Second to this is the dosed water pH meter which is critical to monitor coagulation is occurring within the effective pH range and, for Kooralbyn WTP, provides feedback for the caustic dose rate control. Flow to the dosed water instrument is under gravity and blockages of the dosed water sample line have been reported. A flow switch was installed to detect loss of flow to the instrument and subsequently interlock the WTP due to a loss of CCP monitoring and loss of feedback signal to the caustic dosing system. This was caused by longer sample pipe and flocs in sample water block the pipe. The rotameter float was scaled by metal particles and gets stuck in side the rotameter preventing no flow signal alarm dial out. The impact is reduction in reliability of the coagulation process (a critical control point). Improvement Opportunity (raised R.A 2017): Kooralbyn does not have any capability for timely and online measurement of changes in raw water quality for adequate pH correction that is needed for a reliable coagulation process. The Operator's work around to this issue is to start and stop the caustic dosing system in order to detect changes in raw water pH. The operator also uses coagulated pH as a lagging indicator of changes to raw water pH. This workarounds is only temporary and does not sufficiantly address the risk because of the number of variables and factors that could influence the pH of the process. Risk Treatment (raised APDD WQ Report Kooralbyn WTP - pathgoen treatment assessment report June 2015): Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19.
TKO : Kooralbyn WTP | TKO-17 TKO-18 TKO-15 | Coagulation | Incorrect coagulant dose | Overdose of alum resulting in contaminated treated water including underdose of caustic | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Risk Treatment (raised R.A 2017): The primary signal to detect underdose of coagulant is the coagulant flow meter. Second to this is the dosed water pH meter which is critical to monitor coagulation is occurring within the effective pH range and, for Kooralbyn WTP, provides feedback for the caustic dose rate control. Flow to the dosed water instrument is under gravity and blockages of the dosed water sample line have been reported. A flow switch was installed to detect loss of flow to the instrument and subsequently interlock the WTP due to a loss of CCP monitoring and loss of feedback signal to the caustic dosing system. This was caused by longer sample pipe and flocs in sample water block the pipe. The rotameter float was scaled by metal particles and gets stuck in side the rotameter preventing no flow signal alarm dial out. The impact is reduction in reliability of the coagulation process (a critical control point). Improvement Opportunity (raised R.A 2017): Kooralbyn does not have any capability for timely and online measurement of changes in raw water quality for adequate pH correction that is needed for a reliable coagulation process. The Operator's work around to this issue is to start and stop the caustic dosing system in order to detect changes in raw water pH. The operator also uses coagulated pH as a lagging indicator of changes to raw water pH. This workarounds is only temporary and does not sufficiantly address the risk because of the number of variables and factors that could influence the pH of the process. Risk Treatment (raised APDD WQ Report Kooralbyn WTP - pathgoen treatment assessment report June 2015): Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19.
TKO : Kooralbyn WTP | TKO-17 TKO-18 TKO-15 | Coagulation | Incorrect caustic soda dose | Overdose of caustic soda causing high dosed water pH resulting in contamination of treated water | Risk Assessment | Medium (8) | Process Engineering | 6 | 2020-06-30 | N | Risk Treatment (raised R.A 2017): The primary signal to detect underdose of coagulant is the coagulant flow meter. Second to this is the dosed water pH meter which is critical to monitor coagulation is occurring within the effective pH range and, for Kooralbyn WTP, provides feedback for the caustic dose rate control. Flow to the dosed water instrument is under gravity and blockages of the dosed water sample line have been reported. A flow switch was installed to detect loss of flow to the instrument and subsequently interlock the WTP due to a loss of CCP monitoring and loss of feedback signal to the caustic dosing system. This was caused by longer sample pipe and flocs in sample water block the pipe. The rotameter float was scaled by metal particles and gets stuck in side the rotameter preventing no flow signal alarm dial out. The impact is reduction in reliability of the coagulation process (a critical control point). Improvement Opportunity (raised R.A 2017): Kooralbyn does not have any capability for timely and online measurement of changes in raw water quality for adequate pH correction that is needed for a reliable coagulation process. The Operator's work around to this issue is to start and stop the caustic dosing system in order to detect changes in raw water pH. The operator also uses coagulated pH as a lagging indicator of changes to raw water pH. This workarounds is only temporary and does not sufficiantly address the risk because of the number of variables and factors that could influence the pH of the process. Risk Treatment (raised APDD WQ Report Kooralbyn WTP - pathgoen treatment assessment report June 2015): Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19.
TKO : Kooralbyn WTP | TKO-16 TKO-15 | Coagulation | Incorrect CO2 dose | Note: CO2 injection point available however system is not integrated into SCADA Underdose (absence) of CO2 causing high dosed water pH resulting in contamination of treated water | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Risk Treatment (raised in Bigfoot Lagoon Risk Assessment workshop Feb 2017): Future Control Mitigators and Strategies were identified in the workshop in Feb 2017 to reduce risks associated with running on Bigfoot Lagoon water to acceptable levels including installation of CO2. At time of R.A a project was already in delivery in 17/18 PD program PID02682 AIC: Mobile Powder Activated Carbon Units. Dosing point location proposed to be at WTP. Risk Treatment (raised APDD WQ Report Kooralbyn WTP - pathgoen treatment assessment report June 2015): Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19.
TKO : Kooralbyn WTP | TKO-15 | Flocculation and Settling | Carry over of floc, sludge or algae in settled water | Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed | Risk Assessment | Medium (8) | Asset Planning | 2 | 2020-06-30 | N | Risk Treatment (raised APDD WQ Report Kooralbyn WTP - pathgoen treatment assessment report June 2015): Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146 Update R.A 2017: Proposal with WTP Planning to write BC. Not in PD program for delivery 17/18. Expected 18/19.
TKO : Kooralbyn WTP | TKO-18 TKO-15 | Flocculation and Settling | Failure or incorrect operation of a bypass valve | Failure or incorrect operation of a clarifier bypass valve | Risk Assessment | Medium (8) | Operations - Supply | 8 | 2019-06-30 | N | Improvement Opportunity (raised R.A review 2017): Tag out bypass to ensure clear identification of valve and prevent accidental use. Refer KOO-TBA for Protozoa reduction Risk Treatment item.
TKO : Kooralbyn WTP | TKO-15 | Media Filtration | Filter breakthrough | Fitler breakthrough | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Refer to KOO-TBA for protozoa log reduction risk treatment
TKO : Kooralbyn WTP | KOO13 | Media Filtration | Contamination by animals | Contamination of filtered water tank | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Risk Treatment (raised R.A review 2015): Filtered water tank and treated water tank does not meet standards to prevent ingress/contamination. Update R.A 2017: TKO: Replace filter roofs was in 16/17 PD program and is carrying over into 17/18 to address appropriately designed filter roof access hatch.
TKO : Kooralbyn WTP | KOO13 | Disinfection (primary) | Contamination by animals | Contamination of treated water tank | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Risk Treatment (raised R.A 2017): There are known gaps around treated water pump assets on reservoir roof. Short term gaps need to be addressed. Long terms PID01709 - TKO: Reservoir roof replacement project in 17/18 PD program.
TRA : Rathdowney WTP | TRA-30 | Raw Water Abstraction | Rain event in catchment | Intake of contaminated water that could potentially result in contaminated treated water | Risk Assessment | Medium (8) | Asset Planning | 2 | 2020-06-30 | N | Risk Treatment (raised Rathdowney WTP – pathogen treatment assessment - documented R.A 2017): Refer D15/114408. Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital plannig register.
TRA : Rathdowney WTP | TRA-30 RAD 23 | Supernatant Return | Superntant return quality exceeds treatment capacity | Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose | Risk Assessment | Medium (8) | Process Engineering | 6 | 2020-06-30 | N | Risk Treatment (raised Rathdowney WTP – pathogen treatment assessment - documented R.A 2017): Refer D15/114408. Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital plannig register. Improvement Opportunity (raised R.A review 2017): Supernatant return flow rate maximum is designed to be controlled by SCADA to not exceed 10% of raw water flow. At the time of conducting the R.A review the automation was not enabled and supernatant return flow rate was manually throttled by Operators. Observation is that automation works when WTP running at 5L/s but struggles at current rate of 4 L/s. Process Engineer to investigate improvements to automation control. In addition a return rate of <5 % of the raw water flow is recommended by the AWWA, Water Treatment Alliance and the WaterRA report 1079 Good Practice Guide to the Operation of Drinking Water Supply Systems for the Management of Microbial Risk 2015. Opportunities to meet this requirement using current assets should be investigated with a view to making recommendations for future upgrades if required to meet this target.
TRA : Rathdowney WTP | RAD 18 ALL16 | Coagulation | Incorrect coagulant dose | Underdose of Magnasol 589 including loss of carrier water Or Ineffective coagulation due to elevated pH | Risk Assessment | High (12) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Risk Treatment (raised R.A review 2015): Install a flow meter on the magnasol dosing line with interlocks and pump fault alarms. Update R.A review 2017: Coagulant (589) flow monitoring was installed in Sep 2015 and integrated into SCADA including alarming and WTP interlock functionality. A time of R.A review 2017 the flow trend was assessed as being not reliable for alarming therefore risk remains significant. Risk Treatment (raised R.A review 2017): Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital plannig register.
TRA : Rathdowney WTP | ALL16 | Coagulation | Incorrect coagulant dose | Overdose of Magnasol 589 | Risk Assessment | Medium (8) | Asset Planning | 2 | 2020-06-30 | N | Risk Treatment (raised R.A review 2017): Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital plannig register.
TRA : Rathdowney WTP | ALL16 RAD 24 | Flocculation and Settling | Carry over of floc, sludge or algae in settled water | Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed | Risk Assessment | Medium (8) | Asset Planning | 2 | 2020-06-30 | N | Risk Treatment (raised R.A review 2017): Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital plannig register. Improvement Opportunity (raised R.A review 2017): SCADA and dial out alarming on flocculator failure/fault to be enabled.
TRA : Rathdowney WTP | ALL16 RAD 26 | Media Filtration | Filter breakthrough | Fitler breakthrough | Risk Assessment | Medium (8) | Asset Planning | 2 | 2020-06-30 | N | Risk Treatment (raised R.A review 2017): Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital plannig register. Improvement Opportunity (raised R.A review 2017): Develop an oPRP for filter media inspections
TRA : Rathdowney WTP | ALL16 RAD 27 | Media Filtration | Build up of solids leading to elevated turbidity | High turbidity filtered water from backwash water tank used to backwash filter leading to filter breakthrough when filter back online | Risk Assessment | Medium (8) | Asset Planning | 2 | 2020-06-30 | N | Risk Treatment (raised R.A review 2017): Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Project to commence 17/18. Refer APMP 2017 capital plannig register. Improvement Opportunity (raised R.A review 2017): implement monitoring/inspections of filtered water tank sludge and/or filtered water tank turbidity to detect sludge build up. Including corrective actions.
TBK : Boonah-Kalbar WTP | TBK-9 | Supernatant Return | Superntant return quality exceeds treatment capacity | Intake of supernatant return water that exceeds the treatment capacity of the plant including: - T&O in sludge lagoon impacting treated water T&O - overland flow from surrounding roadside and adjacent farms - rate of return >10% - inadequate poly dose (AN905) into sludge thickener - release of manganese due to low pH and failure to initiate caustic dosing | Risk Assessment | Medium (8) | Asset Planning | 2 | 2020-06-30 | N | Improvement Opportunity (raised INIR-3886: Supernatant Return CCP (DWQMP Regulator Audit Finding 2016): Supernatant return pumps are fixed flow rate and oversized and the automatic valve can not modulate the flow rate to 10%. Pump is faulted by flow rate control valve installed as part of upgrades in 2015. Supernatant return rate at time of audit was >10%. Operations Team has manually throttled pumps as interime operational work around but need to be vigilant when raw water flows drop that supernatant return rate is not >10%. Update at R.A 2017: VFDS not in R&R program for 18/19. Not in PD program for 17/18. WTP Planning are commencing project planning on the sludge system this financial year 17/18. Process Engineers has submitted APIN to WTP Planning July 2017 for VFDs for supernatant pumps at Kalbar WTP 13/07/17. WTP Planning process should also consider formation of T&O in sludge lagoons. Further improvements required to address other operational inefficiencies including the cost of de-sludging lagoons annually.
TBK : Boonah-Kalbar WTP | TBK-17 | Disinfection (primary) | Contamination by animals | Contamination of treated water tank | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Risk Treatment raised (raised Audit 2017): Vermin proofing of reservoir required. Update R.A review 2017: Emergent works request sumbitted and in EW register.
TMD : Maroon Dam WTP | TMD-18 | Raw Water Abstraction | Rain event in catchment | Intake of contaminated water that could potentially result in contaminated treated water | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised 2017): HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP likely to required additional protoza removal (i.e UV).
TMD : Maroon Dam WTP | TMD-18 MAR9 MAR8 | Coagulation | Incorrect coagulant dose | Underdose of alum including inadequate mixing | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised 2017): HBT Pathogen Assessment is required for this WTP. If WTP cannot achieve log reduction target for Cat 4 then additional barrier will be required (i.e UV disinfection). Likelihood can only be reduced to Rare when UV installed. Improvement Opportunity (raised 2015): Recommend conditionally formatting plantdata spreadsheet to prevent excursions being missed. Risk Treatment (raised 2015): Lack of alum flow monitorinng is an unacceptable risk due to periods of low RW pH. Alum flow monitoring required (and injection point flow switch or meter if carrier water used) with interlocks to shutdown the WTP. Raw water pH 5th%iles are <7.5 pH which is the validated SPV upper crtiical limit for dosed water pH using alum. Therefore during a rain event when RW pH is low (5% of the time) if alum dosing was lost this would not trigger the upper crtical limit of pH 7.5. In the short term a low dosed water pH limit will be used which should detect alum dosing failure in most circumstances. Update (R.A 2017): Investigate installation of flow switch to detect loss of alum dose.
TMD : Maroon Dam WTP | TMD-18 MAR9 | Coagulation | Incorrect coagulant dose | Overdose of alum leading to ineffective coagulation affecting treated water quality | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised 2017): HBT Pathogen Assessment is required for this WTP. If WTP cannot achieve log reduction target for Cat 4 then additional barrier will be required (i.e UV disinfection). Likelihood can only be reduced to Rare when UV installed. Improvement Opportunity (raised 2015): Recommend conditionally formatting plantdata spreadsheet to prevent excursions being missed.
TMD : Maroon Dam WTP | TMD-19 TMD-18 | Flocculation and Settling | Carry over of floc, sludge or algae in settled water | Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Improvement Opportunity (raised R.A review 2017): autodesludge on start up would be an operational improvement for this site. Risk Treatment (raised R.A review 2017): HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP likely to require additional protoza removal (i.e UV).
TMD : Maroon Dam WTP | TMD-23 | Disinfection (primary) | Contamination by animals | Contamination of treated water tank | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised R.A 2017): Undertake reservoir inspection in accordance with Seqwater standard.
TMD : Maroon Dam WTP | MAR15 MAR9 | Distribution Pipeline | Elevated water age | Presence of pathogenic bacteria resulting from loss of secondary disnfection barrier | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Improvement Opportunity (raised R.A review 2015): Chlorine residuals in distrubution system need to be improved. HACCP action limit for <0.2 mg/L already in place however not being reported against. Update R.A review 2017: D17/37461 PID02858 - DMA - Maroon Dam - Upgrade Treated Water Reticulation System - Business Case in delivery in 17/18. Improvement Opportunity (raised R.A review 2015): Conditionally format plantdata spreadsheet.
TMD : Maroon Dam WTP | TMD-25 | Distribution Pipeline | Build up of solids leading to elevated turbidity | Turbidity in distribution system. Causes include: - continuos build up over time due to aging assets - change in flow conditions disturbing biofilms | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | D17/37461 PID02858 - DMA - Maroon Dam - Upgrade Treated Water Reticulation System - Business Case in delivery in 17/18. Improvement Opportunity (raised R.A review 2017): determine long term maintenance requirements of system to mitigate build up of turbidity and sediments over time.
TMD : Maroon Dam WTP | MAR6 | Distribution Pipeline | Contamination due to pipe break | Ingress of contaminants leading to contamination of treated water | Risk Assessment | Medium (8) | Project Delivery | 4 | 2019-06-30 | N | Improvement Opportunity (raised R.A review 2015): Assessment of condition of network required to determine need for replacement/renewal of mains as breaks occur every 6-12 months. Update R.A review 2017: under DMA: Maroon Dam – Upgrade the Treated Water Reticulation System in delivery for 17/18
TMG : Moogerah Dam WTP | TMG-15 | Raw Water Abstraction | Rain event in catchment | Intake of contaminated water that could potentially result in contaminated treated water | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised R.A 2017): HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP likely to required additional protoza removal (i.e UV).
TMG : Moogerah Dam WTP | TMG-15 MOO5 | Coagulation | Incorrect coagulant dose | Underdose of alum including inadequate mixing | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised 2017): HBT Pathogen Assessment is required for this WTP. If WTP cannot achieve log reduction target for Cat 4 then additional barrier will be required (i.e UV disinfection). Likelihood can only be reduced to Rare when UV installed. Risk Treatment (raised 2015): Lack of alum flow monitorinng is an unacceptable risk due to periods of low RW pH. Alum flow monitoring required (and injection point flow switch or meter if carrier water used) with interlocks to shutdown the WTP. Raw water pH 5th%iles are <7.5 pH which is s the validated SPV upper crtiical limit for dosed water pH using alum. Therefore during a rain event when RW pH is low (5% of the time) if alum dosing was lost this would not trigger the upper crtical limit of pH 7.5. In the short term a low dosed water pH limit will be used which should detect alum dosing failure in most circumstances. Alum pump fault alarms and lowering dosed water pH limit are interim measures Update (R.A 2017): Investigate installation of flow switch to detect loss of alum dose.
TMG : Moogerah Dam WTP | TMG-15 | Coagulation | Incorrect coagulant dose | Overdose of alum leading to ineffective coagulation affecting treated water quality | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised 2017): HBT Pathogen Assessment is required for this WTP. If WTP cannot achieve log reduction target for Cat 4 then additional barrier will be required (i.e UV disinfection). Likelihood can only be reduced to Rare when UV installed.
TMG : Moogerah Dam WTP | TMG-16 TMG-15 | Flocculation and Settling | Carry over of floc, sludge or algae in settled water | Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Improvement Opportunity (raised R.A review 2017): Investigate opportunities to address clarifier sludge build up requiring manual draining and hose out on a regular basis. Risk Treatment (raised R.A review 2017): HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP likely to require additional protoza removal (i.e UV).
TMG : Moogerah Dam WTP | TMG-19 | Disinfection (primary) | Contamination by animals | Contamination of treated water tank | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Improvement Opportunity (raised R.A reveiw 2017): treated water tank has history of cracks and has not been internally inspected for evidence of ingress. Requires external and internal inspection and engineering assessment. Also need to assess for sediment build up and clean. Following tankering the turbidity increases.
TMG : Moogerah Dam WTP | MOO14 | Distribution Pipeline | Build up of solids leading to elevated turbidity | Turbidity in distribution system. Causes include: - continuos build up over time due to aging assets - change in flow conditions disturbing biofilms | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | Improvement Opportunity (raised HACCP Team meeting 2016): Investigate options for addressing ongoing turbidity (and possibly Mn) water quality issues in distribution system including long term alternative options for supply e.g new mains, rainwater tank supply. Update R.A review 2017: PID027772 - DMO - Moogerah Dam - Replace Exisitng Galvanised Steel Treated Water Reticulation Main in delivery 17/18 Improvement Opportunity (raised R.A review 2017): determine long term maintenance requirements of system to mitigate build up of turbidity and sediments over time.
TMG : Moogerah Dam WTP | ALL1 | Distribution Pipeline | Contamination due to pipe break | Ingress of contaminants leading to contamination of treated water. | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | Improvement Opportunity (raised 2010): Map out retic network; Remove all known cross connections; Investigate historical knowledge of network. Update R.A review 2017: under DMO: Moogerah Dam – Upgrade the Treated Water Reticulation System in delivery for 17/18
TCP : Capalaba WTP | TCP-27 | Disinfection (primary) | Contamination by animals | Contamination of chemical dosing chamber and/or treated water tanks | Risk Assessment | Medium (8) | Project Delivery | 4 | 2021-06-30 | N | Risk Treatment (raised R.A review 2017; GHD Report 2017): Refer recommended improvements to Reservoir Condition Assessment Capalaba Reservoir 1 and Reservoir 2 2017
TMU : Mudgeeraba WTP | TMU-29 | Raw Water Abstraction | Rain event in catchment | Intake of contaminated water that could potentially result in contaminated treated water (HUI & LND) | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatement capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal.
TMU : Mudgeeraba WTP | TMU-30 | Taste and Odour Control | Incorrect PAC dose | Underdose or failure to dose PAC when required leading to customer complaints Note: Overdose of PAC not assessed in 2017 as not expected to result in treated water quality issue. Excess PAC will settle out in clarifier resulting in increased sludge production. | Risk Assessment | High (12) | Asset Planning | 2 | 2022-06-30 | N | Improvement Opportunity (raised R.A 2015): Source water selection is primary preventative measure for managing T&O at Mudgeeraba WTP. More recently the GCDP could be used to blend or supply some zones through the incident process if T&O was an issue. These source water selection options have been successful in avoiding (rather than treating) T&O in the raw water hence likelihood of high T&O in treated water is Rare however in the event that PAC system is required the effectiveness, reliability and operability of both PAC dosing systems (HUI BoHT and WTP inlet channel) is considered poor. The effectiveness of PAC dosing into the inlet channel was found to be completely ineffective in July 2014 based on raw and treated water results and the HUI system asset condition and reliability is questionable and untested. Therefore the likihood of T&O complaints/results at unacceptable levels when dosing PAC is Likely. Update R.A 2017: WTP Planning: The PAC dosing systems (two PAC plants at Mudgeeraba) are known to require upgrades. The existing systems will be reviewed, options for rationalisation will be assessed, and business cases for the recommended upgrades will be prepared. This review addresses an outstanding APIN.
TMU : Mudgeeraba WTP | MUD-22 TMU-36 TMU-37 | Media Filtration | Filter breakthrough | Filter breakthrough resulting in hazards not being adequately controlled include failure of filter aid (LT-20) dose | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Risk Treatment (Raised HACCP internal audit 2014): Review of filtration performance at Mudgeeraba WTP to identify inadequacies to Planning. Following the filter optimisation project the individual filtered data will need to be assessed. If operational changes do not improve filter performance then capital improvements such as addressing the filter to waste restriction or an additional process step (eg UV) should be considered as log removal credits under the Health Based Targets standard cannot be applied based on the current HACCP limits. Update R.A 2017: Further quantitative assessment in Pathogen Treatment Assessment for Mudgeeraba WTP performed June 2015 (D15/116852) confirmed filters don't meet performance expectations on ripening and overall don't meet the HBT filter performance targets for 3.0 log protozoa reduction. Process Engineering team are preparing to trial an extended terminal sub-fluidisation wash (ETSFW) sequence in the filters to determine whether this improves the ripening issues. D17/120476 Mudgeeraba (TMU) Long Term Planning Report has also captured that for individual filters, ripening times are a significant performance issue. Improvement Opportunity (raised R.A review 2017): Develop filter performance reports using continuous online data against the HBT critieria to assist in informing WTP Planning Long Term Planning Report. Improvement Opportunity (raised R.A review 2017): Operators note new filter aid is effective at reducing filter run time when on LND and improving filter performance. Dedicated pumps would allow Ops to set pre filter poly dose rates. Currently bleeding into clarifier launder from pipework sending poly to clarifier floc zone. As this was a trial no dedicated pumps initially put in place. Suggest installation of dedicated poly dosing pumps and dose rate control. Include dial out alarm on poly dosing system failure.
TMU : Mudgeeraba WTP | MUD27 | Media Filtration | Contamination by animals | Contamination of filtered water outlet vessels | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Risk Treatment (raised R.A 2015): Filer outlet are open and require covering similar to NSI WTP and in accordance with relevant sections of the standard.
TMU : Mudgeeraba WTP | TMU-40 | Disinfection (primary) | Contamination by animals | Contamination of treated water tanks (including CCT, Res 1 and Res 2) | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Risk Treatment (raised R.A 2017; GHD Report 2017): Refer recommended improvements to Reservoir Condition Assessment Mudgeeraba Reservoir 1 and Reservoir 2 September 2017
TMU : Mudgeeraba WTP | MUD28 | Whole of system | Loss of control system | Loss of SCADA system or loss of PLC leading to impacts to treated water quality | Risk Assessment | Medium (8) | Operations - Maintenance | 9 | 2020-06-30 | N | Risk Treatment (raised 2015): Alarming to Operator is via external organisation and via the auto dialler. There is a lack of detailed understanding or Functional Description of where alarms are directed. Operators report some alarms not being received. Dial out alarms are currenlty hardwired into annunciator panel. Update R.A review 2017: WQ interlocks enable April 2017. There is a general lack of process regarding location, format, responsible areas and updating of Functional Descriptions (and therefore PLC code). This also includes individual validation of alarm delays on startup. MCS Summary Program (D17/159647) activity ID CMF013 lists Mudgeerabah WTP Finish date as Sep 2022.
TMO : Molendinar WTP | MDR10 TMO-17 | Raw Water Abstraction | Rain event in catchment | Intake of contaminated water that could potentially result in contaminated treated water | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Improvement Opportunity (raised R.A 2013 - previously Risk Treatment): Vertical Profiler does not dial out when there is a change in turbidity. Update R.A 2017: In early 2017 a project was raised to install a dedicated turbitity meter on the raw water main at Hinze Dam. DWQ determined that the risk reduction provided by a turbidity analyser located at the Hinze lower intake for Molendinar WTP was not sufficient to justify the $~100K installation price. This was based on the Hinze raw water being generally stable and when it does change significantly there is a known cause (i.e. significant rain event). There is a water quality profiler located near the lower intake that could be used to inform of changing raw water quality, although it is acknowledged that, at times, is not available. It also requires the Operators to access the intranet as it is not connected to the WTP SCADA. Displaying the VPS data on the Molendinar WTP would be an Improvement Opportunity as per the connectivity from the LHD VPS on Capalaba WTP SCADA. Therefore this item has been reduced from a Risk Treatment to an Improvement Opportunity in 2017. Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatement capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal.
TMO : Molendinar WTP | MDR11 TMO-24 TMO-25 | Disinfection (primary) | Insufficient C.t | Insufficient C.t due to: - low chlorine - high pH due to dosed filtered water caustic overdose - insufficient contact time - high treated water turbidity | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised R.A 2017 from Pathogen assessment conducted 2015): The CCT level and free chlorine HACCP limits are based on a MAXIMUM of 3 treated water pumps operating to meet a C.t of 8 mg.min/L. If more than 3 treated water pumps are required the Operator must contact DWQ Coordinator to recalculate free chlorine limits and minimum CCT level for higher flows (>3 treated water pumps). Refer to D17/75092 : Molendinar WTP - chlorine disinfection C.t calculation. This is noted in the HACCP Plan Wall Chart Procedure but this is an administrative control that may be oversighted. Engineering controls required such as online C.t monitoring with alarming and interlocks on treated water pumps. Further to this issue is that when four or five pumps are required the operating band of the CCT level is very narrow and likely to result in regular start/stopping of the WTP and/or treated water pumps. In addition, if the source water classification increases from a Cat 3 to a Cat 4 this will place further strain on the CCT level operating band. Risk Treatment (raised R.A review 2017): Introduce treated water pump interlocks (and auto gravity valve closure) Disinfection (primary) CCP critical limits as per Fluoridation CCP critical limits. Improvement Opportunity (riased R.A review 2017): Review supply configuration to Southport West zone. Southport West zone is direct feed via gravity valve or direct feed when treated water pumps running if gravity valve is closed (supply to Southport West backfeeds from Mol 4 when pumps offline). Due to the location of the Disinfection analyser being at the outlet of the CCT if/when these interlock there is a large volume of water in the CCT that will require re-treatment or wasting resulting in a loss of supply to the Southport West zone over that time. Under the current arrangment (at the time of the R.A) the zone was being fed direct when the treated water pumps were running however this results in reportedly high pressures in the CoGC system increasing risk of mains break. An ideal configuration would be to supply the Southport West zone from the outlet of the onsite Reservoirs.
TMO : Molendinar WTP | TMO-25 | Disinfection (primary) | Contamination by animals | Contamination of CCT, Res 3, Res 4, Res 5, Res 6 (Note: Res 7 is supply system asset) | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2020-06-30 | N | Risk Treatment (raised R.A 2017): CCT vents/overflow structure not compliant. CCT roof hatches are points of ingress. Risk Treatment (raised R.A 2017; GHD Report 2017): Refer recommended improvements to Reservoir Condition Assessment Molendinar Reservoirs.
TMO : Molendinar WTP | MDR11 | Whole of system | Loss of control system | Loss of SCADA system or loss of PLC leading to impacts to treated water quality | Risk Assessment | Medium (8) | Operations - Maintenance | 9 | 2020-06-30 | N | Risk Treatment (raised R.A 2015): Alarming to Operator is via external organisation and via the auto dialler. There is a lack of detailed understanding or Functional Description of where alarms are directed. Update R.A review 2017: There is a general lack of process regarding location, format, responsible areas and updating of Functional Descriptions (and therefore PLC code). This also includes individual validation of alarm delays on startup. MCS Summary Program (D17/159647) activity ID CMF012 lists Molendinar WTP Finish date as Sep 2021.
TNS : North Stradbroke Island WTP | NSI 17 | Supernatant Return | Superntant return quality exceeds treatment capacity | For Herring Lagoon: Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) For Bores: N/A. Bore process does not include Supernatant Return process | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Improvement Opportunity (raised CL review 2015): installation of online supernatant return turbidity monitoring to montior for return of supernatant quality. Flow rate is fixed to <10% of raw water flow so dedicated flow monitoring not required. Update R.A review 2017: Improvements should also include automation of supernatant return process i.e batch sequence etc control and interlocks on flow and turbidity.
TNS : North Stradbroke Island WTP | NSI8 NSI13 | Coagulation | Incorrect lime dose | For Herring Lagoon (pre lime): Underdose of lime into raw water main leading to: - low alkalinity for coagulation - incorrect dosed water pH Overdose of lime into raw water main leading to: - incorrect dosed water pH For Bores: N/A. Bore water does not pass through Coagulation Process Step | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Risk Treatment (raised R.A review 2015 and DWQ Report to WTP Planning 2015 D14/149372): It is recommended that the coagulation process at NSI WTP is upgraded. This upgrade should consider: - automatic changeover ‘duty’/’standby’ lime dosing pumps - feedback trim control of lime dosing from the dosed water pH analysers in the each of the DAF trains Update R.A 2017: 1) Operationa South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included improvements to Lime System. Project cancelled Oct 2017. Project to be restarted.
TNS : North Stradbroke Island WTP | NSI8 NSI13 | Coagulation | Incorrect coagulant dose | For Herring Lagoon: Underdose of alum leading to loss of coagulation For Bores: N/A. Bore water does not pass through Coagulation Process Step | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Risk Treatment (raised R.A review 2015 and DWQ Report to WTP Planning 2015 D14/149372): It is recommended that the coagulation process at NSI WTP is upgraded. This upgrade should consider: - paging of dosed water pH alarms to the Operator (Complete 2017) - interlock of WTP operation to dosed water pH alarms. This must include a full WTP HAZOP to ensure that all actions required to facilitate the interlock are identified and actioned, such that other unintentional adverse consequences are avoided - feed forward control of coagulant dose - single set of alum dosing pumps (automatic changeover ‘duty’/’standby’ arrangement) that are capable of delivering the required dose across the range of flow and alum doses expected - flow meters on the alum dosing line, interlocked to WTP operation, such that the detection of no alum flow will shutdown the WTP - flow pacing of the alum dose to raw water flow meters on the inlet to each DAF train or installation of appropriate control such that the flow to the DAF basins is equal or known - relocation of the alum dosing points to immediately upstream of the inline rapid mixers Update R.A 2017: 1) Operationa South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included improvements to Lime System. Project cancelled Oct 2017. Project to be restarted.
TNS : North Stradbroke Island WTP | NSI8 NSI13 | Coagulation | Incorrect coagulant dose | For Herring Lagoon: Overdose of alum leading to ineffective coagulation For Bores: N/A. Bore water does not pass through Coagulation Process Step | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Refer above for Underdose of alum
TNS : North Stradbroke Island WTP | TNS-24 | Dissolved Air Flotation (DAF) | Failure or incorrect operation of a bypass valve | Failure or incorrect operation of bypass from flash mixer to settled water main, or Failure or incorrect operation of bypass from supernatant return line to settled water main | Risk Assessment | Medium (8) | Asset Planning | 2 | 2022-06-30 | N | Risk Treatment (Raised R.A 2017): Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF oPRP). Under no circumstances would these bypasses be operated.
TNS : North Stradbroke Island WTP | NSI9/NSI13 TNS-25 | Media Filtration | Filter breakthrough | Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (AN905-PWG) | Risk Assessment | Medium (8) | Project Delivery | 4 | 2020-06-30 | N | Risk Treatment (raised R.A review 2015 and Report to Asset Planning D14/149372 and North Stradbroke Island WTP Pathogen treatment assessment for planning D14/63274): There is limited monitoring and control of the filtration process at NSI WTP. There is no flow monitoring of water leaving each filter or filter outlet valve position, making it difficult to identify, when a filter is ‘on line’ or filtering to waste. This makes it impossible to validate the treatment performance. It is recommended that appropriate instrumentation is installed to facilitate effective online monitoring of the status of each filter. Risk Treatment (raised R.A review 2017): There is no automation to take filters offline when filters are out of spec. Filter automation and interlocks are required. Update R.A review 2017: 1) Operationa South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included improvements to monitoring and control of filter process. Project cancelled Oct 2017. Project to be restarted. Risk Treatment (raised R.A review 2017): Investigate the risk associated with walking over filters due to significant amount of Kangaroo droppings around the site. Refer to Risk Treatment TNS-21 below for improvements to poly batching and dosing system.
TNS : North Stradbroke Island WTP | NSI10 NSI13 | Disinfection (primary) | Insufficient C.t | When running Borefield and Herring Lagoon through CCT and Res 1 (Res 2 balancing or offline) Insufficient C.t due to: - low chlorine - high pH due to post lime overdose - insufficient contact time - high treated water turbidity | Risk Assessment | Medium (8) | Operations - Maintenance | 9 | 2020-06-30 | N | Risk Treatment (raised R.A 2015 and Report to Asset Planning D14/149372): It is recommended, to mitigate the hazardous event ‘insufficient C.t’ that control of disinfection is improved. This improvement should consider: - installation of online free chlorine and pH analysers downstream of the chlorine contact tank and lime dosing point at a point that provides suitably mixed and representative water sample, upstream of the Treated Water Reservoir No. 1. (Complete at R.A 2017) - implementation of associated call out alarming and interlocks to WTP operation from these pre-reservoir analysers - trim control of the chlorine and lime dose using the online free chlorine and pH analysers - dynamic monitoring and call out alarming of C.t is introduced in the SCADA. Interlock to WTP operation should also be implemented. - the maximum instantaneous flow rate leaving the WTP and if required installation of additional contact time to enable the minimum C.t to be achieved under worst case conditions. This should include investigation of the hydraulics of the chlorine contact tank and the potential for flooding of the baffles. Update R.A 2017: 1) Operationa South SCADA maintenance team are in delivery of HACCP alarms and WTP interlocks on HACCP critical limits. 2) PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program 3) TNS Process Improvement Design Basis and Issues and Needs Report Dec 2016 included upgrade and/or additon to the exiting lime dosing system or construction of an alternative means of alkalinity adjustment was captured as a work package. Project cancelled Oct 2017. Project to be restarted. 4) PID02656 - TNS: Renew Chlorine Dosing Lines in Project Delivery 17/18 Program PID02863 - TNS: Replace Chlorinators in Project Delivery 17/18 Program
TNS : North Stradbroke Island WTP | NSI10 NSI13 | Disinfection (primary) | Insufficient C.t | When running Southern Borefield through Res 2 (CCT and Res 1 offline) Insufficient C.t due to: - low chlorine - high pH due to post lime overdose - insufficient contact time - high treated water turbidity | Risk Assessment | Medium (8) | Asset Planning | 2 | 2021-06-30 | N | Risk Treatment as per Insufficient C.t when running Borefield and Herring Lagoon through CCT and Res 1 (Res 2 balancing or offline).
TNS : North Stradbroke Island WTP | NSI18 | Disinfection (primary) | Incorrect lime dose | Underdose of lime resulting in pH <ADWG aesthetic guideline | Risk Assessment | Medium (9) | Asset Planning | 2 | 2021-06-30 | N | Risk Treatment (raised Report to Asset Planning D14/149372 and IMS audit Feb 2016. Increased from IO to Risk Treatment in R.A review 2017 due to potential for widespread aesthetic impact by grid WTP): The lime dosing system is a constant operational issues. Numerous incidents, HACCP Critical Limits excursions and HACCP Action Limit excursions have been reported due to lime dosing system faults.
TNS : North Stradbroke Island WTP | TNS-26 | Disinfection (primary) | Contamination by animals | Contamination of CCT, Res 1, Res 2 | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Risk Treatment (raised R.A 2017): Refer recommended improvements to Reservoir Condition Assessment NSI Reservoirs (D17/90672, D17/90671). CCT fire hose connect point also requires backflow prevention.
TNS : North Stradbroke Island WTP | TNS-29 | Whole of system | Loss of control system | Loss of SCADA system or loss of PLC leading to impacts to treated water quality | Risk Assessment | Medium (8) | Asset Lifecycle Capability | 3 | 2021-06-30 | N | Improvement Opportunity (raised R.A review 2017): There is a general lack of process regarding location, format, responsible areas and updating of Functional Descriptions (and therefore PLC code). This also includes individual validation of alarm delays on startup. MCS Summary Program (D17/159647) does not list NSI WTP as an Activity ID. PID02921 - TNS: MCS Renewal project with PD for delivery in 17/18 program
TAP : Amity Point WTP | ALL16 (AMITY) | Disinfection (primary) | Insufficient C.t | Insufficient C.t due to: - low chlorine - high pH due to incorrect Stabilisation pH control - insufficient contact time - high treated water turbidity | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised R.A 2013): Calculate C.t and ensure that it is adequate through suitable controls including critical alarms/interlocks. C.t calculation currently includes councils town reservoir located near Amity WTP. Update R.A 2015: C.t is currently not met at the BSP. WTP Planning preparing a draft options assessment report. Update R.A 2017: Concept design complete to achieve C.t and BSP. Consultant engaged. Preliminary design complete.
TAP : Amity Point WTP | AMI-9 | Disinfection (primary) | Contamination by animals | Contamination of treated water reservoir | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised R.A 2017): Undertake reservoir inspection in accordance with Seqwater standard.
TAP : Amity Point WTP |  | Disinfection (primary) | Contaimination due to backflow | Contamination of treated water tank resulting from backflow from Redland Water network | Risk Assessment | Medium (8) | Asset Planning | 2 | 2021-06-30 | N | Refer to Risk Treatment for insufficient C.t
TDU : Dunwich WTP | DUN6 | Disinfection (primary) | Insufficient C.t | Insufficient C.t due to: - low chlorine - high pH due to incorrect Stabilisation pH control - insufficient contact time - high treated water turbidity | Risk Assessment | Medium (8) | Asset Planning | 2 | 2021-06-30 | N | Risk Treatment (raised R.A review 2015): Investigate options to meet C.t. Will need ot liaise with Redlands due to 'change' that customers will recieve in free chlorine levels. Options could include increasing min res level. If not able to be reasonably achieved operationally then issue to be handed over to Planning.
TDU : Dunwich WTP | TDU-11 | Disinfection (primary) | Contamination by animals | Contamination of treated water reservoir | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised R.A 2017): Undertake reservoir inspection in accordance with Seqwater standard.
TDU : Dunwich WTP |  | Disinfection (primary) | Contaimination due to backflow | Contamination of treated water tank resulting from backflow from Redland Water network | Risk Assessment | Medium (8) | Asset Planning | 2 | 2021-06-30 | N | Refer to Risk Treatment for insufficient C.t
TPL : Point Lookout WTP | TPL-10 | Disinfection (primary) | Contamination by animals | Contamination of treated water reservoir and balance tank | Risk Assessment | Medium (8) | Water Quality Unit | 10 | 2019-06-30 | N | Risk Treatment (raised R.A 2017): Undertake reservoir inspection in accordance with Seqwater standard. Reservoir roof is box gutter design and likely to have points of ingress.
TPL : Point Lookout WTP | ALL1 | Disinfection (primary) | Failure or incorrect operation of a bypass valve | Failure or incorrect operation (treated water reservoir bypass | Risk Assessment | Medium (8) | Process Engineering | 6 | 2019-06-30 | N | Risk Treatment (raised HACCP Team meeting 2016): Bypass is thought to exist on outlet of 45 kL tank bypassing treated water reservoir. Bypass existance and condition requires confirmation and, if confirmed, removal. Refer REX 724654 Drawing I-DWG-TPL-601 P&ID Treated Water Storage.

## Overarching DWQMP
Drinking Water Quality Improvement Plan - Overarching DWQMP and Supporting Programs
Site | Improvement # | Other Ref | Process Step | Issue | Description | Origin of Improvement | Significant Risk | Responsibility | Due for completion | Completed? Y/N | Comments
All WTPs with UV | DWQ1 | DWQ1 | UV Disinfection | UV System Alarming | Investigate the risk of mercury contamination due to UV lamp breakage and apply the findings to the 2017 risk assessment reviews for those plants that have UV disinfection. | Research | N/A | D. Middleton | 2017-01-31 | Y | Investigation completed. Past on to DWQ Coordinators. Risk is site specific.
Overarching | DWQ2 | Aquality A1.1 | Supporting Programs | A1.1 New CEO (after commencement) person to sign WQ Policy. Updated document to go on Q-Pulse and WTP/SS sites (office/foyers) |  | Aquality | N/A | Governance, Compliance & Internal Audit (Veronica Hajenko) | 2019-12-31 | N | Update 31 JUL 18: New CEO commences in August 2018
Overarching | DWQ3 | Aquality A1.2 | Supporting Programs | A1.2 Ongoing rollout of CRM across relevant sections of Seqwater |  | Aquality | N/A | Manager, Community Relations | 2016-12-31 | Y | Ongoing roll out program. Achieved. No in continuous improvement.
Overarching | DWQ4 | Aquality A2.1 | Supporting Programs | A2.1 Catchment modelling training for Wivenhoe and Northpine. This will reduce reliance on external consultants. The catchment modelling isn't necessarily water quality based, but can be used to model differing scenarios. |  | Aquality | N/A | Morag Stewart, SPPU | 2016-12-31 | Y | Completed. Point of contact Chris Thompson
Overarching | DWQ5 | Aquality A2.2 | Supporting Programs | A2.2 LIMS1 implementation (will tie 5 systems together) LIMS1 didn’t tie-in 5 systems. At most it replaced datapproach, timestudio, link-lims (Ex linkwater), not wiski due to not being able to pull in the extra dimension of verticle profiles. LIMS1 does not currently have GPS data for catchmenet sample points. Further work on integrating databases required. |  | Aquality | N/A | Kelvin O'Halloran | 2019-12-31 | N | Ongoing. Target date extended to ensure it is achieveable.
Overarching | DWQ6 | Aquality A2.3 | Supporting Programs | A2.3 Improvement - prioritised input into the Asset Planning process (well underway) |  | Aquality | N/A | Duncan Middleton / Brian Hester | 2016-12-31 | Y | Completed. A prioritised system now implemented. WQ reports informing asset investment are now utilised by asset planning to prioritise upgrades and other works.
Overarching | DWQ7 | Aquality A2.4 | Supporting Programs | A2.4 Procedure/trigger in our RA process where risks or high uncertainties are brought to the attention of the health authority; either from an event or routine process. |  | Aquality | N/A | Duncan Shillito | 2017-12-31 | Y | 2017 Risk Assessment schedule completed
Overarching | DWQ8 | Aquality A4.1 | Supporting Programs | A4.1 Resource and develop operations manuals and supporting procedures |  | Aquality | N/A | Ops Managers North, Central and South | 2019-12-31 | N | Target date extended to ensure it is achieveable.
Overarching | DWQ9 | Aquality A4.2 Aquality A4.3 | Supporting Programs | A4.2 Recording operator competency TNA implementation actions A4.3 Need to investigate if lapses in HACCP reporting occurring |  | Aquality | N/A | Dan Healy, DWQ | 2018-12-31 | Y | Completed by Learning OD HACCP excursion confidence is current high
Overarching | DWQ10 | Aquality A4.4 | Supporting Programs | A4.4 Moving to a commercial-of-the-shelf database system (e.g. WIMS or using CIS) |  | Aquality | N/A | TBC | TBC | Y | Refer to the LIMS line item above - bringing systems together
Overarching | DWQ11 | Aquality A4.5 Aquality A4.6 | Supporting Programs | A4.5 Support operations staff update plant data sheets with conditional formating for key parameters A4.6 Standardising plant data sheets - plant data log project |  | Aquality | N/A | DWQ Regional Coords Frank Liu | 2016-12-31 | Y | Completed
Overarching | DWQ12 | Aquality A4.7 | Supporting Programs | A4.7 After hours sampling - needs to be addressed with staff issues, equipment and ability to perform sampling in aderse weather (purpose built ute set up), availaility (using Brisbane SAS lab) |  | Aquality | N/A | Kelvin O'Halloran | 2016-12-31 | Y | Completed. AH sampling arrangements in place. Sampling requests through an online form has been established.
Overarching | DWQ13 | Aquality A4.8 | Supporting Programs | A4.8 Investigation procedure/process (prevent recurrence) |  | Aquality | N/A | Helen Warburton | 2016-12-31 | Y | Completed. PRO-00793.
Overarching | DWQ14 | Aquality A4.9 | Supporting Programs | A4.9 Improve HACCP excursion reporting (by sub-region/HACCP region) |  | Aquality | N/A | Regional DWQ Coord | 2016-12-31 | Y | DWQ operator training completed
Overarching | DWQ15 | Aquality A4.10 | Supporting Programs | A4.10 Developing standards at the moment (Engineering support) - still ongoing Ensure standards etc are applied across business (no one is enforcing the standards that we already have developed). Consider use of variation requests/approvals. |  | Aquality | N/A | Dapo K Luke Hellowell Brian Hester | 2016-12-31 | Y | Well established standards library now exists. Ongoing improvement is occurring.
Overarching | DWQ16 | Aquality A4.11 | Supporting Programs | A4.11 Formulate the process from the instrumentation project - trial, acceptance and documentation handover can be improved |  | Aquality | N/A | Dapo K | 2016-12-31 | Y | Completed
Overarching | DWQ17 | Aquality A4.12 | Supporting Programs | A4.12 DWQ/IMS audits and review of accessibility of historical data and compliance |  | Aquality | N/A | Dan Healy Pierre van der Mere | 2016-12-31 | Y | All records are now entered into Risk Wizard database and can be reviewed there.
Overarching | DWQ18 | Aquality A4.13 | Supporting Programs | A4.13 Confirmation that alarm set points are correct and test to esnure they work |  | Aquality | N/A | Matt Bartholemew Dan Healy | 2016-12-31 | Y | Regular audit and interlock-maintenance testing schedules
Overarching | DWQ19 | Aquality A4.14 | Supporting Programs | A4.14 Follow up on Process assessments - process for getting improvements into Seqwater's various systems |  | Aquality | N/A | Jonathan Creamer | 2019-12-31 | N | Collaborative approach to ION requests. Update required on progress.
Overarching | DWQ20 | Aquality A4.15 | Supporting Programs | A4.15 Project handover / commissioning to include documentation, schedules and critical spares |  | Aquality | N/A | Brian Dagg John Gallea Kathleen Thatcher | 2016-12-31 | Y | Completed
Overarching | DWQ21 | Aquality A4.16 | Supporting Programs | A4.16 Determine whether analysers/meters need to be done consistently |  | Aquality | N/A | Peter Pennell | 2019-12-31 | N | Completed. Refer PRO-02120
Overarching | DWQ22 | Aquality A4.17 | Supporting Programs | A4.17 CIS records to be improved for strategic asset maintenance and operational record keeping - simplify the recording arrangement |  | Aquality | N/A | John Gallea Pierre van der Mere (Op representation) | 2019-12-31 | N | To be completed with action DWQ21
Overarching | DWQ23 | Aquality A4.18 | Supporting Programs | A4.18 Improve processes for proactive budgeting and replacement of agining and failing equipment |  | Aquality | N/A | Peter Pennell Bruce Hutton | 2019-12-31 | N | Asset Capability Lifecycle team are now responsible and have established processes for renews and minor work, and major mork is transferred to Asset Planning.
Overarching | DWQ24 | Aquality A4.19 | Supporting Programs | A4.19 Specify Interlock testing - not fully implemented other than fluoridation systems |  | Aquality | N/A | Duncan Shillito Dapo K | 2019-12-31 | Y | Maintenance program in place.
Overarching | DWQ25 | Aquality A4.20 | Supporting Programs | A4.20 Improve the supply and handling of small (20L) quantities to ensure they come from approved suppliers, fr e.g. disinfection SOPs for maintenance and project work when recomissioning assets |  | Aquality | N/A | Sonia Edwards | 2019-12-31 | Y | Disinfection procedures established. Chemical supply contractual arrangements weell established
Overarching | DWQ26 | Aquality A4.21 Aquality A4.22 | Supporting Programs | A4.21 Ensure compliance with standards tha are developed by ETS - projects, contracts and work orders A4.22 Add materials requirements to maintenance and project staff DWQ awareness training |  | Aquality | N/A | Luke Hellowell Dan Healy (training) | 2019-12-31 | Y | Refer DWQ15. DWQ training has a well established program with 2-yearly refresher training.
Overarching | DWQ27 | Aquality A4.23 | Supporting Programs | A4.23 Come up with a checking process that is achieveable with the current staff and recourses, for e.g. using LIMS by having uploadable formats from suppliers and alerts in LIMS for any exceedances. External audit/review |  | Aquality | N/A | Kelvin O'Halloran Sonia Edwards | 2019-12-31 | Y | LIMS alerts system implemented and remains in use.
Overarching | DWQ28 | Aquality A4.24 | Supporting Programs | A4.24 Finalise implementation of chemical delivery procedures across WTPs (already in place at SS sites) |  | Aquality | N/A | David Roberts | 2019-12-31 | N | The impelmentation of suite of procedures had commenced. Three procedures yet to be developed
Overarching | DWQ29 | Aquality A4.25 | Supporting Programs | A4.25 Review couplings requirements (chemical delivery operations) and signage/labelling requirements. Make suggested improvements. |  | Aquality | N/A | David Roberts Duncan Shillito Vince Granahan | 2019-12-31 | Y | Completed. Refer DWQ28
Overarching | DWQ30 | Aquality A4.26 | Supporting Programs | A4.26 Finalise implementation of disinfection SOPs and materials that come into contact with DW training |  | Aquality | N/A | Dan Healy | 2019-12-31 | Y | Training has been completed. Ongoing refresher/new start program.
Overarching | DWQ31 | Aquality A5.1 | Supporting Programs | A5.1 WQ awareness for reception staff |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | N | Update 30 Jun 18: Yet to commence. Scheduled to occur in later half 2018.
Overarching | DWQ32 | Aquality A5.2 | Supporting Programs | A5.2 Non-conformance response procedure to be developed *now linked to investgation procedure* |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | N | Refer to DWQ2. Corporate procedures exist including PRO-00793
Overarching | DWQ33 | Aquality A6.1 Aquality A6.2 Aquality A6.3 | Supporting Programs | A6.1 On-call DWQ pers to communicate to line management as per Incident Controller training. Continue to rollout this training. A6.2 Update incident and communication rocesses in line with the Regional Operations model A6.3 Process for email-OCA Acknowledgement |  | Aquality | N/A | Duncan Shillito Jason Boldeman | 2019-12-31 | Y | All OCA and Incident controller training has been completed by DWQ staff that are on-call. Incident communication processes are now well established and fully implemented. DWQ staff are further developing their emergency management skills by participating in major incident-emergency exercises.
Overarching | DWQ34 | Aquality A6.4 | Supporting Programs | A6.4 Disinfection SOPs to be finalised and applied across the business |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | Y | Refer to DWQ30. Completed
Overarching | DWQ35 | Aquality A6.5 | Supporting Programs | A6.5 Finalise Seqwater Incident investigation procedure (draft) which includes ICAM |  | Aquality | N/A | Helen Warburton | 2019-12-31 | Y | Refer to DWQ2. Completed. PRO-00793
Overarching | DWQ36 | Aquality A7.1 | Supporting Programs | A7.1 Re-look at training for senior leadership and PM positions |  | Aquality | N/A | DWQ (Dan Healy) | 2019-12-31 | N | Updated 30 Jun 18: New induction program for senior managers drafted. Review package and deliver in 2018-19. Review target date accordingly.
Overarching | DWQ37 | Aquality A7.2 Aquality A7.3 | Supporting Programs | A7.2 Establish a detailed HACCP team charter with team member responsibilties A7.3 Complete maintenance/PM rollout of training |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | Y | Completed
Overarching | DWQ38 | Aquality A7.4 | Supporting Programs | A7.4 Feedback in next round of DWQ awareness training through Learning OD (independent party) |  | Aquality | N/A | Learning OD | 2019-12-31 | Y | Completed
Overarching | DWQ39 | Aquality A9.1 Aquality A9.2 | Supporting Programs | A9.1 Strategy being developed for capturing knowledge gaps A9.2 Development of the WQ partnership to capture risks and identify research needs |  | Aquality | N/A | A. Roux D. Shillito | 2019-12-31 | Y | Completed. WQ Partnership now exists
Overarching | DWQ40 | Aquality A9.3 | Supporting Programs | A9.3 Knowledge management - consider establishing a library or portal to share research proposals and outcomes |  | Aquality | N/A | A.Roux | 2019-12-31 | N | Review target date and staff member responsible for completion.
Overarching | DWQ41 | Aquality A9.4 | Supporting Programs | A9.4 Add the Supply System to the DWQMP Validation Report |  | Aquality | N/A | D. Middleton | 2019-12-31 | Y | Completed. Updated document registered on Qpulse.
Overarching | DWQ42 | Aquality A9.5 | Supporting Programs | A9.5 Formal process for communicating changes and any related validation to the Regulator |  | Aquality | N/A | D. Shillito | 2019-12-31 | Y | Completed. Refer to DWQMP submitted to the Regulator as an amendment application during 2016.
Overarching | DWQ43 | Aquality A9.6 | Supporting Programs | A9.6 Establish a Process risk register |  | Aquality | N/A | Dapo | 2019-12-31 | Y | Completed. Process issues register exists/is in use
Overarching | DWQ44 | Aquality A10.1 | Supporting Programs | A10.1 Finalise roll out and formal processes/procedures for records management |  | Aquality | N/A | Records/ICT | 2019-12-31 | Y | Completed. REX (formerly TRIM) is no rolled out.
Overarching | DWQ45 | Aquality A10.2 | Supporting Programs | A10.2 Supply System Operator training including excursion reporting Re-instate use of intranet as a portal to documents/spreadsheets |  | Aquality | N/A | S Oldridge | 2019-12-31 | Y | Completed. Ongoing training and feedback to continue to improve excursion reporting.
Overarching | DWQ46 | Aquality A10.3 | Supporting Programs | A10.3 Operator experience/set up in business use of TRIM so that all records/spreadsheets can migrate from G:drive to TRIM |  | Aquality | N/A | Records/ICT | 2019-12-31 | N | Refer DWQ44. Need to review whether this is the best option or is a database option is better.
Overarching | DWQ47 | Aquality A11.1 | Supporting Programs | A11.1 Business Intelligence Project |  | Aquality | N/A | ICT Manager | 2019-12-31 | N | Refer A10.3
Overarching | DWQ48 | Aquality A12.1 | Supporting Programs | A12.1 Incorporate Senior Executive Review into DWQMP and HACCP team meetings |  | Aquality | N/A | Duncan Shillito | 2019-12-31 | Y | Completed. Any feedback (if provided) from the senior executive review (management review) conducted annually is able to be included in the HACCP team meeting talking points and published on the DWQ intranet.
Overarching | DWQ49 | Aquality A12.2 | Supporting Programs | A12.2 Route for all DWQ improvement items and 'WQ Reports' through Process Engineering |  | Aquality | N/A | Dapo and Dunc M | 2019-12-31 | N | Extension to 2019 to further improve collaboration with DWQ and Process Engineering.
Overarching | DWQ50 | Aquality A12.3 | Supporting Programs | A12.3 The DWQIP for a site is also reviewed at internal audits and HACCP team meetings. |  | Aquality | N/A | Dan Healy | 2016-03-31 | Y | Completed. Standing item at HACCP team meetings
Overarching | DWQ51 | Audit / INIR 3939 | Supporting Programs | Water Treatment Plant data sheets to move from G:drive to TRIM |  | Audit | N/A | Records/ICT | 2017-06-01 | Y | Refer to A10.3 (duplicate item)
Overarching | DWQ52 | Audit / INIR 3942 | Supporting Programs | The current oPRP table is incomplete and a review of the oPRP table is required.(D15/6241). Information regarding the following items are to be included in the table in order to comply with ISO 22000:2005 requirements: • Monitoring procedures that demonstrates that the oPRP is implemented • Corrections and corrective actions to be taken if monitoring shows that the oPRPs are not in control • Responsibilities and authorities • Records of monitoring |  | Audit | N/A | Dan Healy | 2017-06-01 | Y | Completed. oPRPs are now detailed in HACCP plans
Overarching | DWQ53 | Audit / INIR 3946 | Supporting Programs | HACCP documentation- determine a process to achieve a unified process step definition and alignment for all HACCP documentation Define and align the process steps in the HACCP documentation. The affected documents are: Validation standard, HACCP plan- definition of the operating philosophy including the process steps, risk assessment, monitoring plan, wall chart and plant data sheets. |  | Audit | N/A | Regional DWQ Coord | 2017-06-01 | Y | HACCP plan consistency issues have been resolved. Completed.
Overarching | DWQ54 | Audit / INIR 3947 | Supporting Programs | Establishing limits for discrepancy/tollerance between Operator Grab sample results and corresponding online analyser measurements. There is a need for discussions around defining acceptable limits for online vs grab samples in order to determine whether calibration or other corrective actions are required. |  | Audit | N/A | Regional DWQ Coord | 2017-06-01 | Y | Operator and collaborative maintenance contract processes, including the maintenance and calibration of onlien instruments across all operational areas, is now well established.
Overarching | DWQ55 | Audit / INIR 3928 | Supporting Programs | Establish program (e.g work orders in CIS as per fluoride system) for verifying preventative measures for CCP e.g verfication that water quality alarms and interlocks and other preventative measures listed in the HACCP Risk Registers are adequately monitored, enabled and effective. |  | HACCP Critical Limit Excursion | N/A | Dan Healy | 2017-06-01 | Y | Completed. Now regularly reviewed during HACCP team meetings and verified during audits.