## DWQ Improvement Plan
PROTECHT ID | STATUS | LOCATION | TITLE | DESCRIPTION | RISK LEVEL | DATE CREATED | DATE DUE | DATE CLOSED | PROGRESS UPDATES
1002837 | Open | Supply System | Supply System - Brisbane Zone - Disturbance of Sediment Due to one or more of the following events leading to out of specification treated water:- Low level;- Significant rate up or draw; - Valving change altering flow dynamics.Medium (8) (WQ Risk Treatment) | Investigate most effective way to clean Supply System Reservoirs. | M - 8 | 2023-07-19 | 2026-05-28 |  | 30/05/24 - Cleaning of reservoirs is delayed due to the delay of mixer procurement.
1002839 | Open | Supply System | Supply System - Brisbane Zone - Contamination by IngressDue to one or more of the following contaminants leading to out of specification treated water:- Vermin- Rain- Dust or other debrisMedium (8) (WQ Risk Treatment) | Review of Current ROV Inspection Process and procedure to determine effectiveness. | M - 8 | 2023-07-19 | 2028-07-31 |  | 14/03/25 - To be reviewed by Continuous Improvement Team.
1003023 | Closed | Molendinar WTP | TMO-RW-A-10321 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. (WQ Risk Treatment) | TMO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TMO-17) Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatment capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. | M - 8 | 2019-09-02 | 2024-07-31 | 2024-07-22 | Update October 2019: Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81738 Molendinar WTP - HBT Assessment 2018/19 - Draft Report. Note this does not incorporate review of source water category. Rex Ref. D19/81738. Update 21/07/2020: Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled for August 2020 Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. Molendinar WTP Source water assessment was completed 27/11/2023 (Rex D23/257576). no further action required.
1003025 | Closed | Molendinar WTP | TMO-RW-A-10323 Improvement Opportunity: Investigate opportunities to meet < 5 % rate of return recommended by the AWWA, Water Treatment Alliance and the WaterRA report 1079 Good Practice Guide to the Operation of Drinking Water Supply Systems for the Management of Microbial Risk 2015 using current assets with a view to making recommendations for future upgrades if required to meet this target. (WQ Risk Treatment) | TMO - Supernatant Return - Supernatant return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - release of manganese due to low pH from alum overdose or alum spill Medium (5) (TMO-19) 'Improvement Opportunity (raised R.A 2017): A return rate of < 5 % of the raw water flow is recommended by the AWWA, Water Treatment Alliance and the WaterRA report 1079 Good Practice Guide to the Operation of Drinking Water Supply Systems for the Management of Microbial Risk 2015. Current operational feedback is that the WTP would not be able to meet this requirement due to operational bottle necks which would ultimately inhibit filter backwashing or would result in overflow from backwash settling tanks to sludge to sewer tank which results in an increase in trade waste cost. Opportunities to meet this requirement using current assets should be investigated with a view to making recommendations for future upgrades if required to meet this target. | M - 8 | 2019-09-02 | 2027-10-31 | 2024-12-19 | The business needs to determine if the 5% target will be adopted as currently considering controls and conditions that would permit 10% return rates. spe-00320 details CCP limits for return water.
1003027 | Open | Molendinar WTP | TMO-RW-A-10325 Improvement Opportunity: investigate option to install pH analyser in raw water main to improve timeliness of detection of CO2 or lime dosing system failure and therefore reduce volume of water which is outside pH critical limits. (WQ Risk Treatment) | TMO - Coagulation - Incorrect CO2 dose. Underdose or overdose of CO2 leading to incorrect coagulated water pH leading to ineffective control of hazards impacting treated water quality. Medium (5) (previously TMO-21) 'Improvement Opportunity (raised R.A 2017): investigate option to install pH analyser in raw water main to improve timeliness of detection of CO2 or lime dosing system failure and therefore reduce volume of water which is outside pH critical limits. | M - 8 | 2019-09-02 | 2025-11-30 |  | Work with PE to see if this is going to be supported by the business, if not close out as is L5 risk or less.
1003029 | Open | Molendinar WTP | TMO-RW-A-10326 Improvement Opportunity: alum flow paced dosing to include supernatant return. (WQ Risk Treatment) | TMO - Coagulation - Incorrect coagulant dose. Underdose of alum. Medium (5) (previously TMO-22) Improvement Opportunity (raised RA review 2015): Supernatant return is after raw water flow meter therefore chem dosing does not account for increase in flow or and coagulant dose dose not compensate for supernatant return. Return point is after lime and CO2. | M - 8 | 2019-09-02 | 2025-11-30 |  | This is being included in the OT upgrade currently underway. this action will be updated after the project is complete.
1003031 | Closed | Molendinar WTP | TMO-RW-A-10327 Improvement Opportunity: determine upper dosing limits for poly onsite with regard to acrylamide guidelines. Determine if poly pump or design settings prevent overdose above ADWG (to be confirmed) (WQ Risk Treatment) | TMO - Coagulation - Incorrect coagulant aid dose. Over dosing of Poly DADMAC into inlet chamber leading to ineffective coagulation or acrylamide > ADWG OR Underdose of Poly DADMAC into inlet chamber leading to effective coagulation. Note: polyDADMAC not suitable for organics removal, better suited to colloidal removal. Medium (5) Improvement Opportunitiy (raised R.A 2017): determine upper dosing limits for poly onsite with regard to acrylamide guidelines. Determine if poly pump or design settings prevent overdose above ADWG (to be confirmed). | M - 8 | 2019-09-02 | 2025-05-30 | 2025-06-02 | Mass balance determined maximum poly dose is not able to breech ADWG even under lowest flow and existing controls would catch before this event could occur.
1003033 | Open | Molendinar WTP | TMO-RW-A-10331 Improvement Opportunity: Investigate improvements to control system to trigger WTP interlock shutdown when three or more (Operator setpoint) filters are offline due to the HACCP critical limit to avoid increase loading of online filters. (WQ Risk Treatment) | TMO - Media Filtration - Filter breakthrough. Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) dose when dosing (Note: not dosed since 2014) Medium (5) (MDR-11)Improvement Opportunity (raised R.A review 2015): When a filter is queued to backwash on a high turbidity set point, the plant flow rate should be reduced so that flow on that filter is reduced to minimize the potential for break-through. This avoids the bump of extra flow on the other filters (of which there are only 5). | M - 8 | 2019-09-02 | 2026-07-31
1003035 | Closed | Molendinar WTP | TMO-RW-A-10339 Risk Treatment: WTP shutdown takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Under high flow conditions this is not insignificant. Review and optimise interlock sequencing. Develop recovery plans where required if impacts to CCPs during high flow conditions require recovery. (WQ Risk Treatment) | TMO - Whole of System - Loss of control system. Loss of SCADA system or loss of PLC leading to impacts to treated water quality Medium (8) Risk Treatment (raised R.A 2017): Raw water pump shut down takes 20 mins because raw water flow control valve auto shutdown takes 20 mins. Review and optimise interlock sequencing. | M - 8 | 2019-09-02 | 2024-07-31 | 2024-07-22 | Update R.A 2019: WTP shutdown takes 20 mins because raw water valve takes 20 mins to close due to functionality set. This improvement may not be possible until new valve installed. Update R.A 2021: Being actioned under Risk Wizard incident 26864 HACCP critical limit exceedance no coag flow. HACCP crash stop is 12 mins. Detail provided in 2021 RA shows that the plant HACCP interlock for coag >+- 25% discrepancy in flow is 12 mins. this addresses the risk and no further action is required.
1003037 | Closed | Mudgeeraba WTP | TMU-RW-A-10476 Risk Treatment: Review HBT source water category taking into consideration potential for short circuiting under high inflow conditions. (WQ Risk Treatment) | Risk Treatment (raised R.A 2017): Likelihood has been risk assessed as Unlikely due impact of cyc. event in Mar 2017 which requires a review of the HBT source water category. Treatement capability remains unchanged however potential increase in source water category results in protozoa log shortfall in addition to the filter performance failures against the HBT criteria for achieving 3.5 protozoa log removal. TMU - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water (HUI LND) Medium (8) (TMU-29) | M - 8 | 2019-09-05 | 2024-07-31 | 2024-07-22 | Update R.A 2019: PE team currently undertaking second HBT assessment. In draft at time of R.A. Refer D19/81746 Mudgeeraba WTP - HBT Assessment 2018 - Draft Report. Note this does not incorporate review of source water category. Update 14/09/2020: Hinze Dam hydrodynamic QMRA was done in 2015 prior to the dam wall upgrade and therefore the storage curve standard. It is likely possible to use existing information to fill the gap within the model in 20/21 within the Sanitary Survey program. Lake Advancetown Hydrodynamic QMRA Scoping Meeting scheduled late Oct 2020. Update R.A 2021: HBT monitoring over winter. Hydrological monitoring to inform risks associated with buffer in storage. The Mudgeeraba WTP Source Water Assessment was completed 24/11/2023 (rex D23/243289). No further action required.
1003041 | Open | Mudgeeraba WTP | TMU-RW-A-10479 Improvement Opportunity: Relocate supernatant return turbidity meter to location where pH meter is to reduce delay in getting representative sample. (WQ Risk Treatment) | Improvement Opportunity (raised R.A 2017): Relocate supernatant return turbidity meter to location where pH meter is to reduce delay in getting representative sample. TMU - Supernatant Return - Supernatant return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - release of manganese due to low pH from alum overdose or alum spill Medium (5) (TMU-32) | M - 8 | 2019-09-05 | 2026-07-31
1003043 | Open | Mudgeeraba WTP | TMU-RW-A-10480 Improvement Opportunity: Improve reliability and operability of alum dosing system to reduce likelihood of loss of dose or under dose of alum. (WQ Risk Treatment) | Improvement Opportunity (raised R.A 2015): During the weekly alum duty pump changeover alum pump number 1 doesn't prime. That is, changing over from alum pump 1 to pump 2 is successful while changing from alum pump 2 to pump 1 is unsuccessful and operators are required to manually intervene each week. TMU - Coagulation -Incorrect coagulant dose Underdose of alum Medium (5) (MUD24) | M - 8 | 2019-09-05 | 2026-07-31
1003045 | Open | Mudgeeraba WTP | TMU-RW-A-10481 Improvement Opportunity: determine upper dosing limits for poly onsite with regard to acrylamide guidelines. Confirm poly pump or design settings prevent overdose above ADWG. (WQ Risk Treatment) | Improvement Opportunity (raised R.A 2017): determine upper dosing limits for poly onsite with regard to acrylamide guidelines. Confirm poly pump or design settings prevent overdose above ADWG (to be confirmed) TMU - Coagulation - Incorrect coagulant aid dose Over dosing of Poly DADMAC into inlet chamber leading to ineffective coagulation or acrylamide > ADWG OR Underdose of Poly DADMAC into inlet chamber leading to effective coagulation Medium (5) (TMU-33) | M - 8 | 2019-09-05 | 2026-07-31
1003047 | Open | Mudgeeraba WTP | TMU-RW-A-10483 Improvement Opportunity: Settled water turbidity instrument issues to be resolved. Ultraturbs continuously get blocked with floc. Recommend surface scatter. (WQ Risk Treatment) | Improvement Opportunity (raised R.A 2015): Settled water turbidity instrument issues to be resolved. Ultra turbs continuously get blocked with floc. Recommend surface scatter - require daily clean to read correctly. Note: if settled water turbidity is to be sampled before hypo and filter aid dosing points then sample points need to be relocated. Clarifier 1 sample is gravity fed to analyser and blocks. Clarifier 2 sample is pumped and dose not block. TMU - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed/failure - Loss of flocculation aid (LT-20 or 25) into clarifier floc zone Medium (5) (TMU-34) | M - 8 | 2019-09-05 | 2026-01-31
1003049 | Open | Mudgeeraba WTP | TMU-RW-A-10485 Risk Treatment: Undertake improvements to improve filter performance for filters which don't consistently achieve protozoa LRV log reduction credits due to filter ripening spikes. (WQ Risk Treatment) | Risk Treatment (Raised HACCP internal audit 2014): Review of filtration performance at Mudgeeraba WTP to identify inadequacies to Planning. Following the filter optimisation project the individual filtered data will need to be assessed. If operational changes do not improve filter performance then capital improvements such as addressing the filter to waste restriction or an additional process step (eg UV) should be considered as log removal credits under the Health Based Targets standard cannot be applied based on the current HACCP limits. TMU - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) when required Medium (5) (MUD-22) | M - 8 | 2019-09-05 | 2026-01-31
1003051 | Closed | Mudgeeraba WTP | TMU-RW-A-10486 Improvement Opportunity: Develop filter performance reports using continuous online data against the HBT criteria to assist in informing WTP Planning. (WQ Risk Treatment) | Improvement Opportunity (raised R.A review 2017): Develop filter performance reports using continuous online data against the HBT criteria to assist in informing WTP Planning Long Term Planning Report. TMU - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled resulting from: - Filter breakthrough - Underdose or failure to dose filter aid (LT-20) when required Medium (5) (TMU-36) | M - 8 | 2019-09-05 | 2026-01-31 | 2024-12-19 | Filtration assessment 18/19 and full process hbt 22/23 have been completed
1003053 | Open | Mudgeeraba WTP | TMU-RW-A-10490 Improvement Opportunity: Introduce dynamic C.t monitoring in SCADA. (WQ Risk Treatment) | Improvement Opportunity (raised R.A review 2017): Introduce dynamic C.t monitoring in SCADA. TMU - Disinfection (primary) - Insufficient C.t Insufficient C.t (Bypass Closed) due to: - low chlorine - high pH due to caustic overdose - insufficient contact time - high treated water turbidity Medium (5) (TMU-38) | M - 8 | 2019-09-05 | 2026-06-30
1003055 | Open | Mudgeeraba WTP | TMU-RW-A-10491 Improvement Opportunity: Baffle factor currently applied to C.t calculation is 0.3 for CCT and Res 1 and 0.1 for Res 2. Validation of baffle factor will improve operational band at the lower end of the HACCP limits with regard to achieving primary disinfection, in particular during higher flow scenarios. (WQ Risk Treatment) | Improvement Opportunity (raised R.A review 2017): Baffle factor currently applied to C.t calculation is 0.1. Validation of baffle factor will improve operational band at the lower end of the HACCP limits with regard to achieving primary disinfection, in particular during higher flow scenarios. Secondary Disinfection (sufficient free chlorine for distribution system) is achieved by the current HACCP target range which will not change. TMU - Disinfection (primary) - Insufficient C.t Insufficient C.t (Bypass Closed) due to: - low chlorine - high pH due to caustic overdose - insufficient contact time - high treated water turbidity Medium (5) (TMU-39) | M - 8 | 2019-09-05 | 2026-01-31
1003057 | Open | Mudgeeraba WTP | TMU-RW-A-10493 Risk Treatment: Reservoir bypass would not be used due to insufficient C.t. Bypass valve remains in closed position but should be removed at a future opportunity. (WQ Risk Treatment) | Risk Treatment (rasied R.A review 2015): Reservoir bypass requires removal. Update R.A 2017: Short term management: assess water quality risks associated with bypass main remaining offline and short term preventative measures and long term improvements: e.g removal of bypass, improvements to current practice (actuated valve to perform routine flush into network), actuated valve with pipework to sludge handing area, continuous low flow through a smaller bypass line, or leave it isolated and flush if/when we need it. Long term management: Remove the bypass TMU - Disinfection (primary) - Failure or incorrect operation of a bypass valve Failure or incorrect operation of Reservoir 1 and Reservoir 2 bypass resulting in insufficient C.t or Deterioration of water that remains stagnant in the bypass pipe Medium (5) (MUD25) | M - 8 | 2019-09-05 | 2026-01-31
1003061 | Open | Molendinar WTP | TMO-RW-A-10678 Improvement Opportunity: Introduce dynamic C.t monitoring in SCADA. (WQ Risk Treatment) | TMO - Disinfection (primary) - Insufficient C.t. Insufficient C.t resulting from: - low chlorine - insufficient contact time - high pH due to dosed filtered water caustic overdose - high treated water turbidity Medium (5) Improvement Opportunity (raised R.A review 2019): Introduce dynamic C.t monitoring in SCADA. | M - 8 | 2019-09-26 | 2026-06-30 |  | Update R.A 2019: Refer FD. COMPLETE Update R.A 2021: ongoing. Deliver as part of P.E deliverables at time of R.A.
1003065 | Open | Mudgeeraba WTP | TMU-RW-A-11271 Improvement Opportunity: Flow paced alum dosing system to take into account the increase in flow and load from the intermittent supernatant return flow to the inlet structure. (WQ Risk Treatment) | Improvement Opportunity (raised R.A 2017): Flow paced alum dosing doesn't take into account the increase in flow and load from the intermittent supernatant return flow to the inlet structure. TMU - Coagulation - Incorrect coagulant dose Underdose of alum Medium (5) (TMU-32) | M - 8 | 2020-01-21 | 2026-07-31
1003067 | Open | Supply System | Supply System - Disinfection (secondary) - Incorrect ammonia doseUnder dosing aqueous ammonia NH3(aq) leading to out of specification treated water.Medium (8) (WQ Risk Treatment) | NPI Supply Zone Conduct Process Assessment of Caloundra Street WQMF dosing systems. | H - 12 | 2020-07-20 | 2025-11-30 |  | 06/03/2025 - Process Engineering yet to finalise report
1003069 | Open | Molendinar WTP | TMO-RW-A-12917: Undertake investigation into filter blocking phenomenon due to impacts to capacity and significant operational disruption which also results in increase in filter water turbidity Jan 2021. (WQ Risk Treatment) | TMO - Raw Water Abstraction - Cyanobacterial bloom Cyanobacteria bloom leading to: filter blocking algae resulting in reduced filter run time, increased backwash volumes, reduced WTP capacity, increased supernatant return volumes, increased filter breakthrough Medium (6) Improvement Opportunity (raised R.A 2021): TF to speak to CV about how to get research team involved. | M - 8 | 2021-04-23 | 2026-07-31
1003071 | Open | Molendinar WTP | TMO-RW-A-12918 Improvement Opportunity: validate CCT baffle factor of 0.5. (WQ Risk Treatment) | TMO - Disinfection (primary) - Insufficient C.t. Insufficient C.t resulting from: - low chlorine - insufficient contact time - high pH due to dosed filtered water caustic overdose - high treated water turbidity Medium (5) Improvement Opportunity (raised R.A review 2019): Introduce dynamic C.t monitoring in SCADA. | M - 8 | 2021-04-23 | 2026-07-31
1003075 | Open | Mudgeeraba WTP | TMU-RW-A-13001 Improvement Opportunity: Install dual treated water free chlorine and pH instrumentation at outlet of Reservoir 2. This site is a gravity site and loss of treated water instrument requires manual Operator sampling until instrumentation can be re-instated. (WQ Risk Treatment) | Improvement Opportunity (raised incident April 2020): install dual treated water free chlorine and pH instrumentation at outlet of Reservoir 2. This site is a gravity site and loss of treated water instrument requires manual Operator sampling until instrumentation can be re-instated. Occurred on two occasions in 2020. ION01569 has been raised. TMU - Disinfection (primary) - Insufficient C.t Insufficient C.t (Bypass Closed) due to: - low chlorine - high pH due to caustic overdose - insufficient contact time - high treated water turbidity Medium (5) (TMU-39) | M - 8 | 2021-06-10 | 2026-07-31
1003087 | Open | Mt Crosby East Bank WTP | East Bank WTP - Media Filtration - Filter Breakthrough (High 12) (WQ Risk Treatment) | Review more data related to new filter performance. | H - 12 | 2021-08-12 | 2028-12-31 |  | DWQ RA Review 12 Sep 24: Filter refurbishment completed. Review more data related to new refurbished filter performance. Date extended to same date as UV business case/project plan: • Preliminary business case – complete January 2026 • Detailed business case – complete January 2027 • Investment approval – June 2027 • Construction start July 2027 and complete December 2028
1003097 | Closed | Supply System | Supply System - NPI - Disinfection (secondary) - Incorrect Sulfuric Acid DoseUnder dose of sulfuric acid leading to reduced secondary disinfection for break point chlorination High 12 (WQ Risk Treatment) | Complete the commissioning of the Sulfuric Acid dosing system at Caloundra Street WQMF. Essential for RSDOP to progress. | H - 12 | 2023-07-27 | 2025-01-31 | 2025-02-20 | 26/07/24 - Project is currently in delivery and expected to be completed by October 2024. 22/11/24 - Waiting on update from Project Manager. 04/12/24 - Installation completed but waiting to commission system. 20/02/25 - This project has now been constructed and commissioned as confirmed by the Project Manager.
1003197 | Closed | Supply System | Heinemann Road Reservoirs - Locate documentation detailing chlorine dosing control in Reservoirs 2 & 3. If documentation can not be located, new documentation is to be developed. (WQ Risk Treatment) | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | M - 8 | 2020-01-09 | 2025-12-31 | 2025-05-23 | Archive box was ordered from Grace Storage and documentation only described brands of equipment and equipment manuals. Records have been unable to be located. No further work to be carried out on this action.
1003273 | Open | North Stradbroke Island WTP | TNS-RW-A-10182 Risk Treatment: Improvements to dosing, monitoring and alarming relating to poly system. Current impact of failure is minimal under normal conditions however when required, if poly dosing fails, subsequent processes are likely to fail. Improvements required. (WQ Risk Treatment) | TNS - Coagulation - Incorrect coagulant aid dose. For Herring Lagoon: Overdose of AN905 into inlet flocculation tank leading to ineffective coagulation or acrylamide > ADWG OR Underdose of AN905 into inlet flocculation tank leading to ineffective coagulation Medium (8). (TNS-21) | M - 8 | 2019-08-27 | 2029-12-12 |  | Herring Lagoon is no longer in use or able to be used. Plans to consider use of the HL source are moved to the medium/long term period and will requires new capital and process optimisation to occur prior.
1003277 | Open | Mt Crosby East Bank WTP | Eastbank WTP - Coagulation - Incorrect coagulant doseUnderdose of Alum resulting in ineffective coagulation leading to filter breakthrough.Medium (8) (WQ Risk Treatment) | Investigating the installation of UV254 online instruments at the basin outlets for all basins at Eastbank and Westbank, and Holts Hill. | M - 8 | 2020-07-16 | 2025-12-31 |  | DWQ RA 12 Sep 24: PE Investigating the installation of UV254 online instruments at the basin outlets for all basins at East Bank and West Bank, and Holts Hill. Currently operator grab samples.
1003281 | Open | Mt Crosby West Bank WTP | Westbank WTP - Media Filtration - Filter breakthrough.Potential contamination of treated water.Medium (5) (WQ Risk Treatment) | 1). A review of recent filter turbidity data should be undertaken to assess performance and risk in light of the potential protozoa (Crypto) load in the raw water. 2). Consideration should be given to ascertaining if individual flow meters on each filter would be advantageous; 3). Consideration should be given to reviewing the capacity of the "mud plant" at this WTP, which is a bottle neck to backwashing | H - 12 | 2020-07-16 | 2028-12-31 |  | Mt Crosby WTPs additional pathogen barrier (UV) - Project Plan for Preliminary Business Case: • Preliminary business case – complete January 2026 • Detailed business case – complete January 2027 • Investment approval – June 2027 • Construction start July 2027 and complete December 2028
1003291 | Open | Hinze Dam WTP | THZ-RW-A-12154 Risk Treatment: Instigate dial out alarm if raw water flow detected and WTP not running to detect untreated raw water flows entering WTP. (WQ Risk Treatment) | Instigate dial out alarm if raw water flow detected and WTP not running to detect untreated raw water flows entering WTP - this will require a FD to be written for Raw water. THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water Medium (8) (HNZ-5) | M - 8 | 2020-07-28 | 2026-12-17 |  | PE: 2024 - Raising the alarm requires an FD for the raw water to be written as there is no FD at present due to the plant being controlled by relay logic and not the PLC.
1003295 | Closed | Mt Crosby Holts Hill | Mt Crosby Holts Hill - Disinfection (Secondary) - Incorrect Ammonia Dose - Under dosing of ammonia. (Medium 8) (WQ Risk Treatment) | Planned Ammonia upgrade works for Holts Hill | M - 8 | 2021-08-12 | 2024-09-30 | 2024-09-12 | DWQ RA Review 12 Sep 24: Planned Ammonia upgrade works for Holts Hill [COMPLETED]
1003305 | Open | Supply System | Supply System - Redland Zone - Reservoir - Inadequate MixingPoor mixing in a reservoir leading to:- Pockets of reduced quality water.- Increase the possibility of nitrification.- Temperature issues.Medium (8) (WQ Risk Treatment) | Replacement of Mixers at Alexandra Hills Reservoirs 1,3,4 and 5 as well as Heinemann Road Reservoirs 2 and 3 as a priority due to mixing issues. | M - 8 | 2023-08-04 | 2025-10-31 |  | 04/12/24 - Work underway to install Wears mixers in Heinemann Road Reservoir 2 and 3. Failed Pax mixers have been removed. Reservoir cleaning for Res 2 and 3 is planned for mid Jan 2025 with new mixers being installed after that.
1003317 | Open | N/A | Develop a system to guarantee the water quality available to the tanker . Update to tankering procedure (WQ Risk Treatment) | Develop a system to guarantee the water quality available to the tanker. Update to tankering procedure | M - 8 | 2024-02-15 | 2025-10-31
1003329 | Open | Image Flat WTP | Tracking the fluoride upgrade at Image Flat. (WQ Risk Treatment) | Existing fluoride upgrade project will address most of the issue. Implementation anticipated by end 2025. | M - 9 | 2024-02-15 | 2025-12-01
1003335 | Closed | Supply System | Supply System - SWP - Bulk Pipeline - Gravity Feed Operation - Offline assets not properly isolated.Leading to out of specification treated water.Medium (8) (WQ Risk Treatment) | Recommendation for Major Projects to inform construction staff about transition of SWP to gravity feed potable water supply to residents at Beaudesert and the criticality of effective isolation of assets yet to be commissioned. This item is to remain open until gravity feed operation to Beaudesert is ceased and pipeline is commissioned. | M - 8 | 2023-12-07 | 2024-09-30 | 2024-07-25 | Email from CT on 04/12/23 - I can confirm that we will be effecting isolations on SWP in accordance with the updated First Water Plan and that these will be checked with SWP ops before we commission. 28/02/24 - KM sighted Lock Out Permit dated 02/02/24 which is still valid. CT: I confirm that First Water Operation is now complete to allow for commissioning of full scheme operation. Expected handover date end Sept 24.
1003453 | Open | Capalaba WTP | TCP-RW-A-10261 Risk Treatment: Box gutter roof on Reservoir 1 roof subject to intrusion. (WQ Risk Treatment) | TCP - Disinfection (primary) - Contamination by animals - Contamination of chemical dosing chamber and/or treated water tanks Medium (8) (TCP-27) | M - 8 | 2019-08-28 | 2025-12-30 |  | Roof replacement currently planned for delivery in at the end of 2025.
1003513 | Open | North Stradbroke Island WTP | TNS-RW-A-6562 Risk Treatment: Undertake upgrades to Coagulation CCP. (WQ Risk Treatment) | TNS - Coagulation - Incorrect lime dose/ Incorrect Coagulant dose. For Herring Lagoon (pre lime): Underdose of lime into raw water main leading to: - low alkalinity for coagulation - incorrect dosed water pH Overdose of lime into raw water main leading to: - incorrect dosed water pH Medium (8). (NSI-8 NSI-13) Risk Treatment (raised R.A review 2015 and DWQ Report to WTP Planning 2015 D14/149372): It is recommended that the coagulation process at NSI WTP is upgraded. This upgrade should consider: - paging of dosed water pH alarms to the Operator (Complete 2017) - interlock of WTP operation to dosed water pH alarms. This must include a full WTP HAZOP to ensure that all actions required to facilitate the interlock are identified and actioned, such that other unintentional adverse consequences are avoided (Complete Sep 2018) - feed forward control of coagulant dose - single set of alum dosing pumps (automatic changeover ‘duty’/’standby’ arrangement) that are capable of delivering the required dose across the range of flow and alum doses expected - flow meters on the alum dosing line, interlocked to WTP operation, such that the detection of no alum flow will shutdown the WTP - flow pacing of the alum dose to raw water flow meters on the inlet to each DAF train or installation of appropriate control such that the flow to the DAF basins is equal or known - relocation of the alum dosing points to immediately upstream of the inline rapid mixers Currently work to improve process issues at TNS are being investigated - inc those in this RWA. these are planned to be fast tracked. | M - 8 | 2019-04-24 | 2027-02-28
1003527 | Open | Hinze Dam WTP | THZ-RW-A-10398 Improvement Opportunity: Static mixer post ACH dose point would improve coagulation and clarifier performance. (WQ Risk Treatment) | THZ - Coagulation - Inadequate mixing Lack of mixing resulting in poor floc formation resulting in filter breakthrough Medium (5) (HNZ4) | M - 8 | 2019-09-03 | 2026-12-31
1003535 | Closed | Lowood WTP | Central Region- Somerset South- Lowood WTP- installation of UV to implement additional barrier to meet log removal requirements for protozoans (WQ Risk Treatment) | Project is in planning stage and delivery scheduled for 2021/ 2022 Project is underway with delivery expected to be finalised by Dec 24. | M - 8 | 2021-04-19 | 2025-04-30 | 2025-04-09 | Project completion and handover to Ops underway. POPT nearing completion. All HACCP documents updated and Critical Limits locked in. Any minor changes can be made before the project hands over to Ops without the need for MoC.
1003565 | Open | Supply System | Supply System - SRP - Reservoirs - Elevated water ageLong retention times leading to:- Potential for nitrification of chloramines and loss of residual.- Taste and odour issues.- Potential increase in bacteria.Medium (8) (WQ Risk Treatment) | Review operating philosophy of hybrid flows for the SRP | M - 8 | 2023-07-28 | 2025-12-31
1003567 | Open | Supply System | Supply System - Redland Zone - Reservoirs - Contamination by IngressDue to one or more of the following contaminants leading to out of specification treated water:- Vermin- Rain- Dust or other debrisHigh (12) (WQ Risk Treatment) | Roof replacement for Heinemann Road Reservoir 1. | H - 12 | 2023-08-04 | 2025-10-31 |  | 10/01/25 - Procurement issues. Expected to be completed by end of 2025.
1003591 | Closed | Landers Shute WTP | Investigate additional ongoing continuous improvements such as- introduction of interlocking mechansim on filters that closed the outlet instead of the inlet valve, introduction of a secondary critical limit at 1 NTU for >1 minute on individual filters, introduction of 95th percentile critical limit on filtered water turbidity, introduction of interlock on dosed water pH. (WQ Risk Treatment) | NB the interlocking of critical limits is currently managed under the MOC# 1268 Interlocks being worked on - enterprise risk treatment plan tracker - JK - FZ is owner. HACCP function blocks - OTE in conjunction with the CSM. Presently - In the event of breakthrough: inlet will close and an autobackwash will begin, taking the filter offline; however - the volume of the filter will still pass through the broken through filter should this occur. Ideally, the outlet should close and the filter should drain to waste. Flashmixer pH - Out of 2198 samples, the minimum was 6.1 units the 5th percentile was 6.5 (6.5, 6.5) units, the mean was 6.7 (6.7, 6.7) units, the 95th percentile was 6.9 (6.9, 6.9) units and the maximum result was 7.3 units. σ = 0.135 (0.131,0.139). Data:Jan-2015 to Jan-2021. 95% Confidence Intervals in brackets. - Filtered Water Turbidity - Out of 2190 samples, the minimum was 0.011 NTU the 5th percentile was 0.04 (0.04, 0.04) NTU, the mean was 0.071 (0.07, 0.072) NTU, the 95th percentile was 0.12 (0.11, 0.12) NTU and the maximum result was 0.55 NTU. σ = 0.0266 (0.0258,0.0274). Data:Jan-2015 to Jan-2021. 95% Confidence Intervals in brackets. There is a common outlet channel. No individual flow meters. Filter control valve position is displayed on the SCADA. There is a setpoint for filter control rate which determines if filters come on or off. Filter rate control mode is auto or manual. All filters that are to be backwashed go offline and into a queue. Further - investigate the options to include alarming on variance or stdev of trends, as this will give the plant the capability to detect flatlining events (i.e. where the instrument is producing a false superstable reading for any reason). Recent Audit (Task 19145) conducted on 16/2/21 by KD identified issue with flatline trend on filter 5. | M - 8 | 2021-03-09 | 2024-12-01 | 2025-01-24 | Actions are being considered and actioned within the Strategic Business Case - HACCP Northern Interlock Package D24/320180
1003601 | Open | Ewen Maddock WTP | TEM - Raw Water Abstraction Rain event in catchment Contaminant load exceeds treatment capacityMedium (8). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): Undertake HBT Tier 1.5 Assessment to confirm risk | M - 8 | 2020-06-03 | 2026-01-17
1003607 | Closed | Ewen Maddock WTP | TEM - Coagulation Incorrect lime dose Coagulation process failureMedium (8). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): Review of pre lime dosing system to include the following: - Not use raw water as service water for pre-lime (still in use - because its prior to treatment) - Change lime makeup water to plant service water instead of raw water (still in use - because its prior to treatment) - Pressure switches on lime makeup water (MB to check) - Auto shutdown on lime system failure (In place - close out) | M - 8 | 2020-06-03 | 2026-01-17 | 2025-04-09 | These actions have all been completed, or the change was deemed not necessary.
1003609 | Open | Supply System | Supply System - All Zones - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water.Medium (8) (WQ Risk Treatment) | Supply System - All Zones - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water. Medium (8) (WQ Risk Treatment) | M - 8 | 2023-07-24 | 2027-12-31
1003611 | Open | Supply System | Supply System - All Zones - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water.Medium (8) (WQ Risk Treatment) | Either give mains back to Retailers, or retrace another main (real bulk transfer). Determine risk to business and decide course of action. | M - 8 | 2023-07-24 | 2027-12-31
1003613 | Open | Supply System | Supply System - Brisbane Zone - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water.Medium (8) (WQ Risk Treatment) | Supply System - Brisbane Zone - Direct connections to bulk water main (known and unknown). Backflow from direct connections to Seqwater Bulk Mains leading to contamination of treated water.Medium (8) (WQ Risk Treatment) Brisbane CC Mt Coot-tha Botanical Gardens. Reticulation Connections - Mt Crosby reticulation connections, Brighton. | M - 8 | 2023-07-24 | 2028-12-28 |  | 20/02/25 - Significant work is required to determine where there are direct connections and there are resource constraints currently to complete this work.
1003621 | Closed | Ewen Maddock WTP | TEM - Supernatant Return Change in raw water source Contamination of treated waterMedium (8). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): ' VSD for the separated water return pumps the return water tank | M - 8 | 2020-06-03 | 2026-01-17 | 2025-04-09 | These actions have all been completed, or the change was deemed not necessary.
1003633 | Open | Hinze Dam WTP | THZ-RW-A-15547 Risk Treatment from RA - investigate the if the BOHT and its operation achieve any LRV for HBT. (WQ Risk Treatment) | The 2024 Hinze Dam WTP Source Water Assessment and the 2022 Hinze Dam WTP HBT Assessment indicated there is shortfall in treatment which requires process improvements and possibly additional pathogen barriers, However, the BOHT and its operation were included in these assessment and this may achieve some pathogen LRV's which havent been accounted for. this Risk treatment is targeted at investigating LRV achieved by the BOHT and improvements in its operation as well as the other plant processes. | M - 8 | 2024-02-06 | 2030-02-10 |  | Ss discussed with JS (11/2/2025) this will be extended 5 years. This will allow time to consider method validation. Note: if BOHT/source water operations could be shown to effectively reduce the required pathogen LRV treatment and operations controlled to reliably claim this, this would make this processes step a CCP/primary barrier (with the associated monitoring, process controls, alarms and interlocks requirements).
1003639 | Open | Moogerah Dam WTP | TMG-RW-A 10413: Risk Treatment: Investigate opportunities to address clarifier sludge build up requiring manual draining and hose out on a regular basis. (WQ Risk Treatment) | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-16) | M - 8 | 2019-09-05 | 2026-02-28 |  | Current management of desludging from the clarifiers: 1. The Operators are doing daily visual checks on the clarifier and desludge it every 2 weeks. 2. There hasn’t been any incident in the last 4-5 years of floc being carried over to filters, causing filtered water turbidity exceedances. 3. Automation of desludging will involve new valve (either electrically or air actuated), flowmeter, SCADA integration, additional I/O’s (if required) and relevant document updates. 4. I will reach out to MD re this to get a risk assessment done, so that it gets into the ARMA.
1003651 | Open | Ewen Maddock WTP | TEM -Supernatant Return Stormwater entering the process Contamination of treated waterMedium (8). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): Online turbidity and pH instruments to be installed on supernatant return line | M - 8 | 2020-06-03 | 2026-01-17 |  | commissioning occurring this year (2025)
1003653 | Closed | Ewen Maddock WTP | TEM -Ozone (intermediate) Contamination incident - accidental/intentional Introduction of pathogensMedium (8). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): 'Erect contamination signage on/at the BAC filters. Work instructions for working over the BAC should also consider the risk of accidental contamination | M - 8 | 2020-06-03 | 2026-01-17 | 2025-04-09 | Cover over BACs now - this action can be closed.
1003655 | Closed | Ewen Maddock WTP | TEM -Ozone (intermediate) Contamination incident - accidental/intentional Introduction of pathogensMedium (8). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): Investigate further prevention of post barrier contamination to the top of the BAC filters (such as ingress, animals, etc). Covering BACs completely is challenging because of the residual ozone present in the atmosphere. Ozone is heavier than air and invisible to the eye. People and animals can become intoxicated quickly if there is too much ozone in the air. However, there is a potential for contamination of the water on top of the BAC filters (water that has just been ozonated). BAC filters do not provide any log reduction credits for protozoa and as such effectively, anything that contaminates the ozonated water prior to BAC filtration could potentially make its way through to the treated water and the public. There are no further barriers to protozoan. Chlorine disinfection does not get any impact on protozoan parasites. Therefore it is imperitive to - ensure there is no ingress points to the ozonated water prior to BAC and provide an additional treatment barrier for protozoa downstream of the BAC. (not in place yet. but speaking to extra protozoan barriers ala other protozoan limiting hazard risk treatments, as well as reducing the likelihood of introducing contamination to the BACs) | M - 8 | 2020-06-03 | 2026-01-17 | 2025-04-09 | Cover over BACs now - this action can be closed.
1003661 | Closed | Molendinar WTP | TMO-RW-A-10333 Improvement Opportunity: Review supply configuration to Southport West zone to address high pressure issue in City of Gold Coast distribution system. Gravity valve from CCT does not interlock therefore must remain closed and isolated. (WQ Risk Treatment) | TMO - Disinfection (primary) - Failure or incorrect operation of a bypass valve Failure or operation (opening) of CCT gravity main valve which does not interlock Medium (5) (TMO-25) Improvement Opportunity (raised R.A review 2017): Review supply configuration to Southport West zone. Southport West zone is direct feed via gravity valve or direct feed when treated water pumps running if gravity valve is closed (supply to Southport West backfeeds from Mol 4 when pumps offline). Due to the location of the Disinfection analyser being at the outlet of the CCT if/when these interlock there is a large volume of water in the CCT that will require re-treatment or wasting resulting in a loss of supply to the Southport West zone over that time. Under the current arrangement (at the time of the R.A) the zone was being fed direct when the treated water pumps were running however this results in reportedly high pressures in the CoGC system increasing risk of mains break. An ideal configuration would be to supply the Southport West zone from the outlet of the onsite Reservoirs. | M - 8 | 2019-09-02 | 2025-03-02 | 2024-12-19 | Improvement Opportunity (raised R.A fluoride HAZOP 2018): connecting a pipe from Reservoir 6 outlet to the existing Southport West Reservoir pipeline will be now investigated as an alternative. Process Engineering team to progress this alternative option. Note this option was proposed and discussed in 2010. Update R.A 2019: Short term - WTP operations to tag out valve. Long term: ION00534: Supplying treated water to GCCC from the outlet of Reservoir No.6 will involve modification to outlet pipe, installation of valve, changes to SCADA and control system. Update 28/05/2020: Images of Molendinar gravity main valve depicting the valve as being tagged out Supply risk, not water quality - note there is no longer a gravity supply from Mol (now all rising).
1003669 | Closed | Supply System | Heinemann Road Reservoirs - Locate drawings of the chemical dosing arrangement, the sample return water or instrument water draw arrangements in Reservoirs 2 & 3. If they are not available,new drawings need to be done. (WQ Risk Treatment) | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | M - 8 | 2020-01-09 | 2025-03-31 | 2025-03-26 | ION1382 raised to address unavailability of drawing - not in their scope - Regional Ops Manager approved altering ER7 to address PID 26/03/25 - Archive box containing Heinemann Road Chlorine Dosing Ops manuals was delivered to ICON and documents reviewed to see if any relevant information or documents could be found. The required detail was not in the archive box. New mixers are being installed in Heinemann Road Reservoirs and the dosing arrangement is to be changed. Instead of dosing line running across the bottom of the reservoirs, they will be fed into the mixers which will assist with better mixing. Drawings will be provided with the mixers detailing dosing lines. This action is to now be closed.
1003677 | Open | Kooralbyn WTP | TKO-RW-A 10446 Risk Treatment: Assessment of the Kooralbyn WTP treatment capability indicates that the process has the capability to achieve the following 3.5 protozoa log reductions. This represents a protozoa log reduction shortfall of up to 2.0 under the HBT framework. Refer D15/114146. Additional protozoa treatment required i.e UV Disinfection (WQ Risk Treatment) | TKO - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) (TKO-15) TKO - Coagulation - Incorrect coagulant dose Underdose of alum resulting in contaminated treated water including incorrect dosed water pH Medium (8) (TKO-15) TKO - Coagulation - Incorrect CO2 dose Underdose (absence) of CO2 causing high dosed water pH resulting in contamination of treated water Medium (8) (TKO-15) TKO - Flocculation and Settling - Carryonver of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) (TKO-15) TKO - Flocculation and Settling - Failure or incorrect operation of a bypass valve Failure or incorrect operation of a clarifier bypass valve Medium (8) (TKO-15) TKO - Media Filtration - Filter breakthrough Filter breakthrough Medium (8) (TKO-15) | M - 8 | 2019-09-05 | 2026-05-30 |  | This is part of the KKR UV project which ahs been started and stopped by the business several times. Currently a planned activity time TBC.
1003685 | Open | North Pine WTP | TNP- Raw Water Abstraction- Cyanobacteria bloomFor Lake Samsonvale;Blooms of cyanobacteria and other problem algae that could result in treated water contaminationLow (2). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): long term planning to improve north pine PAC in APMP | M - 8 | 2020-02-19 | 2026-02-11
1003695 | Open | Amity Point WTP | TAP-RW-A-11280 Risk Treatment: Introduce protozoa treatment at Amity Point WTP to meet Category 3 minimum pathogen log reduction requirements. (WQ Risk Treatment) | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk Medium (8) Target risk (5) | H - 10 | 2020-01-23 | 2027-06-30 |  | MT 23/6/2025: A technical options paper has been written and will be issued for review shortly. This has identified a potential preferred option which will allow for progression of the design.
1003697 | Open | Point Lookout WTP | TPL-RW-A-11303 Risk Treatment: Update HACCP plan to include oPRP for monitoring Bore asset integrity. Current Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) includes steps 19-21 to check for leaks on pipeline assets which can be referenced. Install online raw water turbidity monitoring to detect bore integrity failure and prevent impacts to CCT from turbidity. (WQ Risk Treatment) | TPL - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk: Medium (8) Target Risk: Medium (5) | H - 10 | 2020-01-24 | 2026-06-30 |  | Raised R.A 2017: Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity (raised HACCP internal audit 2016) Upgrade R.A 2019: ION raised. Ingress issued fixed on production bores 2018/2019. Ongoing inspections to be addressed. Note: Bore 1 offline at time of R.A 2019 due to failed bore casing resulting in high turbidity. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Update HACCP plan as oPRP and Risk Assessment as preventative measure. Update 15/05/2020: ION01368 has been raised to install online raw water turbidity monitoring for the purpose of detecting abstraction of contaminated ground water that exceeds treatment capacity. Review on whether the raw water turbidity monitoring proposed for bores will ever occur or whether the risk will be tolerated. Reassigned to new DWQ Advisor South - DG DG - Risk may become acceptable with increased treatment (UV installation). to be reviewed, otherwise continue efforts for turbidity analysers
1003703 | Open | Lowood WTP | Central Region- Somerset South- Lowood WTP- additional clarifier to mitigate supply and water water quality risks (WQ Risk Treatment) | Additional clarifier is in delivery stage change of action ownership to DH Currently in early planning/design stage - date pushed out to end of FY 27/28 to allow for project completion. | M - 8 | 2021-04-19 | 2028-06-30
1003715 | Open | Supply System | Supply System - Brisbane Zone - Incorrect Ammonia Dose Under dosing aqueous ammonia NH3(aq) leading to out of specification treated water Medium (8) (WQ Risk Treatment) | Review low flow conditions for dosing at Aspley WQMF. Investigate sizing of ammonia dosing pumps to ensure adequate dosing at low levels. | M - 8 | 2023-07-20 | 2026-12-31 |  | 20/06/25 - These actions are currently sitting with PE for further investigation as is degassing valves for Ammonia and chlorine dosing.
1003717 | Open | Supply System | Supply System - Brisbane Zone - Incorrect Ammonia DoseOver dosing of aqueous ammonia NH3(aq) leading to out of specification treated waterMedium (8) (WQ Risk Treatment) | Investigate sizing of ammonia dosing pumps to ensure adequate dosing at low levels. MOC and EAR to be raised. | M - 8 | 2023-07-20 | 2026-12-31 |  | 20/06/25 - This action is currently sitting with PE for further investigation.
1003741 | Open | Supply System | Supply System - Disinfection (secondary) - Incorrect chlorine doseUnder dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water.High (12) (WQ Risk Treatment) | NPI Supply Zone 1. Conduct Process Assessment of Noosa Connection dosing system. | H - 12 | 2020-07-20 | 2028-12-31
1003765 | Open | Supply System | Supply System - Brisbane Zone - Incorrect Ammonia DoseUnder dosing aqueous ammonia NH3(aq) leading to out of specification treated waterMedium (8) (WQ Risk Treatment) | Review low flow conditions for dosing at Aspley WQMF. | M - 8 | 2023-07-20 | 2026-07-31
1003767 | Open | Supply System | Supply System - NPI Zone - Bulk Pipeline - Contamination due to pipe depressurisationIngress of contaminants through:- Pipe joints.- Air valves.- Leaking valves and hydrants.- Aging infrastructure.- Scours.Ingress caused by loss of pressure in main during:- Pipe burst.- Pipe repairs.- Very high flows (e.g. fire fighting) .- Incorrect isolation for maintenanceMedium (8) (WQ Risk Treatment) | Investigate the valve pit inspection programs that it includes the effectiveness of drainage pits. | M - 8 | 2023-07-25 | 2026-12-31
1003769 | Open | Supply System | Supply System - Redland Zone - Bulk Pipeline - Contamination due to pipe depressurisationIngress of contaminants through:- Pipe joints.- Air valves.- Leaking valves and hydrants.- Aging infrastructure.- Scours.Ingress caused by loss of pressure in main during:- Pipe burst.- Pipe repairs.- Very high flows (e.g. fire fighting) .- Incorrect isolation for maintenanceMedium (8) (WQ Risk Treatment) | Implement automated controls for the valves between NSI and Serpentine Creek (MoC #1928). | M - 8 | 2023-08-04 | 2026-12-31 |  | 08/07/25 - Functional Description B for this is currently being updated. Backup code for NSI has also been provided.
1003781 | Open | Point Lookout WTP | TPL-RW-A 11302 Risk Treatment: Introduce protozoa and virus treatment at Point Lookout WTP to meet Category 3 minimum pathogen log reduction requirements. (WQ Risk Treatment) | TPL - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk: Medium (8) Target Risk: Medium (5) DG 2024: the 2023 Source water assessment has determined the source water is a Catchment category 3 therefore requiring an even higher level of protozoa, virus and bacteria treatment. | H - 10 | 2020-01-24 | 2025-08-30 |  | Raised R.A 2017: Undertake Pathogen Assessment of NSI Township WTPs and review of preventative measures and monitoring for managing risk of abstraction of contamination groundwater is required including condition of bore casings, bore location in relation to flood level, condition of seals on above ground assets Update R.A 2019: Based on having a shallow aquifer and essentially no control over the confines of the aquifer there is an assumed level of interaction whether it be continuous or intermittent therefore Point Lookout WTP is likely to be Source Category 2 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 3.0 LRV; protozoa 2.5 LRV under WSAA HBT Manual however this assessment has not formally been done. Protozoa treatment would be required in the form of UV disinfection to achieve protozoa LRV if Category 2 confirmed. Note: Bore 1 offline at time of R.A 2019 due to failed bore casing resulting in high turbidity. UV project is progressing
1003783 | Open | Supply System | Supply System - EPI - Whole of System Decommissioned or offline assets not properly isolated eading to out of specification treated water.Medium (8) (WQ Risk Treatment) | Investigate removal of Kimberley Park Temporary tank. Determine business position on the NSI Booster Pump Station and either decommission or start maintaining these assets. | M - 8 | 2023-08-02 | 2027-12-31 |  | 05/08/25 - The risk of the NSI booster pumps is lower now that they have been confirmed as isolated and locked out.
1003787 | Open | Supply System | Supply System - Brisbane Zone - Decommissioned or offline assets not properly isolated. Leading to out of specification treated water.Medium (8) (WQ Risk Treatment) | Add decommissioned equipment layer within GIS. | M - 8 | 2023-07-24 | 2030-12-31
1003797 | Open | Mt Crosby East Bank WTP | Eastbank WTP - Supernatant Return - Supernatant return quality exceeds treatment capacity.Supernatant return volumes exceed treatment capacity leading to Protozoa in the treated water.High (12) (WQ Risk Treatment) | 1). It should be determined if it would be advantageous to fit interlocks such that the supernatant pumps cannot run when the raw water pumps are offline or if the turbidity critical limit is triggered - Technical Specialist has identified that this would be advantageous. 2). Consideration should be given to undertaking a mass balance of polyacrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for acrylamide monomer in the treated water. 3). VSDs is to be installed on the supernatant return pumps which in conjunction with raw water flow meters will facilitate improved control to ensure that the supernatant to raw water ratio does not exceed 10% of the raw water flow rate. 4) Make modifications and improvements to the current supernatant return process to minimise the impact to stage 3 and 4 basins. | H - 12 | 2020-07-15 | 2027-12-31 |  | DWQ RA Review 12 Sep 24: - It should be determined if it would be advantageous to fit interlocks such that the supernatant pumps cannot run when the raw water pumps are offline or if the turbidity critical limit is triggered - Technical Specialist has identified that this would be advantageous. Update: Been capturedEast Bank Solids Handling Upgrade Project - Unable to waste superntant return water to Holts Hill storages. Only centrate. Exception is if temporary pumping set up is established. No fixed pumps and pipework. Important to be able to waste supernatant during extreme dirty water events when treatment is difficult. - Consideration should be given to undertaking a mass balance of polyacrylamide based polymer being used across the WTP under various operating scenarios, to ascertain if there is any potential of exceeding the ADWG health limit for acrylamide monomer in the treated water.[Chect with BH - change in floc aid from SEP to PWG products may have resolved this issue.] - VSDs is to be installed on the supernatant return pumps which in conjunction with raw water flow meters will facilitate improved control to ensure that the supernatant to raw water ratio does not exceed 10% of the raw water flow rate. - Two train project to make modifications and improvements to the current supernatant return process to minimise the impact to stage 3 and 4 basins.
1003807 | Open | Noosa WTP | TNO- Coagulation Incorrect lime dose Non-optimised coagulationMedium (8). (due to crypto short fall) (WQ Risk Treatment) | Risk Treatment (raised R.A 2019): investigate lime and alum control with focus on start up and lake only water investigate poly as a floc/settling aid install alum dosing flow meter to verify alum dose investigate CO2 dosing to enable formation of calcium carbonate to a higher degree of reliability includine reactivator importance in coag pH validation and control | M - 8 | 2020-02-20 | 2026-02-11
1003809 | Open | Hinze Dam WTP | THZ-RW-A 10397 Risk Treatment: Although this is not known to have occurred at Hinze Dam WTP there is occurrences of coag dosing pipe breakages at other WTPs. There is currently a coagulant flow switch interlocked to WTP operation however coag flow monitoring interlocked to WTP operation is required. (WQ Risk Treatment) | THZ - Coagulation - Incorrect coagulant dose Underdose of ACH resulting in contaminated treated water Medium (8) (HNZ-5) | M - 8 | 2019-09-03 | 2025-12-31 |  | Update R.A review 2017: Confirmed as viable WTP and will continue operating. Project will be pursued by Process Improvement Specialists based on current understanding that WTP will remain for the foreseeable future. To be included in Minor Works upgrade 17/18. Note Control System is very limited in terms of adding any further alarms or monitoring. Sludge upgrade project would trigger upgrade of PLC. Update R.A review 2019: Not delivered at time of R.A. Update 9/07/2021: Sen. DWQ Advisor Sth: wait for outcome of Moogerah and Maroon Dam coag flow meter projects. Similar flow rate and project currently in delivery. Issues with measuring such low flow rate may or may not be overcome. Update 21/09/2021: Senior DWQ Advisor Continuous Improvement to escalate ION184 or raise a new ION to install ACH coag flow meter. In the short term identify options to get existing signals available on the ACH dose pump into SCADA that can be used as the HACCP critical limit to interlock the WTP. Update Hinze Dam WTP HACCP Wall Chart and HACCP Plan Validation 3.2 to document signal in use for this HACCP critical limit. Update 29 NOV 21: Management of this risk to be reviewed on-site and then discussed at next HACCP team meeting (Mar 22). Investigate current condition, confirm need for flow meter over switch to control risk (both should indicate flow when offline - DG to investigate) and facilitate flow switch replacement for flow meter if needed.
1003811 | Open | Rathdowney WTP | TRA-RW-A 10499 Risk Treatment: Pathogen log reduction review outcome was need for UV disinfection to meet protozoa log shortfall. Refer D15/114408. (WQ Risk Treatment) | TRA - Raw Water Abstraction - Rain event in catchment Intake of contaminated water that could potentially result in contaminated treated water Medium (8) TRA - Supernatant Return - Superntatnt return quality exceeds treatment capacity Supernatant return water exceeds the treatment capacity of the plant due to: - rate of return >10% (pathogen risk) - turbidity > HACCP limits (pathogen risk) - insufficient poly dose Medium (8) TRA - Coagulation - Incorrect coagulant dose Underdose of ACH (dosed neat) including loss of carrier water Or Ineffective coagulation due to elevated pH High (12) TRA - Coagulation - Incorrect coagulant dose Overdose of ACH (dosed neat) Medium (8) TRA - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - incorrect flocculation speed Medium (8) TRA - Media Filtration - Filter breakthrough Fitler breakthrough Medium (8) TRA - Media Filtration - Build up of solids leading to elevated turbidity High turbidity filtered water from backwash water tank used to backwash filter leading to filter breakthrough when filter back online Medium (8) | M - 8 | 2019-09-05 | 2025-12-31
1003813 | Closed | Dunwich WTP | TDU-RW-A 11292 Risk Treatment: Undertake Health Based Target assessment of NSI Township WTPs and upgrade WTPs accordingly. (WQ Risk Treatment) | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: Risk: Medium (8) Target Risk: Medium (5) - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned | M - 8 | 2020-01-24 | 2025-12-31 | 2024-11-22 | Undertake Pathogen Assessment of NSI Township WTPs and review of preventative measures and monitoring for managing risk of abstraction of contamination groundwater is required including condition of bore casings, bore location in relation to flood level, condition of seals on above ground assets Update R.A 2019: Based on having a shallow aquifer and essentially no control over the confines of the aquifer there is an assumed level of interaction whether it be continuous or intermittent. There is also point source hazards such as septic systems on Rainbow Cres. Therefore Dunwich WTP, when using Bore 1, 2, 4 is likely to be Source Category 3 having minimum pathogen log reduction requirements bacteria 5.0 LRV; virus 4.0 LRV; protozoa 3.5 LRV under WSAA HBT Manual however this assessment has not formally been done. This would likely increase to Category 4 if Bore 3 were to be reinstated or based on other known point source risks such as septic system and cattle. Refer Risk Treatment Disinfection (primary) for improvements to C.t. Protozoa treatment required in the form of UV disinfection to achieve protozoa LRV. Update 26/03/2020: Pathogen log shortfalls being addressed under TDU – Dunwich WTP Secondary Disinfection Preliminary BC ADWG method for SWA undertaken in 2023 and confirm source as Category 4. project is in delivery to increase treatment accordingly. Completed in 2023, see D23/55889
1003815 | Open | Dunwich WTP | TDU-RW-A 11293 Risk Treatment: Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity to detect contamination of aquifer due to bore failure or other pathway. (WQ Risk Treatment) | TDU - Raw Water Abstraction - Contamination incident - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; Bore 4; that exceeds treatment capacity due: Risk: Medium (8) Target Risk: Medium (5) - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headwork's. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, land use and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Bore 3 - isolated due to contamination from nearby residential septic system Bore 5 - decommissioned | H - 10 | 2020-01-24 | 2025-12-31 |  | Raised R.A 2017: Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Upgrade R.A 2019: ION raised. Ingress issued fixed on production bores 2018/2019? Ongoing inspections to be addressed. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Period inspections of ingress Closed. Update 15/05/2020: ION01367 has been raised to install online raw water turbidity monitoring for the purpose of real time detection of contaminated ground water that exceeds treatment capacity. Facility risk review has stated "Score is too low to bring into program". raw water monitoring is not likely to detect contamination. Following discussions with JS we determined the following - Dunwich WTP is in the process of being upgraded to treat category 4 source water. This will be delivered in the coming 2 years. At this point raw water monitoring will not be required. After delivery close out action.
1003817 | Open | Mt Crosby East Bank WTP | East Bank WTP - Whole of System - Loss of SCADA system or loss of PLC (Medium 8) (WQ Risk Treatment) | Upgrade of system platform across all sites. | M - 8 | 2021-08-12 | 2025-12-31 |  | Upgrade of system platform across all sites. Still progressing. EB mud plant still to be done.
1003821 | Open | Supply System | Supply System - Brisbane Zone - Reservoir - Elevated water age.Long retention times leading to:- Potential for nitrification of chloramines and loss of residual.- Taste and odour issues.- Potential increase in bacteria.High (12) (WQ Risk Treatment) | Historian (when implemented) to develop metric for water age of reservoirs. | M - 8 | 2023-07-19 | 2025-12-31 |  | 04/12/24 - This will be looked at after the implementation of PODMS which is need for this project to be completed.
1003823 | Open | Supply System | Supply System - Gold Coast/NIP - Reservoir - Contamination by Ingress Due to one or more of the following contaminants leading to out of specification treated water:- Vermin- Rain- Dust or other debrisMedium (8) (WQ Risk Treatment) | Investigate replacing box gutters at Molendinar 3 and 4 reservoirs. | M - 8 | 2023-07-31 | 2025-12-31
1003825 | Open | Supply System | Supply System - Redland Zone - Whole of System - Loss of powerLoss of power impacting treated water qualityMedium (8) (WQ Risk Treatment) | Investigate installation of a generator to run Heinemann Rd PS (can be trailer mounted) including shelter. | M - 8 | 2023-08-07 | 2025-12-31 |  | Included in the Supply System Facility Risk Register - RTP 161
1003831 | Open | Noosa WTP | TNO- Media Filtration Filter breakthrough Potential contamination of treated waterMedium (8). from crypto short fall (WQ Risk Treatment) | Risk Treatment (raised R.A 2019): Install appropriate instrumentation, monitoring and control systems to enable effective monitoring and control of filtration. Install /improve filter to waste option (2021: filter to waste operational on timers) Investigate poly dosing as a filter-aid. - potential to introduce air scour (2021: completed) | M - 8 | 2020-02-20 | 2026-02-11 |  | Raised 2021: link to 11397 Long term planning should be looking to add another cryptosporidium barrier to meet the required log credits under the HBT assessment. Contnued development (2021 ra) (create new RW for higher priority) - roll into a tier 1.5 assessment /QMRA for noosa (done before next RA (so <2 years from july 2021)
1003861 | Open | Kirkleagh WTP | TKR- Raw Water Abstraction Contaminant load exceeds treatment capacityMedium (8). (due to crypto short fall) (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): Consider re-evaluating/conducting HBT tier 2/1.5 assessment to verify risk and investigate requirements for upgrades. Installation of UV is in the program to be delivered 2022 as part of the KKR project. | M - 8 | 2020-09-02 | 2026-02-11
1003863 | Open | Jimna WTP | TJI- Raw Water Abstraction Intake of raw water that exceeds the treatment capacity of the plant affecting treated water quality.Medium (8). (due to crypto short fall) (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): An additional Prozoa Treatment barrier is required to address the shortfall against the HBT tier 1 assessment. Alternatively investigation into a tier 1.5/2 assessment to verify the risk | M - 8 | 2020-09-02 | 2026-02-11
1003867 | Open | Kilcoy WTP | TKY -Whole of System Contamination incident - accidental/intentional Intentional and accidental contamination - Medium (6). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): consider ways to alert operator to unauthorised access to the pontoon | M - 8 | 2020-06-03 | 2026-04-21
1003871 | Open | Image Flat WTP | TIF - Raw Water Abstraction Rain event in catchment Increased contaminant loads due to wash-in from the catchments, resulting in contaminated treated waterHigh (12). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): The plant is difficult to operate, thus the likelihood of failure is higher, leading to the higher risk score. Whilst historical data shows the operators have been able to run the plant effectively, there is grave concern about the ongoing operability of particularly the coagulation and filtration barriers. Therefore, an additional Protozoa Treatment barrier is required to address the shortfall against the HBT tier 1 assessment. All sources are HBT Category 4 and so source selection alone is not good enough to mitigate the shortfall. Consideration should be given to -> Quantitative/tier 2 HBT assessment -> real-time water quality and flow monitoring of raw water sources. This will give the operators the ability to chose the most treatable source and consequently mitigate the associated hazards. If the operators had the capacity to see the change in the river in real time, they could move to Wappa, which has some buffer from the rain, or Poona, if manganese and taste and odour are accounted for. -> Lime dosing system improvement to account for colour and alkalinity from the river and wappa ->Alum Mixing improvement | M - 8 | 2020-06-03 | 2026-04-27
1003873 | Open | Image Flat WTP | TIF - Raw Water Abstraction Change in raw water source Contaminant load exceeds treatment capacity (T&O)Medium (9). (WQ Risk Treatment) | Risk Treatment (raised R.A 2020): There is a risk around feed from Wappa Dam direct to plant due to issues with Mn. Valves are physically locked and require a manual changeover to access the Wappa source. Source selection procedures consider the level of all storages and consideration of depth samples on dams is taken into account to assess WQ in conjunction with catchments, intake weir and dams. Therefore, consideration to be given to taste and odour treatment improvements (there is an existing project in place to upgrade PAC dosing plant, but this will only assist in operatability and not in the reduction of TO) and manganese treatment options (there is a BC proposed for reinstating potperm dosing - however it is unlikely to go ahead due to budget constraints). Manganese treatment options would greatly improve the operatability of the plant as if manganese could be dealt with effectively during a TO bloom then the sources can be switched to deal with the manganese. This is currently unavailable and as such most of the time the all of sources cannot be treated effectively | M - 9 | 2020-06-03 | 2026-04-27
1003897 | Open | Supply System | Supply System - Brisbane Zone - Decommissioned or offline assets not properly isolated. Leading to out of specification treated water.Medium (8) (WQ Risk Treatment) | Investigate removal of decommissioned assets. Assets include: Pipe over Mt Crosby Road at Ugly Gully (determine ownership). Camerons Hill Booster PS isolated but not properly decommissioned. Pump 4 and 5 at Stones Road isolated but not decomissioned. 2 offtakes at My Crosby Road - old connection to lockbar main. | M - 8 | 2023-07-24 | 2026-03-31
1003903 | Open | Landers Shute WTP | Investigate options for control of biomass growth in filters. - pre ozonation replacement project including prefilter chlorine - project underway - plant trials underway. Still in asset planning. (WQ Risk Treatment) | Investigate options for control of biomass growth in filters. - pre ozonation replacement project including prefilter chlorine - project underway - plant trials underway. Still in asset planning. (WQ Risk Treatment) | M - 8 | 2021-12-14 | 2026-12-14
1003905 | Open | Landers Shute WTP | Investigate options for collection of chemical waste from site labs. (Complete) install turbidity and pH instrument on return water line. ( see ION https://waternet.corporate.local/forms/Pages/ION.aspx?formId=458)Improvement to stop >10% seperated water return. MOC: https://waternet.corporate.local/forms/Pages/ION.aspx?formId=479 ADM - mass balance acrylamide - potential for contamination (WQ Risk Treatment) | Investigate options for collection of chemical waste from site labs. (Complete) install turbidity and pH instrument on return water line. ( see ION https://waternet.corporate.local/forms/Pages/ION.aspx?formId=458)Improvement to stop >10% seperated water return. MOC: https://waternet.corporate.local/forms/Pages/ION.aspx?formId=479 ADM - mass balance acrylamide - potential for contamination | M - 8 | 2021-12-14 | 2026-12-14
1003929 | Open | Dunwich WTP | TDU-RW-A 11296 Risk Treatment: install solid adequate cover on top of media filter. (WQ Risk Treatment) | TDU - Media Filtration - Contamination by ingress Contamination of Media Filter Risk: Medium (8) Target Risk: Medium (5) | M - 8 | 2020-01-24 | 2026-06-15 |  | DG investigating current condition. Given current works focusing on limestone bed before the filter this is unlikely to progress until after the limestone work.
1003937 | Open | Amity Point WTP | TAP-RW-11281 Risk Treatment: Update HACCP plan to include oPRP for monitoring Bore asset integrity. Current Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) includes steps 19-21 to check for leaks on pipeline assets which can be referenced. Install online raw water turbidity monitoring to detect bore integrity failure and prevent impacts to CCT from turbidity. (WQ Risk Treatment) | TAP - Raw Water Abstraction - Abstraction of contaminated surface water from bore Abstraction of contaminated groundwater (microbiological) from Bore 1; Bore 2; that exceeds treatment capacity due to: - Storms leading to unusual hydraulic connectivity driving short-circuiting. - Floods leading to overtopping of bore headworks. - Over-abstraction from the aquifer leading to loss of pressure or reduced groundwater depth. - Reduced pressurisation of the aquifer due to reduced rainfall charging and/or over-abstraction. - Contamination of the aquifer via other bores or earthworks entry pathways. - Mechanical failure of well casings or cable entry seals on production bores. - Changes in development, landuse and activity near bores leading to aquifer pollution. - Contamination of bores during maintenance and lifting of bore pumps Risk Medium (8) Target risk (5) | M - 8 | 2020-01-23 | 2026-06-30 |  | Raised R.A 2017: Develop an oPRP for monitoring Bore asset integrity as the current checks are only electrical in nature. Bore pumps are run to failure and replaced as required. This approach was based on the difficulties in lifting and inspecting pumps and the pump faults that would follow a pump lifting activity. Lifting pumps can also have potential to introduce contamination. Consideration should be given to include appropriate continuous monitoring of raw water e.g turbidity, pH and conductivity (raised HACCP internal audit 2016) Upgrade R.A 2019: Ingress issued identified. ION 00237 raised. Identified Issues resolved Jan 2019 by Operations Maintenance team. Ongoing inspections of bores (and all WTP assets) to be included in CIS routine work orders. Inspection criteria to be specific as per reservoir inspections checklist. Progression of UV disinfection to treat for hazards is preferable to installing additional online monitoring as standard online monitoring techniques is unlikely to be sensitive enough to detect a surface hazard and ground water interaction. Update 17/04/2020: Copy of Work order obtained. Maintenance Preventative Work Order BNS S1 MM M03 OEP PS Mech Serv: North Stradbroke Island WTP: 3 Monthly North South Bore Pump Station Service requires maintenance to complete 'Bore Pump station Mechanical Inspection - Work Instruction' (TEM-00240 - WI – M03 Bore Pump Stn Insp) which includes steps 19-21 to check for leaks on pipeline assets. Update 15/05/2020: ION01366 has been raised for installing on-line turbidity monitoring of the combined raw. Reassigned to new DWQ Advisor South - DG
1003949 | Open | Supply System | Supply System - Brisbane Zone - Contamination by IngressDue to one or more of the following contaminants leading to out of specification treated water:- Vermin- Rain- Dust or other debrisMedium (8) (WQ Risk Treatment) | Replace/repair Green Hill Reservoir membrane. | M - 8 | 2023-07-19 | 2026-06-30 |  | Identified in the IAMP with completion expected by July 2026. Also identified in the Facility Risk Review Register. RTP 103.
1003951 | Open | Supply System | Supply System - Logan Zone - Loss of Control System Leading to out of specification treated water.Medium (9) (WQ Risk Treatment) | Implement remote manual capability of the Daisy Hill Pumps to be able to fill up Kimberley Park reservoir when 4G outages occur at this site. | M - 9 | 2023-08-09 | 2026-06-30
1003957 | Open | Supply System | Heinemann Road Reservoirs - Add new additional chlorine instruments to individual reservoir outlets 2 and 3. (WQ Risk Treatment) | Finding from Incident Investigation Heinemann Road Reservoirs 2 3 Combined Outlet Total Chlorine Report (REX D19/17613). | M - 8 | 2019-12-19 | 2026-07-30 |  | As per Risk Assessment - D25/14766 Instrument on combined outlet only, not individual reservoirs, need this to be the case. ACTION: MM to add to EWPL. - Update: TBC 28/02/2024: KM - Risk Assessment score in ION was updated Moderate Likely = High due to only having combined monitoring on the outlet currently. There has been a reportable incident to the Water Supply Regulator before because of this configuration.
1003959 | Open | Supply System | Supply System - Disinfection (secondary) - Incorrect ammonia doseUnder dosing aqueous ammonia NH3(aq) leading to out of specification treated waterMedium (5) - EPIMedium (8) - NPIMedium (5) - SRP (WQ Risk Treatment) | 1). Online ammonia instruments to be installed and commissioned at Chambers Flat and Caloundra Street WQMFs. 2). Install Chemscan analyser at Gramzow Road WQMF. 3). Conduct Process Assessment of chambers Flat WQMF dosing systems. | M - 8 | 2019-04-24 | 2026-07-31 |  | 1). Instruments have been installed at Caloundra Street WQMF and Chamber Flat WQMF. Still not operable as yet. 2). Refer to ION 01633 for information on Gramzow Road WQMF Chemscan
1003965 | Open | Point Lookout WTP | TPL-RW-A-11308 Risk Treatment: Remove CCT bypass (WQ Risk Treatment) | Risk Treatment (raised HACCP Team meeting 2016): Bypass is thought to exist on outlet of 45 kL tank bypassing treated water reservoir. Bypass existence and condition requires confirmation and, if confirmed, removal. Refer REX 724654 Drawing I-DWG-TPL-601 PID Treated Water Storage. TPL - Disinfection (primary) - Failure or incorrect operation of a bypass valve Failure or incorrect operation of treated water reservoir bypass (dosed water to balance tank to treated water pumps) Risk: Medium (8) Target Risk: Medium (5) | M - 8 | 2020-01-24 | 2026-09-30 |  | Bypass exists on outlet of 45 kL tank bypassing treated water reservoir. Refer REX 724654 Drawing I-DWG-TPL-601 PID Treated Water Storage. Update R.A 2019: Bypass valve closed 2019. ION raised for valve and intermediate balance tank to be removed. ION00430 Reassigned to new DWQ Advisor South - DG DG: This improvement will take considerable work. DWQ will work to include with plant augmentation in medium term.
1003971 | Open | Supply System | Supply System - Logan Zone - Reservoirs - Contamination by IngressDue to one or more of the following contaminants leading to out of specification treated water:- Vermin- Rain- Dust or other debrisMedium (8) (WQ Risk Treatment) | Investigate possible solutions to reduce the likelihood of WQ related issues with the Break of Head Tank. | H - 12 | 2023-08-08 | 2026-10-30
1003977 | Closed | Mt Crosby East Bank WTP | Eastbank WTP - Coagulation - Flash mixer failure.Ineffective coagulation, flocculation and sedimentation, filter breakthrough and out of specification treated water.Medium (8). (WQ Risk Treatment) | 1). Installation of jet flash mixers for Sedimentation Basins No. 3 and 4. RTP ID 70 - Captured in the Facility Risk Review for Central - Sitting with ASP | M - 8 | 2019-04-24 | 2026-12-29 | 2024-09-12 | DWQ RA Review 12 Sep 24: - Installation of jet flash mixers for Sedimentation Basins No. 3 and 4. [Installed but never commissioned successfully - didn't work. Upgrades to chanels and riser in basin 3 have sufficiently improved mixing. CLOSED]
1003983 | Open | Supply System | Supply System - SRP - Contamination by IngressDue to one or more of the following contaminants leading to out of specification treated water:- Vermin- Rain- Dust or other debrisMedium (8) (WQ Risk Treatment) | 1. Investigate when Stapylton Reservoir is due for refurbishment and identify any works planned to reduce the risk of ingress due to the size of roof sheeting. 2. Determine when Ventilation at Molendinar 7 reservoir is being upgraded and escalate if required. | M - 8 | 2023-07-31 | 2026-12-31 |  | 1. Stapylton Balance Tank has been fed into the Facility Risk Review Register for Supply System via EAR196. Facility Risk Review RTP ID 324. This item has been discussed with Engineering Standards, Maintenance and Supply System Ops team. Due to overall reservoir vermin proofing being done and due to the type of breathers under the roof, the risk has been assessed as low compared to other reservoirs in the network. Ventilator upgrade completed in Feb 2024 which included vermin mesh. This risk will be checked annually to make sure it has not increased. Stapylton Balance Tank is not in the capital program for the next 10 years. 2. Molendinar Reservoir 7 has been fed into the Facility Risk Review Register for Supply System via EAR199. Facility Risk Review RTP ID 326
1003985 | Open | Supply System | Supply System - Redland Zone - Disinfection (Secondary) - Incorrect Chlorine dose. Overdosing of sodium hypochlorite leading to out of specification treated water. Medium (8) (WQ Risk Treatment) | 1. Develop P&ID's for Alex Hills and Heinemann Road Reservoirs. 2. Chemical dosing manuals cannot be located for Heinemann Road Reservoirs 3. Conduct a Process Assessment of Heinemann Road and Alex Hills dosing. | M - 8 | 2023-08-07 | 2026-12-31 |  | 15/07/25 - 2. Documents have been checked in the archives and dosing manuals have not been able to be located. This item was due to an overdose previously around location of instrument draw of points in the reservoir. This has not been able to be determined.
1003989 | Open | Moogerah Dam WTP | TMG-RW-A 10411 Risk Treatment: HBT Assessment required for this WTP. Conservative assessment made at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP requires additional protozoa removal (i.e UV). (WQ Risk Treatment) | TMG - Flocculation and Settling - Carryover of floc, sludge or algae in settled water Carry over of floc, sludge or algae on to the filters causing filter break through caused by: - clarifier boil up - inadequate solids removal - Build up of solids in settled water balance tank Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Filter breakthrough resulting in hazards not being adequately controlled Medium (8) (TMG-15) TMG - Media Filtration - Filter breakthrough Deterioration of Granular Activated Carbon (GAC) media resulting in inadequate removal of TO (primarily) and organics and manganese (secondary) due to: exceed GAC lifespan Medium (8) (TMG-15) | M - 8 | 2019-09-05 | 2027-05-31 |  | Update R.A 2020: Conservative assessment at the time of the R.A based on source water risk (Cat 4) and standard log reduction credits through conventional WTP processes. WTP will require additional protozoa treatment (i.e UV). Update 2020: ION01470 raised for the installation of UV
1003999 | Open | Mt Crosby West Bank WTP | Westbank WTP - Disinfection (primary) - Contamination of service water distribution system due to main break or backflow incident. (Risk Treatment) Potential contamination of treated water.Medium (8). (WQ Risk Treatment) | Conduct audit of the the service water to ensure that there are adequate measures in place to stop backflow events. | M - 8 | 2019-04-24 | 2027-07-30 |  | Audit completed. Recommendations to be delivered. Refer to ION 01642 for further information. Update 16/01/2024: ION 01642 (raised 2020) is still in the initiation phase and has not yet been assigned by the Change Coordinator. Risk to be discussed at the next HACCP Team meeting (Mar 24) to determine priority and moving things forward through the Change Coordinator. ION to progress and design/capital works to be undertaken through the subsequent ION stages.
1004001 | Open | Supply System | Supply System - Logan Zone - Loss of Power Leading to out of specification treated water. Medium (8) (WQ Risk Treatment) | Investigate implementation of permanent generator at Trinder Park. | M - 8 | 2023-08-09 | 2027-07-30
1004003 | Open | Supply System | Supply System - Disinfection (secondary) - Incorrect chlorine doseUnder dosing of sodium hypochlorite causing poor secondary disinfection leading to out of specification treated water.Medium (8). (WQ Risk Treatment) | Redlands Supply Zone - Investigation of having duplicate single instruments for Heinemann Road Reservoirs 1, 2 3. | M - 8 | 2019-04-24 | 2027-10-31 |  | Refer to ION 01629 for further information on this improvement.
1004009 | Open | Supply System | Supply System - NPI Zone - Bulk Pipeline - Contamination due to pipe depressurisationIngress of contaminants through:- Pipe joints.- Air valves.- Leaking valves and hydrants.- Aging infrastructure.- Scours.Ingress caused by loss of pressure in main during:- Pipe burst.- Pipe repairs.- Very high flows (e.g. fire fighting) .- Incorrect isolation for maintenanceMedium (8) (WQ Risk Treatment) | SCADA PLC upgrade on NPI which includes full commissioning to the operating philosophy of NPI. | M - 8 | 2023-07-25 | 2027-12-31 |  | This will be included in a SCADA project being completed in 2027.
1004011 | Open | Supply System | Supply System - Redland Zone - Reservoirs - Contamination by IngressDue to one or more of the following contaminants leading to out of specification treated water:- Vermin- Rain- Dust or other debrisHigh (12) (WQ Risk Treatment) | Investigate box gutters at Alexandra Hills 4 Reservoir. | M - 8 | 2023-08-04 | 2027-12-31 |  | Replace roof including re-design of gutter for Alexandra Hills Reservoir 4 is in the IAMP Capital Program for delivery in 2026/2027
1004017 | Open | North Stradbroke Island WTP | TNS-RW-A-9565 Risk Treatment: Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF (oPRP). Under no circumstances would these bypasses be operated. (WQ Risk Treatment) | TNS - Dissolved Air Flotation (DAF) - Failure or incorrect operation of a bypass valve. Failure or incorrect operation of bypass from flash mixer to settled water main, or Failure or incorrect operation of bypass from supernatant return line to settled water main". Medium (8). (TNS-24) | M - 8 | 2019-04-24 | 2028-06-30 |  | Update R.A 2018: Raised RR workshop 2018. Update 25/03/2020: ION raised (ION01324): Supernatant return to Filter inlet (bypass Coagulation CCP and DAF oPRP) needs to be removed. Flash mixer to Filter inlet (bypass Coagulation CCP floc zone and DAF oPRP). Under no circumstances would these bypasses be operated. DG: Ops do not run in direct filtration mode (never have).
1004019 | Open | Mt Crosby East Bank WTP | Eastbank WTP - Raw Water Abstraction - Change in Raw Water Source (Risk Treatment). Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water. High (12) (formerly Medium (8)).. (WQ Risk Treatment) | 1). Undertake HBT Assessment for this site. Completed. Refer Rex D19/46266 Eastbank WTP - HBT Assessment 2017-18 - HBT Assessment Report July 2017 - June 2018. 2) Long term planning is underway for this WTP. | H - 12 | 2019-04-24 | 2028-12-31 |  | RA Review 12 Sep 24: - Undertake HBT Assessment for this site. [completed] - Long term planning is underway for the Mt Crosby WTPs - major WTP upgrade with additional barrier at West Bank enabling East bank to gofline during dirty water event peaks. MSC staged projects expected to improve interlock capabilities. Update as at 28 Oct 24: The Mt Crosby Resilience Improvements Strategic Assessment (Draft) identified the highest ranking option to address the resilience service need to be “1b Improve Existing: Install additional pathogen treatment barrier”. The Project Planning team, led by BH, will lead evaluation of this option. As the Strategic Assessment will very likely meet the requirements for a Strategic Business Case, we will move straight to preparation of a Preliminary Business case. We (BH) have prepared a draft Project Plan for preparation of the Preliminary Business Case which is located here: Record D24/265948: Mt Crosby Health based target pathogen barrier - Project Plan Project plan very roughly: • Preliminary business case – complete January 2026 • Detailed business case – complete January 2027 • Investment approval – June 2027 • Construction start July 2027 and complete December 2028
1004021 | Open | Mt Crosby West Bank WTP | Westbank WTP - Raw Water Abstraction - Change in raw water source (Risk Treatment) Intake of raw water that exceeds the treatment capacity of the WTP resulting in out of specification treated water.Medium (8). (WQ Risk Treatment) | 1). Undertake HBT Assessment for this site; 2). Long term planning is underway for this WTP. | H - 12 | 2019-04-24 | 2028-12-29 |  | 1). QMRA Mid Brisbane River study is currently underway. 2). Mid Brisbane River Water Supply Strategy Review is currently underway. Findings from this study will help inform long term planning requirements for Mt Crosby Eastbank and Westbank WTPs. Integrated Asset Management Plans - Mt Crosby to be completed by Oct 2022.
1004025 | Open | Supply System | Supply System - Reservoir - Elevated water age.Long retention times leading to:- Potential for nitrification of chloramines and loss of residual.- Taste and odour issues.- Potential increase in bacteria.Medium (8) (WQ Risk Treatment) | 1. Review options around performance (efficient mixing), replacement and installation of reservoir mixers in Supply System. 2. Investigate installation of mixer at Mt Cotton to assist with water age issues. Common Inlet/Outlet. | H - 12 | 2020-07-17 | 2028-12-29 |  | 15/07/25 - Decision on future direction of mixer replacements will be made after development of an Asset Class Plan, Maintenance Plan and Renewals plan. Business Case for Heinemann Road Reservoirs is waiting for funding approval.
1004027 | Open | Supply System | Supply System - Brisbane Zone - Reservoir - Elevated water age.Long retention times leading to:- Potential for nitrification of chloramines and loss of residual.- Taste and odour issues.- Potential increase in bacteria.High (12) (WQ Risk Treatment) | Investigate additional dosing facilities in the network. | M - 8 | 2023-07-19 | 2028-12-31 |  | 04/12/24 - Will be informed by long term planning for the Supply System.
1004031 | Open | Esk WTP | Esk WTP Upgrade - Replacement WTP design-construct-commission (Project IW289700) (WQ Risk Treatment) | Please refer to Project IW289700 for details. | H - 12 | 2024-02-19 | 2030-02-19
1004033 | Open | Lowood WTP | Somerset South- Lowood WTP- risk treatment Medium (6). (WQ Risk Treatment) | Consideration should be given to looking at the most effective means of managing cyanotoxins (i.e. saxitoxins) and TO compounds at this WTP (i.e. PAC dosing etc.) | H - 10 | 2020-07-21 | 2030-04-30 |  | During the latest risk assessment review DS stated that there are no plans to upgrade the current WTP with a PAC dosing system. DS will discuss with the stakeholders on a desired level of T and O compounds.
1004035 | Open | Supply System | Supply System - NPI Zone - Reservoirs - Elevated water age. Long retention times leading to:- Potential for nitrification of chloramines and loss of residual.- Taste and odour issues.- Potential increase in bacteria.High (12) (WQ Risk Treatment) | Investigate mixers at Narangba as its a more urgent requirement. | M - 8 | 2023-07-27 | 2030-12-31 |  | This has been included in the Networks Facility Risk Review process.
1004039 | Open | Mt Crosby West Bank WTP | Westbank WTP - Raw Water Abstraction - Cyanobacteria bloomIntake of a high level of contaminants Medium (6) (WQ Risk Treatment) | Options analysis to be undertaken to feed into business case for project, looking at the most effective means of managing cyanotoxins (i.e. saxitoxins) and TO compounds at this WTP (i.e. PAC dosing etc.). | M - 9 | 2020-07-16 | 2031-12-31 |  | Mid Brisbane River Water Supply Strategy Review is currently underway. Findings from this study will help inform long term planning requirements for Mt Crosby Eastbank and Westbank WTPs IMP WQ Investment Strategy Report (D23/272266): Mt Crosby Catchment: Very Poor - Improve catchment performance and target sites/hazardous events which may cause catchment to exceed HBT Cat 4. Catchment investment of Tier 1 and Tier 2 minimum. The MCA assessment for treatment options is completely focussed on HBT improvements and does not include TO/cyano toxin removal treatment options. The future duplication/upgrade of Mt Crosby Westbank currently includes options for TO/cyano toxin removal through either PAC or ozone-BAC or GAC solutions. Westbank treated water combines with Eastbank treated water and could be used to reduce production at Eastbank and dilute any contaminant levels following the upgrade. This project is in the early scoping phase and is not yet scheduled for commencement. The current risk prioritisation is focussed on health (HBT) improvements menaing that aesthetic improvements (TO) and no significant cyano toxin events for Mt Crosby does not prioritise this capital improvement. There is a push from operations to increase attention to the need for TO removal treatment capability at Mt Crosby in the lead up to the 2032 Olympic games based on significant risks to the organisation other than WQ-health.
1004039 | Open | Mt Crosby West Bank WTP | Westbank WTP - Raw Water Abstraction - Cyanobacteria bloom, T&O and conductivity/hardness Intake of a high level of contaminants (WQ Risk Treatment) | Options analysis to be undertaken to feed into business case for project, looking at the most effective means of managing cyanotoxins (i.e. saxitoxins) and TO compounds at this WTP (i.e. PAC dosing etc.). | M - 9 | 2020-07-16 | 2031-12-31 |  | Mid Brisbane River Water Supply Strategy Review is currently underway. Findings from this study will help inform long term planning requirements for Mt Crosby Eastbank and Westbank WTPs IMP WQ Investment Strategy Report (D23/272266): Mt Crosby Catchment: Very Poor - Improve catchment performance and target sites/hazardous events which may cause catchment to exceed HBT Cat 4. Catchment investment of Tier 1 and Tier 2 minimum. The MCA assessment for treatment options is completely focussed on HBT improvements and does not include TO/cyano toxin removal treatment options. The future duplication/upgrade of Mt Crosby Westbank currently includes options for TO/cyano toxin removal through either PAC or ozone-BAC or GAC solutions. Westbank treated water combines with Eastbank treated water and could be used to reduce production at Eastbank and dilute any contaminant levels following the upgrade. This project is in the early scoping phase and is not yet scheduled for commencement. The current risk prioritisation is focussed on health (HBT) improvements menaing that aesthetic improvements (TO) and no significant cyano toxin events for Mt Crosby does not prioritise this capital improvement. There is a push from operations to increase attention to the need for TO removal treatment capability at Mt Crosby in the lead up to the 2032 Olympic games based on significant risks to the organisation other than WQ-health.
1004067 | Open | Ewen Maddock WTP | PE to investigate potential improvements to reliability and robustness at ewen maddock to reduce likelihood of underdosing (WQ Risk Treatment) | PE to investigate potential improvements to reliability and robustness at ewen maddock to reduce likelihood of underdosing | M - 8 | 2024-02-15 | 2034-02-15
1014059 | Closed | Kooralbyn WTP | Kooralbyn WTP - Tag out clarifier bypass valve and install a lock to secure position of the valve as closed. (WQ Risk Treatment) | Tag out clarifier bypass valve and install a lock to secure position of the valve as closed. (If the bypass valve were operated, theoretically, it would result in the bypass of an QCP however, in the case of Kooralbyn, the WTP currently does not meet the HBT target for protozoa therefore this bypass cannot be operated.) | M - 8 | 2024-06-13 10:44 | 2024-12-31 | 2024-12-18 | Tag out clarifier bypass valve completed and lock installed to secure position of the valve as closed.
1087782 | Open | Image Flat WTP | Raw water valves and Filter valves MUST FAIL CLOSED (WQ Risk Treatment) | There have been several instances where the generator has failed to start. The valves MUST fail CLOSED. | M - 8 | 2024-10-15 09:18 | 2025-12-01 |  | Recommend operations create a SOP in the event of a power failure the outlet valves are manually closed by the duty operator. If new actuators are required a MOC would have to be submitted. Maintenance trialed a self-closing actuator that worked during the recent event, however it was damaged during the event. 4 fail to close actuators have been ordered from rotork to resolve this issue and avoid any future WQ incidents. Current lead time is 22 weeks. NE: We close it once they're in.
1113535 | Open | Dunwich WTP | Dunwich WTP increased Pathogen Treatment required (WQ Risk Treatment) | The source water assessment, process engineering and HACCP RA have identified that a treatemtn shortfall exists at Dunwich. the source water challenge is bacteria 6 lrv, virus 6 lrv, proto 5 lrv. the current level of treatment is bacteria 4 lrv, virus 4 lrv, proto 0 lrv. there for the treatment shortfall is bacteria 2 lrv, virus 2 lrv, proto 5 lrv. | H - 10 | 2024-11-27 16:15 | 2025-11-27 |  | A project is underway to deliver this.
1113543 | Open | North Stradbroke Island WTP | WQ Risk Treatment: 2024 HACCP RA create procedure, signage, process monitoring and protection and storm water protection | 1) create procedure details the tankering process from NSI into each of the NSI town WTPs 2) install signage to identify the location of the TW tanker coupling point 3) install service water flow monitoring to better monitor tankering water flow/volume and, determine if needed and install transient pressure protection. 4) install a riser or similar protection to prevent storm water entering tanker coupling valve pit. | M - 8 | 2024-11-27 16:48 | 2026-06-30
1116822 | Open | Dayboro WTP | TDY & TKE UVT Analysers (WQ Risk Treatment) | The plant has no online UVT monitoring and hence no way to validate or enact this requirement. There is a risk that if the plant were to fall below 90% UVT and it is not identified, the required pathogenic log reduction may not be achieved. | H - 12 | 2024-12-03 | 2026-03-27
1118171 | Open | Supply System | Supply System - SWP Zone - Bulk Pipeline - High flow, rapid flow changes or reverse flow in pipelines leading to: Scouring and sloughing of biofilm and sediment. Medium (8) (WQ Risk Treatment) | Operational activity to be undertaken to inspect internal pipeline during defect period | M - 8 | 2024-04-12 | 2026-12-31 |  | SWP is not operational and has not been fully commissioned as yet
1118174 | Open | Supply System | Supply System - SWP Zone - Reservoirs - Elevated water age - Long retention times leading to: - Potential for nitrification of chloramines and loss of residual. - Taste and odour issues. - Potential increase in bacteria. Medium (8) (WQ Risk Treatment) | Operational philosophy to be developed for the Beaudesert WTP and the SWP, especially in winter. | M - 8 | 2024-04-12 | 2026-12-31 |  | SWP is currently not operational and has not been fully commissioned. SWP dosing facility is not producing water so no winter operating Philosophy has been developed as yet.
1118176 | Open | Supply System | Supply System - SWP Zone - Reservoirs - Inadequate Mixing - Poor mixing in a reservoir leading to: - Pockets of reduced quality water. - Increase the possibility of nitrification Medium (8) (WQ Risk Treatment) | Verification sampling to be conducted at the pump station for 12 months to obtain data to determine water age risk in reservoir. | M - 8 | 2024-04-12 | 2027-12-31 |  | SWP is currently not operational and has not been fully commissioned so sampling has not been started at the pump station yet.
1126738 | Open | Kooralbyn WTP | Kooralbyn WTP- acid dosing to control coagulation pH correction (WQ Risk Treatment) | Acid dosing point to be installed as part of the sludge management upgrade | M - 8 | 2024-12-18 11:38 | 2025-12-31
1137940 | Open | North Stradbroke Island WTP | NSI Tankering risks - signage, storm water protection, process monitoring and protection, procedure (WQ Risk Treatment) | NSI Tankering risks - signage, storm water protection, process monitoring and protection, procedure 1. Confirm Ops or maintenance are able to install. | M - 8 | 2025-01-08 16:53 | 2025-10-31 |  | The required corrective actions for this action will be delivered by PE under action 1113543
1154451 | Open | Capalaba WTP | investigate increased OC/THM mitigation (WQ Risk Treatment) | Source water challenge is resulting in elevated THM and poor chlorine residual in the TW. the RA identified THMs as a M9 mitigated risk -requiring treatment. note due date is set to before the next summer period. | M - 9 | 2025-02-03 16:23 | 2025-10-01
1154455 | Open | Capalaba WTP | investigate increased T&O removal (WQ Risk Treatment) | Source water challenge is resulting in elevated taste and odour in the TW. the RA identified T&O as a M9 mitigated risk -requiring treatment. due date is set for before the next summer period - in line with THM action (1154451) | M - 9 | 2025-02-03 16:38 | 2025-10-01
1155767 | Open | Mudgeeraba WTP | investigate and implement increased pathogen reduction in response to HID being cat 4 under the source water assessment (WQ Risk Treatment) | 1) investigate and implement preventative measure to achieve 4 lrv removal of virus/bacteria. 2) investigate and implement preventative measure to achieve additional 1 lrv removal of protozoa | M - 8 | 2025-02-05 12:58 | 2025-12-01
1155796 | Open | Molendinar WTP | investigate and implement increased pathogen reduction in response to HID being cat 4 under the source water assessment (WQ Risk Treatment) | 1) investigate and implement preventative measure to achieve 4 lrv removal of virus/bacteria. 2) investigate and implement preventative measure to achieve additional 1 lrv removal of protozoa | M - 8 | 2025-02-05 17:53 | 2026-02-05
1178959 | Open | Ewen Maddock WTP | Introduction of another protozoa / crypto barrier (WQ Risk Treatment) | Another barrier is required for crypto as we have a 1 log credit shortfall against the ADWG Chapter 5. | M - 8 | 2025-03-12 09:53 | 2035-12-31
1210554 | Open | Capalaba WTP | TCP THM mitigation works (WQ Risk Treatment) | A series of supply augmentations and WTP process improvements were investigated and to reduce the area that would receive water with elevated THMs and mitigate THM generation in the WTP. | M - 9 | 2025-05-02 10:02 | 2025-09-12 |  | This has recently been raised as a VH16 risk in the ARMA process (specifically on having the current PAC system available due to a safety risk). There is increased focus on restoring the PAC system and improving capacity before the 25/26 summer.
1211897 | Open | Linville WTP | WQ RISK TREATMENT: action to install new high level res linville | A significant failure in the inspection program led to the mass contamination of the high level reservoir with a number of amphibians. Testing of the water revealed there was no elevated risk (no total/ecoli and elevated free chlorine) however the entrainment of the animals in the reservoir for some time is a significant risk. The high level res should be inspected by operator. | M - 8 | 2025-05-07 12:14 | 2030-05-31
1234971 | Open | Linville WTP | DWQMP - HACCP Risk Assessment Action - Linville WTP - Secure Res Hatches (WQ Risk Treatment) | The reservoir hatches at Linville require securing | M - 8 | 2025-06-05 08:22 | 2025-08-30
1275909 | Open | Lowood WTP | Central Region- Somerset South- Lowood WTP- Back up power generator for raw water PS (WQ Risk Treatment) | Lowood WTP- Back up power generator for raw water PS (project in planning); Plug and play option set up, but takes work to bring online with portable generator | M - 8 | 2021-04-19 | 2028-06-30 |  | Project in planning stages.
1275923 | Open | Mt Crosby East Bank WTP | East Bank WTP - Whole of System - Camerons Hill Reservoirs improve vermin proofing (Medium 8) (WQ Risk Treatment) | Upgrade vermin proofing need to Seqwater standard at CH1 and CH2 reservoirs. | M - 8 | 2021-12-08 | 2028-12-31 |  | Still progressing through planning.
1275926 | Open | Mt Crosby East Bank WTP | East Bank WTP - Fluoridation - Holts Hill fluoridation system rectification works (Medium 8) (WQ Risk Treatment) | Continue ongoing rectification works with the Holts Hill Fluoride project to address issues identified after the upgrade including the service water. | M - 9 | 2021-12-08 | 2028-12-31 |  | Still progressing through planning.
1275930 | Open | Mt Crosby West Bank WTP | Westbank WTP - Service water - Backflow prevention audit (WQ Risk Treatment) | Full audit needs to be undertaken on backflow prevention at West Bank WTP. | M - 8 | 2020-07-16 | 2028-12-31 |  | Still progressing through planning.
1275932 | Open | Mt Crosby West Bank WTP | Westbank WTP - Coagulation-Flocculation-Sedimentation - Upgrade baffled floc chambers (WQ Risk Treatment) | Upgrade Baffled floc chambers - these have aged and are degredaded. Possible short circuiting - needs refurbishment to perform well | M - 8 | 2020-07-16 | 2028-12-31 |  | Still progressing through planning.